## Mapping
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37
StationWare | [6 empty] | Common |  |  | Import | [12 empty] | Export
[8 empty] | Enumeration |  | Pre-Condition |  |  |  |  | Instruction | [7 empty] | Pre-Condition | [5 empty] | Instruction
Key | Chapter | Display name | Range | Unit | Description | Type | Group | Mapping | Type |  | Setting | Operator | Value | Default |  | Operator | Value | Target | Parameter | Type | Scale | Offset |  | Source | Parameter | Type | Operator | Value |  | Source | Parameter | Type | Operator | Value | Scale | Offset
x110 | Funktionsumfang | 110 | nur dreipolig¦25278;ein-/dreipolig¦25279 |  | Auslöseverhalten | Enum | Configuration | 0;3 | String |  |  |  |  | 0 | 2 |  |  | Distance Polygonal\Single Pole Trip | aDipset | String |  |  | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Single Pole Trip | aDipset | String
[18 empty] | Distance Circular\Single Pole Trip | aDipset | String |  |  |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Single Pole Trip | aDipset | String
x114 | Funktionsumfang | 114 | Impedanz-Anregung¦25149;I-Anregung¦25150;U-I-Anregung¦25151;U-I-phi-Anregung¦25152;nicht vorhanden¦7 |  | Distanzschutz Anregung | Enum | Configuration | z;oc;ui;up | String |  |  |  |  | oc | 2 |  |  | Distance Polygonal\Starting | atype | String |  |  | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Starting | atype | String
[18 empty] | Distance Circular\Starting | atype | String |  |  |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Starting | atype | String
x115 | Funktionsumfang | 115 | Polygon-Charakteristik¦25101;Kreis-Charakteristik¦25102 |  | Distanzzonen-Charakteristik | Enum | Configuration | 0;1 | Real |  |  |  |  | 0 | 4 | E | 0 | Distance Polygonal | outserv | Real | 0 | 0 | [6 empty] | 2 | Distance Circular | outserv | Real | E | 0 | 0 | 1
[16 empty] | E | 0 | Distance Circular | outserv | Real | 0 | 1 | [7 empty] | Distance Polygonal | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Distance Polygonal | outserv | Real | 0 | 1
[16 empty] | E | 1 | Distance Circular | outserv | Real | 0 | 0
x121 | Funktionsumfang | 121 | Mitnahme über Messbereichserweiterung¦25113;Mitnahme über Anregung¦25196;Signalvergleich¦25114;Richtungsvergleich¦25117;Unblocking¦25115;Blocking¦25116;Rückwärtige Verriegelung¦25197;Streckenschutz¦25198;nicht vorhanden¦7 |  | Distanzschutz Signalzusatz | Enum | Configuration | PUTT;N/A;POTT;N/A;N/A;N/A;N/A;COMP;OFF | String | 2 | x115 | E | 0 | OFF | 13 | E | PUTT | Distance Polygonal\Signal Send | outserv | Real | 0 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 | 3 | Distance Polygonal\Signal Send | sLogic | String | E | PUTT=TRIP |  | PUTT
[16 empty] | E | PUTT | Distance Polygonal\Signal Send | sLogic | String |  | PUTT=TRIP | [7 empty] | Distance Polygonal\Signal Send | sLogic | String | E | POTT=TRIP |  | POTT
[16 empty] | E | PUTT | Distance Polygonal\Signal Receive | outserv | Real | 0 | 0 | [7 empty] | Distance Polygonal\Signal Send | sLogic | String | E | COMP=TRIP |  | COMP
[16 empty] | E | POTT | Distance Polygonal\Signal Send | outserv | Real | 0 | 0 |  | Distance Circular | outserv | Real | E | 0 | 3 | Distance Polygonal\Signal Send | sLogic | String | E | PUTT=TRIP |  | PUTT
[16 empty] | E | POTT | Distance Polygonal\Signal Send | sLogic | String |  | POTT=TRIP | [7 empty] | Distance Polygonal\Signal Send | sLogic | String | E | POTT=TRIP |  | POTT
[16 empty] | E | POTT | Distance Polygonal\Signal Receive | outserv | Real | 0 | 0 | [7 empty] | Distance Polygonal\Signal Send | sLogic | String | E | COMP=TRIP |  | COMP
[16 empty] | E | COMP | Distance Polygonal\Signal Send | outserv | Real | 0 | 0
[16 empty] | E | COMP | Distance Polygonal\Signal Send | sLogic | String |  | COMP=TRIP
[16 empty] | E | COMP | Distance Polygonal\Signal Receive | outserv | Real | 0 | 0
[16 empty] | E | N/A | Distance Polygonal\Signal Send | outserv | Real | 0 | 1
[16 empty] | E | N/A | Distance Polygonal\Signal Receive | outserv | Real | 0 | 1
[16 empty] | E | OFF | Distance Polygonal\Signal Send | outserv | Real | 0 | 1
[16 empty] | E | OFF | Distance Polygonal\Signal Receive | outserv | Real | 0 | 1
[11 empty] | x115 | E | 1 |  | 13 | E | PUTT | Distance Circular\Signal Send | outserv | Real | 0 | 0
[16 empty] | E | PUTT | Distance Circular\Signal Send | sLogic | String |  | PUTT=TRIP
[16 empty] | E | PUTT | Distance Circular\Signal Receive | outserv | Real | 0 | 0
[16 empty] | E | POTT | Distance Circular\Signal Send | outserv | Real | 0 | 0
[16 empty] | E | POTT | Distance Circular\Signal Send | sLogic | String |  | POTT=TRIP
[16 empty] | E | POTT | Distance Circular\Signal Receive | outserv | Real | 0 | 0
[16 empty] | E | COMP | Distance Circular\Signal Send | outserv | Real | 0 | 0
[16 empty] | E | COMP | Distance Circular\Signal Send | sLogic | String |  | COMP=TRIP
[16 empty] | E | COMP | Distance Circular\Signal Receive | outserv | Real | 0 | 0
[16 empty] | E | N/A | Distance Circular\Signal Send | outserv | Real | 0 | 1
[16 empty] | E | N/A | Distance Circular\Signal Receive | outserv | Real | 0 | 1
[16 empty] | E | OFF | Distance Circular\Signal Send | outserv | Real | 0 | 1
[16 empty] | E | OFF | Distance Circular\Signal Receive | outserv | Real | 0 | 1
x126 | Funktionsumfang | 126 | nicht vorhanden¦7;UMZ/AMZ (IEC-Kurven)¦25103;UMZ/AMZ (IEC-Kurven) mit 3. UMZ-Stufe¦25503 |  | Überstromzeitschutz | Enum | Configuration | Disabled;TOC IEC;Definite | String |  |  |  |  | Disabled | 4 | E | Disabled | Overcurrent | outserv | Real | 0 | 1 | 3 | Overcurrent | outserv | Real | E | 1 | [7 empty] | Disabled
[16 empty] | NE | Disabled | Overcurrent | outserv | Real | 0 | 0 |  | Overcurrent\Ip> | outserv | Real | E | 0 | 2 | Overcurrent\Ip> | pcharac |  | SW | IEC |  | TOC IEC
[16 empty] | E | Definite | Overcurrent\Ip> | pcharac | [16 empty] | Definite
[16 empty] | E | Definite | Overcurrent\3I0p | pcharac |  |  |  |  | Overcurrent\3I0p | outserv | Real | E | 0 | 2 | Overcurrent\3I0p | pcharac |  | SW | IEC |  | TOC IEC
Definite
x133 | Funktionsumfang | 133 | 1 WE-Zyklus¦25175;2 WE-Zyklen¦25176;3 WE-Zyklen¦25177;4 WE-Zyklen¦25178;5 WE-Zyklen¦25179;6 WE-Zyklen¦25180;7 WE-Zyklen¦25181;8 WE-Zyklen¦25182;ASP¦25174;nicht vorhanden¦7 |  | Automatische Wiedereinschaltung | Enum | Configuration | 1;2;3;4;5;6;7;8;-1;0 | Real |  |  |  |  | 0 | 4 | G | 0 | Distance Polygonal\Reclosing | oplockout | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 | 2 | Distance Polygonal\Reclosing | outserv | Real | E | 1 | 0 | 0
[16 empty] | E | 0 | Distance Polygonal\Reclosing | outserv | Real | 0 | 1 | [7 empty] | Distance Polygonal\Reclosing | oplockout | Real |  |  | 1 | 0
[16 empty] | G | 0 | Distance Circular\Reclosing | oplockout | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 | 2 | Distance Circular\Reclosing | outserv | Real | E | 1 | 0 | 0
[16 empty] | E | 0 | Distance Circular\Reclosing | outserv | Real | 0 | 1 | [7 empty] | Distance Circular\Reclosing | oplockout | Real |  |  | 1 | 0
x137 | Funktionsumfang | 137 | nicht vorhanden¦7;vorhanden¦8;vorhanden mit Kompoundierung¦25238 |  | Spannungsschutz | Enum | Configuration | 0;1;2 | Real |  |  |  |  | 0 | 2 | E | 0 | Voltage | outserv | Real | 0 | 1 | [7 empty] | Voltage | outserv | Real | E | 1 | 0 | 0
[16 empty] | NE | 0 | Voltage | outserv | Real | 0 | 0
x204 | Anlagendaten 1 | 204 | 80-125 | V | Wandler-Nennspannung, sekundär | Real | Configuration | [7 empty] | 3 |  |  | Measurement | Unom | Real | 1 | 0 | [7 empty] | Measurement | Unom | Real |  |  | 1 | 0
[18 empty] | Measurement Delta | Unom | Real | 1 | 0
[18 empty] | Measurement Seq | Unom | Real | 1 | 0
x207 | Anlagendaten 1 | 207 | geerdet¦25133;gelöscht¦25134;isoliert¦25135 |  | Sternpunktbehandlung des Netzes | Enum | Configuration | 0;1;2 | Real | [5 empty] | 2 |  |  | Distance Polygonal\Starting | isysstar | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Starting | isysstar | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Starting | isysstar | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Starting | isysstar | Real |  |  | 1 | 0
x237 | Anlagendaten 1 | 237 | Anpassungsfaktoren RE/RL bzw. XE/XL¦25147;Anpassungsfaktor K0¦25148 |  | Format der Erdimpedanzanpassungsfaktoren | Enum | Configuration | 0;1 | Real | [5 empty] | 4 |  |  | Distance Polygonal\Polarizing Z1 | complexrepr | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Polarizing Z1 | complexrepr | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Polarizing Z1b-Z5 | complexrepr | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Polarizing Z1 | complexrepr | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Polarizing Z1 | complexrepr | Real | 1 | 0
[18 empty] | Distance Circular\Polarizing Z1b-Z5 | complexrepr | Real | 1 | 0
x1105 | Anlagendaten 2 | 1105 | 30-89 | ° | Winkel der Leitungsimpedanz | Real | Setting | [7 empty] | 4 |  |  | Distance Polygonal\Polarizing Z1 | lineangle | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Polarizing Z1 | lineangle | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Polarizing Z1b-Z5 | lineangle | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Polarizing Z1 | lineangle | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Polarizing Z1 | lineangle | Real | 1 | 0
[18 empty] | Distance Circular\Polarizing Z1b-Z5 | lineangle | Real | 1 | 0
x1116 | Anlagendaten 2 | 1116 | -0.33-7.00 |  | Anpassungsfaktor RE/RL für die 1. Zone | Real | Setting | [7 empty] | 2 |  |  | Distance Polygonal\Polarizing Z1 | ReRl | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Polarizing Z1 | ReRl | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Polarizing Z1 | ReRl | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Polarizing Z1 | ReRl | Real |  |  | 1 | 0
x1117 | Anlagendaten 2 | 1117 | -0.33-7.00 |  | Anpassungsfaktor XE/XL für die 1. Zone | Real | Setting | [7 empty] | 2 |  |  | Distance Polygonal\Polarizing Z1 | XeXl | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Polarizing Z1 | XeXl | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Polarizing Z1 | XeXl | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Polarizing Z1 | XeXl | Real |  |  | 1 | 0
x1118 | Anlagendaten 2 | 1118 | -0.33-7.00 |  | Anpassungsfaktor RE/RL f. höhere Zonen | Real | Setting | [7 empty] | 2 |  |  | Distance Polygonal\Polarizing Z1b-Z5 | ReRl | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Polarizing Z1b-Z5 | ReRl | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Polarizing Z1b-Z5 | ReRl | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Polarizing Z1b-Z5 | ReRl | Real |  |  | 1 | 0
x1119 | Anlagendaten 2 | 1119 | -0.33-7.00 |  | Anpassungsfaktor XE/XL f. höhere Zonen | Real | Setting | [7 empty] | 2 |  |  | Distance Polygonal\Polarizing Z1b-Z5 | XeXl | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Polarizing Z1b-Z5 | XeXl | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Polarizing Z1b-Z5 | XeXl | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Polarizing Z1b-Z5 | XeXl | Real |  |  | 1 | 0
x1120 | Anlagendaten 2 | 1120 | 0.000-4.000 |  | Anpassungsfaktor K0 (Z1) | Real | Setting | [7 empty] | 2 |  |  | Distance Polygonal\Polarizing Z1 | k0 | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Polarizing Z1 | k0 | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Polarizing Z1 | k0 | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Polarizing Z1 | k0 | Real |  |  | 1 | 0
x1121 | Anlagendaten 2 | 1121 | -135.00-135.00 | deg | Anpassungswinkel K0 (Z1) | Real | Setting | [7 empty] | 2 |  |  | Distance Polygonal\Polarizing Z1 | phik0 | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Polarizing Z1 | phik0 | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Polarizing Z1 | phik0 | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Polarizing Z1 | phik0 | Real |  |  | 1 | 0
x1122 | Anlagendaten 2 | 1122 | 0.000-4.000 |  | Anpassungsfaktor K0 (> Z1) | Real | Setting | [7 empty] | 2 |  |  | Distance Polygonal\Polarizing Z1b-Z5 | k0 | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Polarizing Z1b-Z5 | k0 | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Polarizing Z1b-Z5 | k0 | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Polarizing Z1b-Z5 | k0 | Real |  |  | 1 | 0
x1123 | Anlagendaten 2 | 1123 | -135.00-135.00 | deg | Anpassungswinkel K0 (> Z1) | Real | Setting | [7 empty] | 2 |  |  | Distance Polygonal\Polarizing Z1b-Z5 | phik0 | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Polarizing Z1b-Z5 | phik0 | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Polarizing Z1b-Z5 | phik0 | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Polarizing Z1b-Z5 | phik0 | Real |  |  | 1 | 0
x1126 | Anlagendaten 2 | 1126 | 0.00-8.00 |  | Koppelimp. f. Parallell.ltgs.komp. RM/RL | Real | Setting | [7 empty] | 4 |  |  | Distance Polygonal\Polarizing Z1 | RmRl | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Polarizing Z1 | RmRl | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Polarizing Z1b-Z5 | RmRl | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Polarizing Z1 | RmRl | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Polarizing Z1 | RmRl | Real | 1 | 0
[18 empty] | Distance Circular\Polarizing Z1b-Z5 | RmRl | Real | 1 | 0
x1127 | Anlagendaten 2 | 1127 | 0.00-8.00 |  | Koppelimp. f. Parallell.ltgs.komp. XM/XL | Real | Setting | [7 empty] | 4 |  |  | Distance Polygonal\Polarizing Z1 | XmXl | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Polarizing Z1 | XmXl | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Polarizing Z1b-Z5 | XmXl | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Polarizing Z1 | XmXl | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Polarizing Z1 | XmXl | Real | 1 | 0
[18 empty] | Distance Circular\Polarizing Z1b-Z5 | XmXl | Real | 1 | 0
x1128 | Anlagendaten 2 | 1128 | 50-95 | % | Erdstromverhältnis Parallelleitungskomp. | Real | Setting | [7 empty] | 4 |  |  | Distance Polygonal\Polarizing Z1 | PcompRatio | Real | 0.01 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Polarizing Z1 | PcompRatio | Real |  |  | 100 | 0
[18 empty] | Distance Polygonal\Polarizing Z1b-Z5 | PcompRatio | Real | 0.01 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Polarizing Z1 | PcompRatio | Real |  |  | 100 | 0
[18 empty] | Distance Circular\Polarizing Z1 | PcompRatio | Real | 0.01 | 0
[18 empty] | Distance Circular\Polarizing Z1b-Z5 | PcompRatio | Real | 0.01 | 0
x1201 | Distanzschutz allgemein | 1201 | Ein¦22;Aus¦23 |  | Distanzschutz | Enum | Setting | 0;1 | Real | [5 empty] | 2 |  |  | Distance Polygonal\Distance Trip | outserv | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Distance Trip | outserv | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Distance Trip | outserv | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Distance Trip | outserv | Real |  |  | 1 | 0
x1202 | Distanzschutz allgemein | 1202 | 0.05-4.00 | A | Mindestphasenstrom Iph> | Real | Setting | [7 empty] | 2 |  |  | Distance Polygonal\Starting | Iphmins | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Starting | Iphmins | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Starting | Iphmins | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Starting | Iphmins | Real |  |  | 1 | 0
x1203 | Distanzschutz allgemein | 1203 | 0.05-4.00 | A | Erdfehlererkennung 3I0> | Real | Setting | [7 empty] | 2 |  |  | Distance Polygonal\Starting | Iegs | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Starting | Iegs | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Starting | Iegs | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Starting | Iegs | Real |  |  | 1 | 0
x1204 | Distanzschutz allgemein | 1204 | 1-100;oo=9999999 | V | Erdfehlererkennung 3U0> | Real | Setting | [7 empty] | 2 |  |  | Distance Polygonal\Starting | Ue | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Starting | Ue | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Starting | Ue | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Starting | Ue | Real |  |  | 1 | 0
x1205 | Distanzschutz allgemein | 1205 | 10-200 | V | 3U0>: Ansprechwert für gel./isol. Netze | Real | Setting | [7 empty] | 2 |  |  | Distance Polygonal\Starting | Ueiso | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Starting | Ueiso | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Starting | Ueiso | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Starting | Ueiso | Real |  |  | 1 | 0
x1207A | Distanzschutz allgemein | 1207A | 0.05-0.30 |  | 3I0>-Anregestabilisierung (3I0>/Iphmax) | Real | Setting | [7 empty] | 2 |  |  | Distance Polygonal\Starting | Estabfac | Real | 100 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Starting | Estabfac | Real |  |  | 0.01 | 0
[18 empty] | Distance Circular\Starting | Estabfac | Real | 100 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Starting | Estabfac | Real |  |  | 0.01 | 0
x1209A | Distanzschutz allgemein | 1209A | 3I0> ODER 3U0>¦25240;3I0> UND 3U0>¦25241 |  | Kriterien für Erdfehlererkennung | Enum | Setting | 1;0 | Real | [5 empty] | 2 |  |  | Distance Polygonal\Starting | iEarthdet | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Starting | iEarthdet | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Starting | iEarthdet | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Starting | iEarthdet | Real |  |  | 1 | 0
x1210 | Distanzschutz allgemein | 1210 | mit Distanzschutz General-Anregung¦25244;mit Zonen-Anregung¦25245 |  | Start der Zonenzeiten | Enum | Setting | 1;0 | String | [5 empty] | 2 |  |  | Distance Polygonal\Timer Start | aDipset | String |  |  | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Timer Start | aDipset | String
[18 empty] | Distance Circular\Timer Start | aDipset | String |  |  |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Timer Start | aDipset | String
x1211 | Distanzschutz allgemein | 1211 | 30-90 | ° | Winkel der Distanzschutzcharakteristik | Real | Setting | [7 empty] | 6 |  |  | Distance Polygonal\Z1 | phi | Real | 1 | 0 | 6 | Distance Polygonal\Z1 | outserv | Real | E | 0 |  | Distance Polygonal\Z1 | phi | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z1b | phi | Real | 1 | 0 |  | Distance Polygonal\Z1b | outserv | Real | E | 0 |  | Distance Polygonal\Z1b | phi | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z2 | phi | Real | 1 | 0 |  | Distance Polygonal\Z2 | outserv | Real | E | 0 |  | Distance Polygonal\Z2 | phi | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z3 | phi | Real | 1 | 0 |  | Distance Polygonal\Z3 | outserv | Real | E | 0 |  | Distance Polygonal\Z3 | phi | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z4 | phi | Real | 1 | 0 |  | Distance Polygonal\Z4 | outserv | Real | E | 0 |  | Distance Polygonal\Z4 | phi | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z5 | phi | Real | 1 | 0 |  | Distance Polygonal\Z5 | outserv | Real | E | 0 |  | Distance Polygonal\Z5 | phi | Real |  |  | 1 | 0
x1220 | Distanzschutz allgemein | 1220 | L3 (L1) AZYKLISCH¦25153;L1 (L3) AZYKLISCH¦25154;L2 (L1) AZYKLISCH¦25155;L1 (L2) AZYKLISCH¦25156;L3 (L2) AZYKLISCH¦25157;L2 (L3) AZYKLISCH¦25158;L3 (L1) ZYKLISCH¦25159;L1 (L3) ZYKLISCH¦25160;alle beteiligten Schleifen¦12676 |  | Phasenbevorzugung f. Doppelerdschlüsse | Enum | Setting | 0;1;2;3;4;5;6;7;8 | Real | [5 empty] | 2 |  |  | Distance Polygonal\Starting | iPHPRE | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Starting | iPHPRE | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Starting | iPHPRE | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Starting | iPHPRE | Real |  |  | 1 | 0
x1221A | Distanzschutz allgemein | 1221A | Blockierung der voreilenden Phase¦12823;Blockierung der nacheilenden Phase¦12821;alle beteiligten Schleifen¦12676;nur Phase-Phase Schleifen¦12527;nur Phase-Erde Schleifen¦12528 |  | Schleifenauswahl bei Ph-Ph-E-Anregung | Enum | Setting | 3;4;5;6;7 | Real | [5 empty] | 2 |  |  | Distance Polygonal\Starting | iPhPhE | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Starting | iPhPhE | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Starting | iPhPhE | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Starting | iPhPhE | Real |  |  | 1 | 0
x1241 | Distanzschutz allgemein | 1241 | 0.100-600.000;oo=9999999 | Ohm | Grenze RL des Lastkegels für LE-Schleif. | Real | Setting | [6 empty] | 9999999 | 6 | S | 9999999 | Distance Polygonal\Load Area | Rloadphe | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 | 2 | Distance Polygonal\Load Area | outserv | Real | E | 1 | 0 | 9999999
[16 empty] | S | 9999999 | Distance Polygonal\Load Area | outserv | Real | 0 | 0 | [7 empty] | Distance Polygonal\Load Area | Rloadphe | Real |  |  | 1 | 0
[16 empty] | E | 9999999 | Distance Polygonal\Load Area | outserv | Real | 0 | 1 |  | Distance Circular | outserv | Real | E | 0 | 2 | Distance Circular\Load Area | outserv | Real | E | 1 | 0 | 9999999
[16 empty] | S | 9999999 | Distance Circular\Load Area | Rloadphe | Real | 1 | 0 | [7 empty] | Distance Circular\Load Area | Rloadphe | Real |  |  | 1 | 0
[16 empty] | S | 9999999 | Distance Circular\Load Area | outserv | Real | 0 | 0
[16 empty] | E | 9999999 | Distance Circular\Load Area | outserv | Real | 0 | 1
x1242 | Distanzschutz allgemein | 1242 | 20-60 | ° | Öffnungswinkel des Lastkegels f. LE-Sch. | Real | Setting | [7 empty] | 2 |  |  | Distance Polygonal\Load Area | philoadphe | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Load Area | philoadphe | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Load Area | philoadphe | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Load Area | philoadphe | Real |  |  | 1 | 0
x1243 | Distanzschutz allgemein | 1243 | 0.100-600.000;oo=9999999 | Ohm | Grenze RL des Lastkegels für LL-Schleif. | Real | Setting |  |  |  | x1241 | S | 9999999 |  | 6 | S | 9999999 | Distance Polygonal\Load Area | Rloadphph | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 | 2 | Distance Polygonal\Load Area | outserv | Real | E | 1 | 0 | 9999999
[16 empty] | S | 9999999 | Distance Polygonal\Load Area | outserv | Real | 0 | 0 | [7 empty] | Distance Polygonal\Load Area | Rloadphph | Real |  |  | 1 | 0
[16 empty] | E | 9999999 | Distance Polygonal\Load Area | outserv | Real | 0 | 1 |  | Distance Circular | outserv | Real | E | 0 | 2 | Distance Circular\Load Area | outserv | Real | E | 1 | 0 | 9999999
[16 empty] | S | 9999999 | Distance Circular\Load Area | Rloadphph | Real | 1 | 0 | [7 empty] | Distance Circular\Load Area | Rloadphph | Real |  |  | 1 | 0
[16 empty] | S | 9999999 | Distance Circular\Load Area | outserv | Real | 0 | 0
[16 empty] | E | 9999999 | Distance Circular\Load Area | outserv | Real | 0 | 1
x1244 | Distanzschutz allgemein | 1244 | 20-60 | ° | Öffnungswinkel des Lastkegels f. LL-Sch. | Real | Setting | [7 empty] | 2 |  |  | Distance Polygonal\Load Area | philoadphph | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Load Area | philoadphph | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Load Area | philoadphph | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Load Area | philoadphph | Real |  |  | 1 | 0
x1301 | Distanzzonen (Polygon) | 1301 | vorwärts¦12514;rückwärts¦12515;ungerichtet¦12516;unwirksam¦12656 |  | Betriebsart der Zone Z1 | Enum | Setting | 0;1;2;3 | Real | 2 | x115 | E | 0 | 3 | 3 | NE | 3 | Distance Polygonal\Z1 | idir | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 | 2 | Distance Polygonal\Z1 | outserv | Real | E | 1 | 0 | 3
[16 empty] | NE | 3 | Distance Polygonal\Z1 | outserv | Real | 0 | 0 | [7 empty] | Distance Polygonal\Z1 | idir | Real |  |  | 1 | 0
[16 empty] | E | 3 | Distance Polygonal\Z1 | outserv | Real | 0 | 1 |  | Distance Circular | outserv | Real | E | 0 | 2 | Distance Circular\Z1 | outserv | Real | E | 1 | 0 | 3
[15 empty] | 3 | S | 2 | Distance Circular\Z1 | idir | Real | 1 | 0 | [7 empty] | Distance Circular\Z1 | idir | Real |  |  | 1 | 0
[16 empty] | S | 2 | Distance Circular\Z1 | outserv | Real | 0 | 0
[16 empty] | GE | 2 | Distance Circular\Z1 | outserv | Real | 0 | 1
x1302 | Distanzzonen (Polygon) | 1302 | 0.050-600.000 | Ohm | Resistanz R(Z1) | Real | Setting | [10 empty] | Distance Polygonal\Z1 | Rmax | Real | 1 | 0 |  | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Z1 | Rmax | Real |  |  | 1 | 0
x1303 | Distanzzonen (Polygon) | 1303 | 0.050-600.000 | Ohm | Reaktanz X(Z1) | Real | Setting | [10 empty] | Distance Polygonal\Z1 | Xmax | Real | 1 | 0 |  | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Z1 | Xmax | Real |  |  | 1 | 0
x1304 | Distanzzonen (Polygon) | 1304 | 0.050-600.000 | Ohm | Resistanz bei Erdfehlern RE(Z1) | Real | Setting | [10 empty] | Distance Polygonal\Z1 | REmax | Real | 1 | 0 |  | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Z1 | REmax | Real |  |  | 1 | 0
x1305 | Distanzschutz allgemein | 1305 | 0.00-30.00;oo=9999999 | sec | Verzögerungszeit T1-1pol | Real | Setting | [7 empty] | 2 |  |  | Distance Polygonal\TZ1 1Pol | Tdelay | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\TZ1 1Pol | Tdelay | Real |  |  | 1 | 0
[18 empty] | Distance Circular\TZ1 1Pol | Tdelay | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\TZ1 1Pol | Tdelay | Real |  |  | 1 | 0
x1306 | Distanzschutz allgemein | 1306 | 0.00-30.00;oo=9999999 | sec | Verzögerungszeit T1-mehrpol | Real | Setting | [7 empty] | 2 |  |  | Distance Polygonal\TZ1 | Tdelay | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\TZ1 | Tdelay | Real |  |  | 1 | 0
[18 empty] | Distance Circular\TZ1 | Tdelay | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\TZ1 | Tdelay | Real |  |  | 1 | 0
x1307 | Distanzzonen (Polygon) | 1307 | 0-45 | deg | Polygonabschrägung (1. Quadrant) | Real | Setting | [10 empty] | Distance Polygonal\Z1 | beta | Real | 1 | 0 |  | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Z1 | beta | Real |  |  | 1 | 0
x1502 | Distanzzonen (Kreis) | 1502 | 0.050-600.000 | Ohm | ZR(Z1), Radius der Zone Z1 | Real | Setting | [10 empty] | Distance Circular\Z1 | Zm | Real | 0 | 1 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Z1 | Zm | Real |  |  | 1 | 0
x1503 | Distanzzonen (Kreis) | 1503 | 10-90;0 | deg | ALPHA(Z1), Winkel f. Resistanzreserve | Real | Setting | [7 empty] | 3 | GE | 10 | Distance Circular\Z1 | arcalpha | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 | 2 | Distance Circular\Z1 | arcen | Real | E | 0 | 0 | 0
[16 empty] | GE | 10 | Distance Circular\Z1 | arcen | Real | 0 | 1 | [7 empty] | Distance Circular\Z1 | arcalpha | Real |  |  | 1 | 0
[16 empty] | S | 10 | Distance Circular\Z1 | arcen | Real | 0 | 0
x1311 | Distanzzonen (Polygon) | 1311 | vorwärts¦12514;rückwärts¦12515;ungerichtet¦12516;unwirksam¦12656 |  | Betriebsart der Zone Z2 | Enum | Setting | 0;1;2;3 | Real | 2 | x115 | E | 0 | 3 | 3 | NE | 3 | Distance Polygonal\Z2 | idir | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 | 2 | Distance Polygonal\Z2 | outserv | Real | E | 1 | 0 | 3
[16 empty] | NE | 3 | Distance Polygonal\Z2 | outserv | Real | 0 | 0 | [7 empty] | Distance Polygonal\Z2 | idir | Real |  |  | 1 | 0
[16 empty] | E | 3 | Distance Polygonal\Z2 | outserv | Real | 0 | 1 |  | Distance Circular | outserv | Real | E | 0 | 2 | Distance Circular\Z2 | outserv | Real | E | 1 | 0 | 3
[15 empty] | 3 | S | 2 | Distance Circular\Z2 | idir | Real | 1 | 0 | [7 empty] | Distance Circular\Z2 | idir | Real |  |  | 1 | 0
[16 empty] | S | 2 | Distance Circular\Z2 | outserv | Real | 0 | 0
[16 empty] | GE | 2 | Distance Circular\Z2 | outserv | Real | 0 | 1
x1312 | Distanzzonen (Polygon) | 1312 | 0.050-600.000 | Ohm | Resistanz R(Z2) | Real | Setting | [10 empty] | Distance Polygonal\Z2 | Rmax | Real | 1 | 0 |  | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Z2 | Rmax | Real |  |  | 1 | 0
x1313 | Distanzzonen (Polygon) | 1313 | 0.050-600.000 | Ohm | Reaktanz X(Z2) | Real | Setting | [10 empty] | Distance Polygonal\Z2 | Xmax | Real | 1 | 0 |  | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Z2 | Xmax | Real |  |  | 1 | 0
x1314 | Distanzzonen (Polygon) | 1314 | 0.050-600.000 | Ohm | Resistanz bei Erdfehlern RE(Z2) | Real | Setting | [10 empty] | Distance Polygonal\Z2 | REmax | Real | 1 | 0 |  | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Z2 | REmax | Real |  |  | 1 | 0
x1315 | Distanzschutz allgemein | 1315 | 0.00-30.00;oo=9999999 | sec | Verzögerungszeit T2-1pol | Real | Setting | [7 empty] | 2 |  |  | Distance Polygonal\TZ2 1Pol | Tdelay | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\TZ2 1Pol | Tdelay | Real |  |  | 1 | 0
[18 empty] | Distance Circular\TZ2 1Pol | Tdelay | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\TZ2 1Pol | Tdelay | Real |  |  | 1 | 0
x1316 | Distanzschutz allgemein | 1316 | 0.00-30.00;oo=9999999 | sec | Verzögerungszeit T2-mehrpol | Real | Setting | [7 empty] | 2 |  |  | Distance Polygonal\TZ2 | Tdelay | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\TZ2 | Tdelay | Real |  |  | 1 | 0
[18 empty] | Distance Circular\TZ2 | Tdelay | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\TZ2 | Tdelay | Real |  |  | 1 | 0
x1317A | Distanzschutz allgemein | 1317A | Nein¦24;Ja¦25 |  | Einpoliges AUS bei Fehler in Z2 | Enum | Setting | 0;1 | String | [5 empty] | 2 |  |  | Distance Polygonal\Z2 Trip | aDipset | String |  |  | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Z2 Trip | aDipset | String
[18 empty] | Distance Circular\Z2 Trip | aDipset | String |  |  |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Z2 Trip | aDipset | String
x1512 | Distanzzonen (Kreis) | 1512 | 0.050-600.000 | Ohm | ZR(Z2), Radius der Zone Z2 | Real | Setting | [10 empty] | Distance Circular\Z2 | Zm | Real | 0 | 1 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Z2 | Zm | Real |  |  | 1 | 0
x1513 | Distanzzonen (Kreis) | 1513 | 10-90;0 | deg | ALPHA(Z2), Winkel f. Resistanzreserve | Real | Setting | [7 empty] | 3 | GE | 10 | Distance Circular\Z2 | arcalpha | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 | 2 | Distance Circular\Z2 | arcen | Real | E | 0 | 0 | 0
[16 empty] | GE | 10 | Distance Circular\Z2 | arcen | Real | 0 | 1 | [7 empty] | Distance Circular\Z2 | arcalpha | Real |  |  | 1 | 0
[16 empty] | S | 10 | Distance Circular\Z2 | arcen | Real | 0 | 0
x1321 | Distanzzonen (Polygon) | 1321 | vorwärts¦12514;rückwärts¦12515;ungerichtet¦12516;unwirksam¦12656 |  | Betriebsart der Zone Z3 | Enum | Setting | 0;1;2;3 | Real | 2 | x115 | E | 0 | 3 | 3 | NE | 3 | Distance Polygonal\Z3 | idir | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 | 2 | Distance Polygonal\Z3 | outserv | Real | E | 1 | 0 | 3
[16 empty] | NE | 3 | Distance Polygonal\Z3 | outserv | Real | 0 | 0 | [7 empty] | Distance Polygonal\Z3 | idir | Real |  |  | 1 | 0
[16 empty] | E | 3 | Distance Polygonal\Z3 | outserv | Real | 0 | 1 |  | Distance Circular | outserv | Real | E | 0 | 2 | Distance Circular\Z3 | outserv | Real | E | 1 | 0 | 3
[15 empty] | 3 | S | 2 | Distance Circular\Z3 | idir | Real | 1 | 0 | [7 empty] | Distance Circular\Z3 | idir | Real |  |  | 1 | 0
[16 empty] | S | 2 | Distance Circular\Z3 | outserv | Real | 0 | 0
[16 empty] | GE | 2 | Distance Circular\Z3 | outserv | Real | 0 | 1
x1322 | Distanzzonen (Polygon) | 1322 | 0.050-600.000 | Ohm | Resistanz R(Z3) | Real | Setting | [10 empty] | Distance Polygonal\Z3 | Rmax | Real | 1 | 0 |  | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Z3 | Rmax | Real |  |  | 1 | 0
x1323 | Distanzzonen (Polygon) | 1323 | 0.050-600.000 | Ohm | Reaktanz X(Z3) | Real | Setting | [10 empty] | Distance Polygonal\Z3 | Xmax | Real | 1 | 0 |  | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Z3 | Xmax | Real |  |  | 1 | 0
x1324 | Distanzzonen (Polygon) | 1324 | 0.050-600.000 | Ohm | Resistanz bei Erdfehlern RE(Z3) | Real | Setting | [10 empty] | Distance Polygonal\Z3 | REmax | Real | 1 | 0 |  | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Z3 | REmax | Real |  |  | 1 | 0
x1325 | Distanzschutz allgemein | 1325 | 0.00-30.00;oo=9999999 | sec | Verzögerungszeit T3 | Real | Setting | [7 empty] | 2 |  |  | Distance Polygonal\TZ3 | Tdelay | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\TZ3 | Tdelay | Real |  |  | 1 | 0
[18 empty] | Distance Circular\TZ3 | Tdelay | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\TZ3 | Tdelay | Real |  |  | 1 | 0
x1522 | Distanzzonen (Kreis) | 1522 | 0.050-600.000 | Ohm | ZR(Z3), Radius der Zone Z3 | Real | Setting | [10 empty] | Distance Circular\Z3 | Zm | Real | 0 | 1 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Z3 | Zm | Real |  |  | 1 | 0
x1523 | Distanzzonen (Kreis) | 1523 | 10-90;0 | deg | ALPHA(Z3), Winkel f. Resistanzreserve | Real | Setting | [7 empty] | 3 | GE | 10 | Distance Circular\Z3 | arcalpha | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 | 2 | Distance Circular\Z3 | arcen | Real | E | 0 | 0 | 0
[16 empty] | GE | 10 | Distance Circular\Z3 | arcen | Real | 0 | 1 | [7 empty] | Distance Circular\Z3 | arcalpha | Real |  |  | 1 | 0
[16 empty] | S | 10 | Distance Circular\Z3 | arcen | Real | 0 | 0
x1331 | Distanzzonen (Polygon) | 1331 | vorwärts¦12514;rückwärts¦12515;ungerichtet¦12516;unwirksam¦12656 |  | Betriebsart der Zone Z4 | Enum | Setting | 0;1;2;3 | Real | 2 | x115 | E | 0 | 3 | 3 | NE | 3 | Distance Polygonal\Z4 | idir | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 | 2 | Distance Polygonal\Z4 | outserv | Real | E | 1 | 0 | 3
[16 empty] | NE | 3 | Distance Polygonal\Z4 | outserv | Real | 0 | 0 | [7 empty] | Distance Polygonal\Z4 | idir | Real |  |  | 1 | 0
[16 empty] | E | 3 | Distance Polygonal\Z4 | outserv | Real | 0 | 1 |  | Distance Circular | outserv | Real | E | 0 | 2 | Distance Circular\Z4 | outserv | Real | E | 1 | 0 | 3
[15 empty] | 3 | S | 2 | Distance Circular\Z4 | idir | Real | 1 | 0 | [7 empty] | Distance Circular\Z4 | idir | Real |  |  | 1 | 0
[16 empty] | S | 2 | Distance Circular\Z4 | outserv | Real | 0 | 0
[16 empty] | GE | 2 | Distance Circular\Z4 | outserv | Real | 0 | 1
x1332 | Distanzzonen (Polygon) | 1332 | 0.050-600.000 | Ohm | Resistanz R(Z4) | Real | Setting | [10 empty] | Distance Polygonal\Z4 | Rmax | Real | 1 | 0 |  | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Z4 | Rmax | Real |  |  | 1 | 0
x1333 | Distanzzonen (Polygon) | 1333 | 0.050-600.000 | Ohm | Reaktanz X(Z4) | Real | Setting | [10 empty] | Distance Polygonal\Z4 | Xmax | Real | 1 | 0 |  | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Z4 | Xmax | Real |  |  | 1 | 0
x1334 | Distanzzonen (Polygon) | 1334 | 0.050-600.000 | Ohm | Resistanz bei Erdfehlern RE(Z4) | Real | Setting | [10 empty] | Distance Polygonal\Z4 | REmax | Real | 1 | 0 |  | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Z4 | REmax | Real |  |  | 1 | 0
x1335 | Distanzschutz allgemein | 1335 | 0.00-30.00;oo=9999999 | sec | Verzögerungszeit T4 | Real | Setting |  |  | 2 | x115 | E | 0 |  | 2 |  |  | Distance Polygonal\TZ4 | Tdelay | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\TZ4 | Tdelay | Real |  |  | 1 | 0
[18 empty] | Distance Circular\TZ4 | Tdelay | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\TZ4 | Tdelay | Real |  |  | 1 | 0
x1532 | Distanzzonen (Kreis) | 1532 | 0.050-600.000 | Ohm | ZR(Z4), Radius der Zone Z4 | Real | Setting | [10 empty] | Distance Circular\Z4 | Zm | Real | 0 | 1 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Z4 | Zm | Real |  |  | 1 | 0
x1533 | Distanzzonen (Kreis) | 1533 | 10-90;0 | deg | ALPHA(Z4), Winkel f. Resistanzreserve | Real | Setting | [7 empty] | 3 | GE | 10 | Distance Circular\Z4 | arcalpha | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 | 2 | Distance Circular\Z4 | arcen | Real | E | 0 | 0 | 0
[16 empty] | GE | 10 | Distance Circular\Z4 | arcen | Real | 0 | 1 | [7 empty] | Distance Circular\Z4 | arcalpha | Real |  |  | 1 | 0
[16 empty] | S | 10 | Distance Circular\Z4 | arcen | Real | 0 | 0
x1341 | Distanzzonen (Polygon) | 1331 | vorwärts¦12514;rückwärts¦12515;ungerichtet¦12516;unwirksam¦12656 |  | Operating mode Z5 | Enum | Setting | 0;1;2;3 | Real | 2 | x115 | E | 0 | 3 | 3 | NE | 3 | Distance Polygonal\Z5 | idir | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 | 2 | Distance Polygonal\Z5 | outserv | Real | E | 1 | 0 | 3
[16 empty] | NE | 3 | Distance Polygonal\Z5 | outserv | Real | 0 | 0 | [7 empty] | Distance Polygonal\Z5 | idir | Real |  |  | 1 | 0
[16 empty] | E | 3 | Distance Polygonal\Z5 | outserv | Real | 0 | 1 |  | Distance Circular | outserv | Real | E | 0 | 2 | Distance Circular\Z5 | outserv | Real | E | 1 | 0 | 3
[15 empty] | 3 | S | 2 | Distance Circular\Z5 | idir | Real | 1 | 0 | [7 empty] | Distance Circular\Z5 | idir | Real |  |  | 1 | 0
[16 empty] | S | 2 | Distance Circular\Z5 | outserv | Real | 0 | 0
[16 empty] | GE | 2 | Distance Circular\Z5 | outserv | Real | 0 | 1
x1342 | Distanzzonen (Polygon) | 1342 | 0.050-600.000 | Ohm | Resistanz R(Z5) | Real | Setting | [10 empty] | Distance Polygonal\Z5 | Rmax | Real | 1 | 0 |  | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Z5 | Rmax | Real |  |  | 1 | 0
x1343 | Distanzzonen (Polygon) | 1343 | 0.050-600.000 | Ohm | Reaktanz X(Z5)+ (Richtung vorwärts) | Real | Setting | [10 empty] | Distance Polygonal\Z5 | Xmax | Real | 1 | 0 |  | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Z5 | Xmax | Real |  |  | 1 | 0
x1344 | Distanzzonen (Polygon) | 1344 | 0.050-600.000 | Ohm | Resistanz bei Erdfehlern RE(Z5) | Real | Setting | [10 empty] | Distance Polygonal\Z5 | REmax | Real | 1 | 0 |  | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Z5 | REmax | Real |  |  | 1 | 0
x1345 | Distanzschutz allgemein | 1345 | 0.00-30.00;oo=9999999 | sec | Verzögerungszeit T5 | Real | Setting | [7 empty] | 2 |  |  | Distance Polygonal\TZ5 | Tdelay | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\TZ5 | Tdelay | Real |  |  | 1 | 0
[18 empty] | Distance Circular\TZ5 | Tdelay | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\TZ5 | Tdelay | Real |  |  | 1 | 0
x1346 | Distanzzonen (Polygon) | 1346 | 0.050-600.000 | Ohm | Reaktanz X(Z5)- (Richtung rückwärts) | Real | Setting | [10 empty] | Distance Polygonal\Z5 | Xmin | Real | 1 | 0 |  | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Z5 | Xmin | Real |  |  | 1 | 0
x1542 | Distanzzonen (Kreis) | 1542 | 0.050-600.000 | Ohm | ZR(Z5), Radius der Zone Z5 | Real | Setting | [10 empty] | Distance Circular\Z5 | Zm | Real | 0 | 1 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Z5 | Zm | Real |  |  | 1 | 0
x1543 | Distanzzonen (Kreis) | 1543 | 10-90;0 | deg | ALPHA(Z5), Winkel f. Resistanzreserve | Real | Setting | [7 empty] | 3 | GE | 10 | Distance Circular\Z5 | arcalpha | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 | 2 | Distance Circular\Z5 | arcen | Real | E | 0 | 0 | 0
[16 empty] | GE | 10 | Distance Circular\Z5 | arcen | Real | 0 | 1 | [7 empty] | Distance Circular\Z5 | arcalpha | Real |  |  | 1 | 0
[16 empty] | S | 10 | Distance Circular\Z5 | arcen | Real | 0 | 0
x1351 | Distanzzonen (Polygon) | 1351 | vorwärts¦12514;rückwärts¦12515;ungerichtet¦12516;unwirksam¦12656 |  | Betriebsart der Zone Z1B | Enum | Setting | 0;1;2;3 | Real | 2 | x115 | E | 0 | 3 | 3 | NE | 3 | Distance Polygonal\Z1b | idir | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 | 2 | Distance Polygonal\Z1b | outserv | Real | E | 1 | 0 | 3
[16 empty] | NE | 3 | Distance Polygonal\Z1b | outserv | Real | 0 | 0 | [7 empty] | Distance Polygonal\Z1b | idir | Real |  |  | 1 | 0
[16 empty] | E | 3 | Distance Polygonal\Z1b | outserv | Real | 0 | 1 |  | Distance Circular | outserv | Real | E | 0 | 2 | Distance Circular\Z1b | outserv | Real | E | 1 | 0 | 3
[15 empty] | 3 | S | 2 | Distance Circular\Z1b | idir | Real | 1 | 0 | [7 empty] | Distance Circular\Z1b | idir | Real |  |  | 1 | 0
[16 empty] | S | 2 | Distance Circular\Z1b | outserv | Real | 0 | 0
[16 empty] | GE | 2 | Distance Circular\Z1b | outserv | Real | 0 | 1
x1352 | Distanzzonen (Polygon) | 1352 | 0.050-600.000 | Ohm | Resistanz R(Z1B) | Real | Setting | [10 empty] | Distance Polygonal\Z1b | Rmax | Real | 1 | 0 |  | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Z1b | Rmax | Real |  |  | 1 | 0
x1353 | Distanzzonen (Polygon) | 1353 | 0.050-600.000 | Ohm | Reaktanz X(Z1B) | Real | Setting | [10 empty] | Distance Polygonal\Z1b | Xmax | Real | 1 | 0 |  | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Z1b | Xmax | Real |  |  | 1 | 0
x1354 | Distanzzonen (Polygon) | 1354 | 0.050-600.000 | Ohm | Resistanz bei Erdfehlern RE(Z1B) | Real | Setting | [10 empty] | Distance Polygonal\Z1b | REmax | Real | 1 | 0 |  | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Z1b | REmax | Real |  |  | 1 | 0
x1355 | Distanzschutz allgemein | 1355 | 0.00-30.00;oo=9999999 | sec | Verzögerungszeit T1B-1pol | Real | Setting | [7 empty] | 2 |  |  | Distance Polygonal\TZ1b 1Pol | Tdelay | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\TZ1b 1Pol | Tdelay | Real |  |  | 1 | 0
[18 empty] | Distance Circular\TZ1b 1Pol | Tdelay | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\TZ1b 1Pol | Tdelay | Real |  |  | 1 | 0
x1356 | Distanzschutz allgemein | 1356 | 0.00-30.00;oo=9999999 | sec | Verzögerungszeit T1B-mehrpol | Real | Setting | [7 empty] | 2 |  |  | Distance Polygonal\TZ1b | Tdelay | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\TZ1b | Tdelay | Real |  |  | 1 | 0
[18 empty] | Distance Circular\TZ1b | Tdelay | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\TZ1b | Tdelay | Real |  |  | 1 | 0
x1552 | Distanzzonen (Kreis) | 1552 | 0.050-600.000 | Ohm | ZR(Z1B), Radius der Zone Z1B | Real | Setting | [10 empty] | Distance Circular\Z1b | Zm | Real | 0 | 1 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Z1b | Zm | Real |  |  | 1 | 0
x1553 | Distanzzonen (Kreis) | 1553 | 10-90;0 | deg | ALPHA(Z1B), Winkel f. Resistanzreserve | Real | Setting | [7 empty] | 3 | GE | 10 | Distance Circular\Z1b | arcalpha | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 | 2 | Distance Circular\Z1b | arcen | Real | E | 0 | 0 | 0
[16 empty] | GE | 10 | Distance Circular\Z1b | arcen | Real | 0 | 1 | [7 empty] | Distance Circular\Z1b | arcalpha | Real |  |  | 1 | 0
[16 empty] | S | 10 | Distance Circular\Z1b | arcen | Real | 0 | 0
x1601 | Distanzschutz allgemein | 1601 | LE:Uphe/LL:Uphph¦25161;LE: Uphph/LL: Uphph¦25162;LE: Uphe/LL: Uphe¦25163;LE: Uphe/LL: I>>¦25164 |  | Anregeprogramm U/I-Anregung | Enum | Setting | 0;1;2;3 | Real | [5 empty] | 2 |  |  | Distance Polygonal\Starting | iProgUI | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Starting | iProgUI | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Starting | iProgUI | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Starting | iProgUI | Real |  |  | 1 | 0
x1602 | Distanzschutz allgemein | 1602 | 0-30;oo=9999999 | sec | Endzeit gerichtet | Real | Setting |  |  | 2 | x114 | NE | z |  | 4 |  |  | Distance Polygonal\T Directional | Tdelay | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 | 2 | Distance Polygonal\T Directional | outserv | Real | E | 1 | 0 | 9999999
[18 empty] | Distance Circular\T Directional | Tdelay | Real | 1 | 0 | [7 empty] | Distance Polygonal\T Directional | Tdelay | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\T Directional | outserv | Real | 0 | 0 |  | Distance Circular | outserv | Real | E | 0 | 2 | Distance Circular\T Directional | outserv | Real | E | 1 | 0 | 9999999
[18 empty] | Distance Circular\T Directional | outserv | Real | 0 | 0 | [7 empty] | Distance Circular\T Directional | Tdelay | Real |  |  | 1 | 0
[15 empty] | 2 |  |  | Distance Polygonal\T Directional | outserv | Real | 0 | 1
[18 empty] | Distance Circular\T Directional | outserv | Real | 0 | 1
x1603 | Distanzschutz allgemein | 1603 | 0-30;oo=9999999 | sec | Endzeit ungerichtet | Real | Setting |  |  | 2 | x114 | NE | z |  | 4 |  |  | Distance Polygonal\T Non Directional | Tdelay | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 | 2 | Distance Polygonal\T Non Directional | outserv | Real | E | 1 | 0 | 9999999
[18 empty] | Distance Circular\T Non Directional | Tdelay | Real | 1 | 0 | [7 empty] | Distance Polygonal\T Non Directional | Tdelay | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\T Non Directional | outserv | Real | 0 | 0 |  | Distance Circular | outserv | Real | E | 0 | 2 | Distance Circular\T Non Directional | outserv | Real | E | 1 | 0 | 9999999
[18 empty] | Distance Circular\T Non Directional | outserv | Real | 0 | 0 | [7 empty] | Distance Circular\T Non Directional | Tdelay | Real |  |  | 1 | 0
[15 empty] | 2 |  |  | Distance Polygonal\T Non Directional | outserv | Real | 0 | 1
[18 empty] | Distance Circular\T Non Directional | outserv | Real | 0 | 1
x1610 | Distanzschutz allgemein | 1610 | 0.25-10.00 | A | Iph>>: Ansprechwert | Real | Setting | [7 empty] | 2 |  |  | Distance Polygonal\Starting | Iphggs | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Starting | Iphggs | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Starting | Iphggs | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Starting | Iphggs | Real |  |  | 1 | 0
x1611 | Distanzschutz allgemein | 1611 | 0.10-4.00 | A | Iph>: Ansprechwert | Real | Setting | [7 empty] | 2 |  |  | Distance Polygonal\Starting | Iphgs | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Starting | Iphgs | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Starting | Iphgs | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Starting | Iphgs | Real |  |  | 1 | 0
x1612 | Distanzschutz allgemein | 1612 | 20-70 | V | Uphe: Ansprechwert bei Iph>> | Real | Setting | [7 empty] | 2 |  |  | Distance Polygonal\Starting | UpheIgg | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Starting | UpheIgg | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Starting | UpheIgg | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Starting | UpheIgg | Real |  |  | 1 | 0
x1613 | Distanzschutz allgemein | 1613 | 20-70 | V | Uphe: Ansprechwert bei Iph> | Real | Setting | [7 empty] | 2 |  |  | Distance Polygonal\Starting | UpheIg | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Starting | UpheIg | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Starting | UpheIg | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Starting | UpheIg | Real |  |  | 1 | 0
x1614 | Distanzschutz allgemein | 1614 | 40-130 | V | Uphph: Ansprechwert bei Iph>> | Real | Setting | [7 empty] | 2 |  |  | Distance Polygonal\Starting | UphphIgg | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Starting | UphphIgg | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Starting | UphphIgg | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Starting | UphphIgg | Real |  |  | 1 | 0
x1615 | Distanzschutz allgemein | 1615 | 40-130 | V | Uphph: Ansprechwert bei Iph> | Real | Setting | [7 empty] | 2 |  |  | Distance Polygonal\Starting | UphphIg | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Starting | UphphIg | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Starting | UphphIg | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Starting | UphphIg | Real |  |  | 1 | 0
x1616 | Distanzschutz allgemein | 1616 | 0.10-8.00 | A | Iphi>: Ansprechwert | Real | Setting | [7 empty] | 2 |  |  | Distance Polygonal\Starting | Iphigs | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Starting | Iphigs | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Starting | Iphigs | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Starting | Iphigs | Real |  |  | 1 | 0
x1617 | Distanzschutz allgemein | 1617 | 20-70 | V | Uphe: Ansprechwert bei Iphi> | Real | Setting | [7 empty] | 2 |  |  | Distance Polygonal\Starting | UpheIgphi | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Starting | UpheIgphi | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Starting | UpheIgphi | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Starting | UpheIgphi | Real |  |  | 1 | 0
x1618 | Distanzschutz allgemein | 1618 | 40-130 | V | Uphph: Ansprechwert bei Iphi> | Real | Setting | [7 empty] | 2 |  |  | Distance Polygonal\Starting | UphphIgphi | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Starting | UphphIgphi | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Starting | UphphIgphi | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Starting | UphphIgphi | Real |  |  | 1 | 0
x1619A | Distanzschutz allgemein | 1619A | Vorwärts und Rückwärts¦25165;vorwärts¦12514 |  | Wirkrichtung der Winkelanregung | Enum | Setting | 0;1 | Real | [5 empty] | 2 |  |  | Distance Polygonal\Starting | effectphi | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Starting | effectphi | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Starting | effectphi | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Starting | effectphi | Real |  |  | 1 | 0
x1620 | Distanzschutz allgemein | 1620 | 30-60 | deg | phi: Untere Grenze | Real | Setting | [7 empty] | 2 |  |  | Distance Polygonal\Starting | phig | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Starting | phig | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Starting | phig | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Starting | phig | Real |  |  | 1 | 0
x1621 | Distanzschutz allgemein | 1621 | 90-120 | deg | phi: Obere Grenze | Real | Setting | [7 empty] | 2 |  |  | Distance Polygonal\Starting | phis | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Starting | phis | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Starting | phis | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Starting | phis | Real |  |  | 1 | 0
x2101 | Distanzschutz Signalzusatz | 2101 | Ein¦22;Aus¦23 |  | Distanzschutz-Signalzusatz | Enum | Setting | 0;1 | Real | 2 | x115 | E | 0 | 1 | 2 |  |  | Distance Polygonal\Signal Send | outserv | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Signal Send | outserv | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Signal Receive | outserv | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Signal Send | outserv | Real |  |  | 1 | 0
[15 empty] | 2 |  |  | Distance Circular\Signal Send | outserv | Real | 1 | 0
[18 empty] | Distance Circular\Signal Receive | outserv | Real | 1 | 0
x2103A | Distanzschutz Signalzusatz | 2103A | 0.00-30.00:0.01 | s | Sendesignalverlängerung | Real | Setting |  |  | 2 | x121 | E | COMP | 0.05 | 4 |  |  | Distance Polygonal\T Send | Tdelay | Real | 0 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\T Send | Tdelay | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\T Send 1Pol | Tdelay | Real | 0 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\T Send | Tdelay | Real |  |  | 1 | 0
[18 empty] | Distance Circular\T Send | Tdelay | Real | 0 | 0
[18 empty] | Distance Circular\T Send 1Pol | Tdelay | Real | 0 | 0
[15 empty] | 4 |  |  | Distance Polygonal\T Send | Tdelay | Real | 1 | 0
[18 empty] | Distance Polygonal\T Send 1Pol | Tdelay | Real | 1 | 0
[18 empty] | Distance Circular\T Send | Tdelay | Real | 1 | 0
[18 empty] | Distance Circular\T Send 1Pol | Tdelay | Real | 1 | 0
x2601 | Überstromzeitschutz | 2601 | Ein: aktiv nur bei Messspannungsausfall¦25108;Ein: immer aktiv¦25237;Aus¦23 |  | Betriebsart | Enum | Setting | 0;1;2 | Real |  |  |  |  | 0 | 8 | E | 0 | Overcurrent\Operation Mode | aDipset | String |  | 3 | 7 | Overcurrent\Ip> | outserv | Real | E | 0 | 2 | Overcurrent\Operation Mode | aDipset | String | E | 3 |  | 0
[16 empty] | E | 1 | Overcurrent\Operation Mode | aDipset | String |  | 0 | [13 empty] | 1
[16 empty] | E | 2 | Overcurrent\Ip> | outserv | Real | 0 | 1 |  | Overcurrent\Iph> | outserv | Real | E | 0 | 2 | Overcurrent\Operation Mode | aDipset | String | E | 3 |  | 0
[16 empty] | E | 2 | Overcurrent\Iph> | outserv | Real | 0 | 1 | [13 empty] | 1
[16 empty] | E | 2 | Overcurrent\Iph>> | outserv | Real | 0 | 1 |  | Overcurrent\Iph>> | outserv | Real | E | 0 | 2 | Overcurrent\Operation Mode | aDipset | String | E | 3 |  | 0
[16 empty] | E | 2 | Overcurrent\3I0p | outserv | Real | 0 | 1 | [13 empty] | 1
[16 empty] | E | 2 | Overcurrent\3I0> | outserv | Real | 0 | 1 |  | Overcurrent\3I0p | outserv | Real | E | 0 | 2 | Overcurrent\Operation Mode | aDipset | String | E | 3 |  | 0
[16 empty] | E | 2 | Overcurrent\3I0>> | outserv | Real | 0 | 1 | [13 empty] | 1
[24 empty] | Overcurrent\3I0> | outserv | Real | E | 0 | 2 | Overcurrent\Operation Mode | aDipset | String | E | 3 |  | 0
1
[24 empty] | Overcurrent\3I0>> | outserv | Real | E | 0 | 2 | Overcurrent\Operation Mode | aDipset | String | E | 3 |  | 0
1
2
x2610 | Überstromzeitschutz | 2610 | 0.10-25.00;oo=9999999 | A | Iph>>: Ansprechwert | Real | Setting |  |  |  | x2601 | NE | 2 |  | 3 | S | 9999999 | Overcurrent\Iph>> | Ipsetr | Real | 1 | 0 | [6 empty] | 2 | Overcurrent\Iph>> | outserv | Real | E | 1 | 0 | 9999999
[16 empty] | S | 9999999 | Overcurrent\Iph>> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\Iph>> | Ipsetr | Real |  |  | 1 | 0
[16 empty] | E | 9999999 | Overcurrent\Iph>> | outserv | Real | 0 | 1
x2611 | Überstromzeitschutz | 2611 | 0.00-30.00;oo=9999999 | sec | Iph>>: Zeitverzögerung | Real | Setting | [10 empty] | Overcurrent\Iph>> | Tset | Real | 1 | 0 | [7 empty] | Overcurrent\Iph>> | Tset | Real |  |  | 1 | 0
x2612 | Überstromzeitschutz | 2612 | 0.05-25.00;oo=9999999 | A | 3I0>>: Ansprechwert | Real | Setting |  |  |  | x2601 | NE | 2 |  | 3 | S | 9999999 | Overcurrent\3I0>> | Ipsetr | Real | 1 | 0 | [6 empty] | 2 | Overcurrent\3I0>> | outserv | Real | E | 1 | 0 | 9999999
[16 empty] | S | 9999999 | Overcurrent\3I0>> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\3I0>> | Ipsetr | Real |  |  | 1 | 0
[16 empty] | E | 9999999 | Overcurrent\3I0>> | outserv | Real | 0 | 1
x2613 | Überstromzeitschutz | 2613 | 0.00-30.00;oo=9999999 | sec | 3I0>>: Zeitverzögerung | Real | Setting | [10 empty] | Overcurrent\3I0>> | Tset | Real | 1 | 0 | [7 empty] | Overcurrent\3I0>> | Tset | Real |  |  | 1 | 0
x2620 | Überstromzeitschutz | 2620 | 0.10-25.00;oo=9999999 | A | Iph>: Ansprechwert | Real | Setting |  |  |  | x2601 | NE | 2 |  | 3 | S | 9999999 | Overcurrent\Iph> | Ipsetr | Real | 1 | 0 | [6 empty] | 2 | Overcurrent\Iph> | outserv | Real | E | 1 | 0 | 9999999
[16 empty] | S | 9999999 | Overcurrent\Iph> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\Iph> | Ipsetr | Real |  |  | 1 | 0
[16 empty] | E | 9999999 | Overcurrent\Iph> | outserv | Real | 0 | 1
x2621 | Überstromzeitschutz | 2621 | 0.00-30.00;oo=9999999 | sec | Iph>: Zeitverzögerung | Real | Setting | [10 empty] | Overcurrent\Iph> | Tset | Real | 1 | 0 | [7 empty] | Overcurrent\Iph> | Tset | Real |  |  | 1 | 0
x2622 | Überstromzeitschutz | 2622 | 0.05-25.00;oo=9999999 | A | 3I0>: Ansprechwert | Real | Setting |  |  |  | x2601 | NE | 2 |  | 3 | S | 9999999 | Overcurrent\3I0> | Ipsetr | Real | 1 | 0 | [6 empty] | 2 | Overcurrent\3I0> | outserv | Real | E | 1 | 0 | 9999999
[16 empty] | S | 9999999 | Overcurrent\3I0> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\3I0> | Ipsetr | Real |  |  | 1 | 0
[16 empty] | E | 9999999 | Overcurrent\3I0> | outserv | Real | 0 | 1
x2623 | Überstromzeitschutz | 2623 | 0.00-30.00;oo=9999999 | sec | 3I0>: Zeitverzögerung | Real | Setting | [10 empty] | Overcurrent\3I0> | Tset | Real | 1 | 0 | [7 empty] | Overcurrent\3I0> | Tset | Real |  |  | 1 | 0
x2640 | Überstromzeitschutz | 2640 | 0.10-4.00;oo=9999999 | A | IP: Ansprechwert | Real | Setting |  |  |  | x2601 | NE | 2 |  | 3 | S | 9999999 | Overcurrent\Ip> | Ipsetr | Real | 1 | 0 | [6 empty] | 2 | Overcurrent\Iph> | outserv | Real | E | 1 | 0 | 9999999
[16 empty] | S | 9999999 | Overcurrent\Ip> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\Iph> | Ipsetr | Real |  |  | 1 | 0
[16 empty] | E | 9999999 | Overcurrent\Ip> | outserv | Real | 0 | 1
x2642 | Überstromzeitschutz | 2642 | 0.05-3.00;oo=9999999 | sec | IP: AMZ-Zeit für IEC-Kennlinien T IP | Real | Setting |  |  |  | x126 | E | TOC IEC |  |  |  |  | Overcurrent\Ip> | Tpset | Real | 1 | 0 |  | Overcurrent\Ip> | pcharac |  | SW | IEC |  | Overcurrent\Ip> | Tpset | Real |  |  | 1 | 0
x2646 | Überstromzeitschutz | 2646 | 0.00-30.00 | sec | IP: AMZ-Zusatzverzögerung T IPverz | Real | Setting |  |  |  | x126 | E | TOC IEC |  |  |  |  | Overcurrent\Ip> | Tadder | Real | 1 | 0 |  | Overcurrent\Ip> | pcharac |  | SW | IEC |  | Overcurrent\Ip> | Tadder | Real |  |  | 1 | 0
x2650 | Überstromzeitschutz | 2650 | 0.05-4.00;oo=9999999 | A | 3I0P: Ansprechwert | Real | Setting |  |  |  | x2601 | NE | 2 |  | 3 | S | 9999999 | Overcurrent\3I0p | Ipsetr | Real | 1 | 0 | [6 empty] | 2 | Overcurrent\3I0p | outserv | Real | E | 1 | 0 | 9999999
[16 empty] | S | 9999999 | Overcurrent\3I0p | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\3I0p | Ipsetr | Real |  |  | 1 | 0
[16 empty] | E | 9999999 | Overcurrent\3I0p | outserv | Real | 0 | 1
x2652 | Überstromzeitschutz | 2652 | 0.05-3.00;oo=9999999 | sec | 3I0P: AMZ-Zeit für IEC-Kennlinien T 3I0P | Real | Setting |  |  |  | x126 | E | TOC IEC |  |  |  |  | Overcurrent\3I0p | Tpset | Real | 1 | 0 |  | Overcurrent\3I0p | pcharac |  | SW | IEC |  | Overcurrent\3I0p | Tpset | Real |  |  | 1 | 0
x2656 | Überstromzeitschutz | 2656 | 0.00-30.00 | sec | 3I0P: AMZ-Zusatzverzögerung T 3I0Pverz | Real | Setting |  |  |  | x126 | E | TOC IEC |  |  |  |  | Overcurrent\3I0p | Tadder | Real | 1 | 0 |  | Overcurrent\3I0p | pcharac |  | SW | IEC |  | Overcurrent\3I0p | Tadder | Real |  |  | 1 | 0
x2660 | Überstromzeitschutz | 2660 | Invers¦12559;Stark invers¦12560;Extrem invers¦12561;AMZ Langzeit¦25126 |  | IEC-Kennlinie | Enum | Setting | IEC Normal Inverse;IEC Very Inverse;IEC Extremely Inverse;IEC Long Inverse | String |  | x126 | E | TOC IEC |  | 2 |  |  | Overcurrent\Ip> | pcharac |  |  |  | 2 | Overcurrent\Ip> | outserv | Real | E | 0 |  | Overcurrent\Ip> | pcharac |  | SW | IEC
[18 empty] | Overcurrent\3I0p | pcharac |  |  |  |  | Overcurrent\3I0p | outserv | Real | E | 0 |  | Overcurrent\3I0p | pcharac |  | SW | IEC
x3401 | Automatische Wiedereinschaltung | 3401 | Ein¦22;Aus¦23 |  | Automatische Wiedereinschaltung | Enum | Setting | 0;1 | Real |  | x133 | G | 0 |  | 2 |  |  | Distance Polygonal\Reclosing | outserv | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Reclosing | outserv | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Reclosing | outserv | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Reclosing | outserv | Real |  |  | 1 | 0
x3403 | Automatische Wiedereinschaltung | 3403 | 0.50-300.00 | sec | Sperrzeit nach Wiedereinschaltung | Real | Setting | [7 empty] | 2 |  |  | Distance Polygonal\Reclosing | resettime | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Reclosing | resettime | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Reclosing | resettime | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Reclosing | resettime | Real |  |  | 1 | 0
x3456 | Automatische Wiedereinschaltung | 3456 | 0.01-1800.00;oo=9999999 |  | Pausenzeit bei 1poliger Auslösung | Real | Setting | [7 empty] | 2 | S | 9999999 | Distance Polygonal\Reclosing | recltime11ph | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Reclosing | recltime11ph | Real |  |  | 1 | 0
[16 empty] | S | 9999999 | Distance Circular\Reclosing | recltime11ph | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Reclosing | recltime11ph | Real |  |  | 1 | 0
x3457 | Automatische Wiedereinschaltung | 3457 | 0.01-1800.00;oo=9999999 |  | Pausenzeit bei 3poliger Auslösung | Real | Setting | [7 empty] | 2 | S | 9999999 | Distance Polygonal\Reclosing | recltime1 | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Reclosing | recltime1 | Real |  |  | 1 | 0
[16 empty] | S | 9999999 | Distance Circular\Reclosing | recltime1 | Real | 1 | 0 |  | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Reclosing | recltime1 | Real |  |  | 1 | 0
x3468 | Automatische Wiedereinschaltung | 3468 | 0.01-1800.00;oo=9999999 |  | Pausenzeit bei 3poliger Auslösung | Real | Setting |  |  |  | x133 | GE | 2 |  | 2 | S | 9999999 | Distance Polygonal\Reclosing | recltime2 | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 | 2 | Distance Polygonal\Reclosing | oplockout | Real | S | 2 | 0 | 9999999
[16 empty] | S | 9999999 | Distance Circular\Reclosing | recltime2 | Real | 1 | 0 | [7 empty] | Distance Polygonal\Reclosing | recltime2 | Real |  |  | 1 | 0
[24 empty] | Distance Circular | outserv | Real | E | 0 | 2 | Distance Circular\Reclosing | oplockout | Real | S | 2 | 0 | 9999999
[30 empty] | Distance Circular\Reclosing | recltime2 | Real |  |  | 1 | 0
x3479 | Automatische Wiedereinschaltung | 3479 | 0.01-1800.00;oo=9999999 |  | Pausenzeit bei 3poliger Auslösung | Real | Setting |  |  |  | x133 | GE | 3 |  | 2 | S | 9999999 | Distance Polygonal\Reclosing | recltime3 | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 | 2 | Distance Polygonal\Reclosing | oplockout | Real | S | 3 | 0 | 9999999
[16 empty] | S | 9999999 | Distance Circular\Reclosing | recltime3 | Real | 1 | 0 | [7 empty] | Distance Polygonal\Reclosing | recltime3 | Real |  |  | 1 | 0
[24 empty] | Distance Circular | outserv | Real | E | 0 | 2 | Distance Circular\Reclosing | oplockout | Real | S | 3 | 0 | 9999999
[30 empty] | Distance Circular\Reclosing | recltime3 | Real |  |  | 1 | 0
x3490 | Automatische Wiedereinschaltung | 3490 | 0.01-1800.00;oo=9999999 |  | Pausenzeit bei 3poliger Auslösung | Real | Setting |  |  |  | x133 | GE | 4 |  | 2 | S | 9999999 | Distance Polygonal\Reclosing | recltime4 | Real | 1 | 0 | 2 | Distance Polygonal | outserv | Real | E | 0 | 2 | Distance Polygonal\Reclosing | oplockout | Real | S | 4 | 0 | 9999999
[16 empty] | S | 9999999 | Distance Circular\Reclosing | recltime4 | Real | 1 | 0 | [7 empty] | Distance Polygonal\Reclosing | recltime4 | Real |  |  | 1 | 0
[24 empty] | Distance Circular | outserv | Real | E | 0 | 2 | Distance Circular\Reclosing | oplockout | Real | S | 4 | 0 | 9999999
[30 empty] | Distance Circular\Reclosing | recltime4 | Real |  |  | 1 | 0
x3701 | Spannungsschutz | 3701 | Aus¦23;Nur Meldung¦12700;Ein¦22;U> nur melden, U>> Auslösung¦25188 |  | Betriebsart Ph-E-Überspannungsschutz | Enum | Setting | 0;1;2;3 | Real |  |  |  |  | 0 | 7 | E | 0 | Voltage\Uph-e>> | outserv | Real | 0 | 1 | 3 | Voltage\Uph-e>(>) | aDipset | String | E | 00 | 3 | Voltage\Uph-e> | outserv | Real | E | 0 | 0 | 1
[16 empty] | E | 0 | Voltage\Uph-e> | outserv | Real | 0 | 1 | [7 empty] | Voltage\Uph-e>> | outserv | Real | E | 0 | 0 | 1
[16 empty] | NE | 0 | Voltage\Uph-e>> | outserv | Real | 0 | 0 | [13 empty] | 0
[16 empty] | NE | 0 | Voltage\Uph-e> | outserv | Real | 0 | 0 |  | Voltage\Uph-e>(>) | aDipset | String | E | 11 | 3 | Voltage\Uph-e> | outserv | Real | E | 0 | 0 | 2
[16 empty] | E | 1 | Voltage\Uph-e>(>) | aDipset | String |  | 00 | [7 empty] | Voltage\Uph-e>> | outserv | Real | E | 0 | 0 | 2
[16 empty] | E | 2 | Voltage\Uph-e>(>) | aDipset | String |  | 11 | [13 empty] | 0
[16 empty] | E | 3 | Voltage\Uph-e>(>) | aDipset | String |  | 10 |  | Voltage\Uph-e>(>) | aDipset | String | E | 10 | 3 | Voltage\Uph-e> | outserv | Real | E | 0 | 0 | 3
[30 empty] | Voltage\Uph-e>> | outserv | Real | E | 0 | 0 | 3
0
x3702 | Spannungsschutz | 3702 | 1.0-170.0;oo=9999999 | V | Uph>: Ansprechwert | Real | Setting |  |  |  | x3701 | NE | 0 |  | 3 | S | 9999999 | Voltage\Uph-e> | Usetr | Real | 1 | 0 | [6 empty] | 2 | Voltage\Uph-e> | outserv | Real | E | 1 | 0 | 9999999
[16 empty] | S | 9999999 | Voltage\Uph-e> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Uph-e> | Usetr | Real |  |  | 1 | 0
[16 empty] | E | 9999999 | Voltage\Uph-e> | outserv | Real | 0 | 1
x3703 | Spannungsschutz | 3703 | 0.00-100.00;oo=9999999 | sec | Uph>: Zeitverzögerung | Real | Setting | [10 empty] | Voltage\Uph-e> | Tdel | Real | 1 | 0 | [7 empty] | Voltage\Uph-e> | Tdel | Real |  |  | 1 | 0
x3704 | Spannungsschutz | 3704 | 1.0-170.0;oo=9999999 | V | Uph>>: Ansprechwert | Real | Setting |  |  |  | x3701 | NE | 0 |  | 3 | S | 9999999 | Voltage\Uph-e>> | Usetr | Real | 1 | 0 | [6 empty] | 2 | Voltage\Uph-e>> | outserv | Real | E | 1 | 0 | 9999999
[16 empty] | S | 9999999 | Voltage\Uph-e>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Uph-e>> | Usetr | Real |  |  | 1 | 0
[16 empty] | E | 9999999 | Voltage\Uph-e>> | outserv | Real | 0 | 1
x3705 | Spannungsschutz | 3705 | 0.00-100.00;oo=9999999 | sec | Uph>>: Zeitverzögerung | Real | Setting | [10 empty] | Voltage\Uph-e>> | Tdel | Real | 1 | 0 | [7 empty] | Voltage\Uph-e>> | Tdel | Real |  |  | 1 | 0
x3711 | Spannungsschutz | 3711 | Aus¦23;Nur Meldung¦12700;Ein¦22;U> nur melden, U>> Auslösung¦25188 |  | Betriebsart Ph-Ph-Überspannungsschutz | Enum | Setting | 0;1;2;3 | Real |  |  |  |  | 0 | 7 | E | 0 | Voltage\Uph-ph>> | outserv | Real | 0 | 1 | 3 | Voltage\Uph-ph>(>) | aDipset | String | E | 00 | 3 | Voltage\Uph-ph> | outserv | Real | E | 0 | 0 | 1
[16 empty] | E | 0 | Voltage\Uph-ph> | outserv | Real | 0 | 1 | [7 empty] | Voltage\Uph-ph>> | outserv | Real | E | 0 | 0 | 1
[16 empty] | NE | 0 | Voltage\Uph-ph>> | outserv | Real | 0 | 0 | [13 empty] | 0
[16 empty] | NE | 0 | Voltage\Uph-ph> | outserv | Real | 0 | 0 |  | Voltage\Uph-ph>(>) | aDipset | String | E | 11 | 3 | Voltage\Uph-ph> | outserv | Real | E | 0 | 0 | 2
[16 empty] | E | 1 | Voltage\Uph-ph>(>) | aDipset | String |  | 00 | [7 empty] | Voltage\Uph-ph>> | outserv | Real | E | 0 | 0 | 2
[16 empty] | E | 2 | Voltage\Uph-ph>(>) | aDipset | String |  | 11 | [13 empty] | 0
[16 empty] | E | 3 | Voltage\Uph-ph>(>) | aDipset | String |  | 10 |  | Voltage\Uph-ph>(>) | aDipset | String | E | 10 | 3 | Voltage\Uph-ph> | outserv | Real | E | 0 | 0 | 3
[30 empty] | Voltage\Uph-ph>> | outserv | Real | E | 0 | 0 | 3
0
x3712 | Spannungsschutz | 3712 | 2.0-220.0;oo=9999999 | V | Uphph>: Ansprechwert | Real | Setting |  |  |  | x3711 | NE | 0 |  | 3 | S | 9999999 | Voltage\Uph-ph> | Usetr | Real | 1 | 0 | [6 empty] | 2 | Voltage\Uph-ph> | outserv | Real | E | 1 | 0 | 9999999
[16 empty] | S | 9999999 | Voltage\Uph-ph> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Uph-ph> | Usetr | Real |  |  | 1 | 0
[16 empty] | E | 9999999 | Voltage\Uph-ph> | outserv | Real | 0 | 1
x3713 | Spannungsschutz | 3713 | 0.00-100.00;oo=9999999 | sec | Uphph>: Zeitverzögerung | Real | Setting | [10 empty] | Voltage\Uph-ph> | Tdel | Real | 1 | 0 | [7 empty] | Voltage\Uph-ph> | Tdel | Real |  |  | 1 | 0
x3714 | Spannungsschutz | 3714 | 2.0-220.0;oo=9999999 | V | Uphph>>: Ansprechwert | Real | Setting |  |  |  | x3711 | NE | 0 |  | 3 | S | 9999999 | Voltage\Uph-ph>> | Usetr | Real | 1 | 0 | [6 empty] | 2 | Voltage\Uph-ph>> | outserv | Real | E | 1 | 0 | 9999999
[16 empty] | S | 9999999 | Voltage\Uph-ph>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Uph-ph>> | Usetr | Real |  |  | 1 | 0
[16 empty] | E | 9999999 | Voltage\Uph-ph>> | outserv | Real | 0 | 1
x3715 | Spannungsschutz | 3715 | 0.00-100.00;oo=9999999 | sec | Uphph>>: Zeitverzögerung | Real | Setting | [10 empty] | Voltage\Uph-ph>> | Tdel | Real | 1 | 0 | [7 empty] | Voltage\Uph-ph>> | Tdel | Real |  |  | 1 | 0
x3721 | Spannungsschutz | 3721 | Aus¦23;Nur Meldung¦12700;Ein¦22;U> nur melden, U>> Auslösung¦25188 |  | Betriebsart 3U0 (oder Ux)-Übersp.-schutz | Enum | Setting | 0;1;2;3 | Real |  |  |  |  | 0 | 7 | E | 0 | Voltage\U0>> | outserv | Real | 0 | 1 | 3 | Voltage\U0>(>) | aDipset | String | E | 00 | 3 | Voltage\U0> | outserv | Real | E | 0 | 0 | 1
[16 empty] | E | 0 | Voltage\U0> | outserv | Real | 0 | 1 | [7 empty] | Voltage\U0>> | outserv | Real | E | 0 | 0 | 1
[16 empty] | NE | 0 | Voltage\U0>> | outserv | Real | 0 | 0 | [13 empty] | 0
[16 empty] | NE | 0 | Voltage\U0> | outserv | Real | 0 | 0 |  | Voltage\U0>(>) | aDipset | String | E | 11 | 3 | Voltage\U0> | outserv | Real | E | 0 | 0 | 2
[16 empty] | E | 1 | Voltage\U0>(>) | aDipset | String |  | 00 | [7 empty] | Voltage\U0>> | outserv | Real | E | 0 | 0 | 2
[16 empty] | E | 2 | Voltage\U0>(>) | aDipset | String |  | 11 | [13 empty] | 0
[16 empty] | E | 3 | Voltage\U0>(>) | aDipset | String |  | 10 |  | Voltage\U0>(>) | aDipset | String | E | 10 | 3 | Voltage\U0> | outserv | Real | E | 0 | 0 | 3
[30 empty] | Voltage\U0>> | outserv | Real | E | 0 | 0 | 3
0
x3722 | Spannungsschutz | 3722 | 1.0-220.0;oo=9999999 | V | 3U0>: Ansprechwert (oder Ux>) | Real | Setting | [7 empty] | 3 | S | 9999999 | Voltage\U0> | Usetr | Real | 1 | 0 | [6 empty] | 2 | Voltage\U0> | outserv | Real | E | 1 | 0 | 9999999
[16 empty] | S | 9999999 | Voltage\U0> | outserv | Real | 0 | 0 | [7 empty] | Voltage\U0> | Usetr | Real |  |  | 1 | 0
[16 empty] | E | 9999999 | Voltage\U0> | outserv | Real | 0 | 1
x3723 | Spannungsschutz | 3723 | 0.00-100.00;oo=9999999 | sec | 3U0>: Zeitverzögerung (oder Ux>) | Real | Setting | [10 empty] | Voltage\U0> | Tdel | Real | 1 | 0 | [7 empty] | Voltage\U0> | Tdel | Real |  |  | 1 | 0
x3724 | Spannungsschutz | 3724 | 1.0-220.0;oo=9999999 | V | 3U0>>: Ansprechwert (oder Ux>>) | Real | Setting | [7 empty] | 3 | S | 9999999 | Voltage\U0>> | Usetr | Real | 1 | 0 | [6 empty] | 2 | Voltage\U0>> | outserv | Real | E | 1 | 0 | 9999999
[16 empty] | S | 9999999 | Voltage\U0>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\U0>> | Usetr | Real |  |  | 1 | 0
[16 empty] | E | 9999999 | Voltage\U0>> | outserv | Real | 0 | 1
x3725 | Spannungsschutz | 3725 | 0.00-100.00;oo=9999999 | sec | 3U0>>: Zeitverzögerung (oder Ux>>) | Real | Setting | [10 empty] | Voltage\U0>> | Tdel | Real | 1 | 0 | [7 empty] | Voltage\U0>> | Tdel | Real |  |  | 1 | 0
x3731 | Spannungsschutz | 3731 | Aus¦23;Nur Meldung¦12700;Ein¦22;U> nur melden, U>> Auslösung¦25188 |  | Betriebsart Mitsystem-Übersp.-schutz | Enum | Setting | 0;1;2;3 | Real |  |  |  |  | 0 | 7 | E | 0 | Voltage\U1>> | outserv | Real | 0 | 1 | 3 | Voltage\U1>(>) | aDipset | String | E | 00 | 3 | Voltage\U1> | outserv | Real | E | 0 | 0 | 1
[16 empty] | E | 0 | Voltage\U1> | outserv | Real | 0 | 1 | [7 empty] | Voltage\U1>> | outserv | Real | E | 0 | 0 | 1
[16 empty] | NE | 0 | Voltage\U1>> | outserv | Real | 0 | 0 | [13 empty] | 0
[16 empty] | NE | 0 | Voltage\U1> | outserv | Real | 0 | 0 |  | Voltage\U1>(>) | aDipset | String | E | 11 | 3 | Voltage\U1> | outserv | Real | E | 0 | 0 | 2
[16 empty] | E | 1 | Voltage\U1>(>) | aDipset | String |  | 00 | [7 empty] | Voltage\U1>> | outserv | Real | E | 0 | 0 | 2
[16 empty] | E | 2 | Voltage\U1>(>) | aDipset | String |  | 11 | [13 empty] | 0
[16 empty] | E | 3 | Voltage\U1>(>) | aDipset | String |  | 10 |  | Voltage\U1>(>) | aDipset | String | E | 10 | 3 | Voltage\U1> | outserv | Real | E | 0 | 0 | 3
[30 empty] | Voltage\U1>> | outserv | Real | E | 0 | 0 | 3
0
x3732 | Spannungsschutz | 3732 | 2.0-220.0;oo=9999999 | V | U1>: Ansprechwert | Real | Setting |  |  |  | x3731 | NE | 0 |  | 3 | S | 9999999 | Voltage\U1> | Usetr | Real | 1 | 0 | [6 empty] | 2 | Voltage\U1> | outserv | Real | E | 1 | 0 | 9999999
[16 empty] | S | 9999999 | Voltage\U1> | outserv | Real | 0 | 0 | [7 empty] | Voltage\U1> | Usetr | Real |  |  | 1 | 0
[16 empty] | E | 9999999 | Voltage\U1> | outserv | Real | 0 | 1
x3733 | Spannungsschutz | 3733 | 0.00-100.00;oo=9999999 | sec | U1>: Zeitverzögerung | Real | Setting | [10 empty] | Voltage\U1> | Tdel | Real | 1 | 0 | [7 empty] | Voltage\U1> | Tdel | Real |  |  | 1 | 0
x3734 | Spannungsschutz | 3734 | 2.0-220.0;oo=9999999 | V | U1>>: Ansprechwert | Real | Setting |  |  |  | x3731 | NE | 0 |  | 3 | S | 9999999 | Voltage\U1>> | Usetr | Real | 1 | 0 | [6 empty] | 2 | Voltage\U1>> | outserv | Real | E | 1 | 0 | 9999999
[16 empty] | S | 9999999 | Voltage\U1>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\U1>> | Usetr | Real |  |  | 1 | 0
[16 empty] | E | 9999999 | Voltage\U1>> | outserv | Real | 0 | 1
x3735 | Spannungsschutz | 3735 | 0.00-100.00;oo=9999999 | sec | U1>>: Zeitverzögerung | Real | Setting | [10 empty] | Voltage\U1>> | Tdel | Real | 1 | 0 | [7 empty] | Voltage\U1>> | Tdel | Real |  |  | 1 | 0
x3741 | Spannungsschutz | 3741 | Aus¦23;Nur Meldung¦12700;Ein¦22;U> nur melden, U>> Auslösung¦25188 |  | Betriebsart Gegensystem-Übersp.-schutz | Enum | Setting | 0;1;2;3 | Real |  |  |  |  | 0 | 7 | E | 0 | Voltage\U2>> | outserv | Real | 0 | 1 | 3 | Voltage\U2>(>) | aDipset | String | E | 00 | 3 | Voltage\U2> | outserv | Real | E | 0 | 0 | 1
[16 empty] | E | 0 | Voltage\U2> | outserv | Real | 0 | 1 | [7 empty] | Voltage\U2>> | outserv | Real | E | 0 | 0 | 1
[16 empty] | NE | 0 | Voltage\U2>> | outserv | Real | 0 | 0 | [13 empty] | 0
[16 empty] | NE | 0 | Voltage\U2> | outserv | Real | 0 | 0 |  | Voltage\U2>(>) | aDipset | String | E | 11 | 3 | Voltage\U2> | outserv | Real | E | 0 | 0 | 2
[16 empty] | E | 1 | Voltage\U2>(>) | aDipset | String |  | 00 | [7 empty] | Voltage\U2>> | outserv | Real | E | 0 | 0 | 2
[16 empty] | E | 2 | Voltage\U2>(>) | aDipset | String |  | 11 | [13 empty] | 0
[16 empty] | E | 3 | Voltage\U2>(>) | aDipset | String |  | 10 |  | Voltage\U2>(>) | aDipset | String | E | 10 | 3 | Voltage\U2> | outserv | Real | E | 0 | 0 | 3
[30 empty] | Voltage\U2>> | outserv | Real | E | 0 | 0 | 3
0
x3742 | Spannungsschutz | 3742 | 2.0-220.0;oo=9999999 | V | U2>: Ansprechwert | Real | Setting |  |  |  | x3741 | NE | 0 |  | 3 | S | 9999999 | Voltage\U2> | Usetr | Real | 1 | 0 | [6 empty] | 2 | Voltage\U2> | outserv | Real | E | 1 | 0 | 9999999
[16 empty] | S | 9999999 | Voltage\U2> | outserv | Real | 0 | 0 | [7 empty] | Voltage\U2> | Usetr | Real |  |  | 1 | 0
[16 empty] | E | 9999999 | Voltage\U2> | outserv | Real | 0 | 1
x3743 | Spannungsschutz | 3743 | 0.00-100.00;oo=9999999 | sec | U2>: Zeitverzögerung | Real | Setting | [10 empty] | Voltage\U2> | Tdel | Real | 1 | 0 | [7 empty] | Voltage\U2> | Tdel | Real |  |  | 1 | 0
x3744 | Spannungsschutz | 3744 | 2.0-220.0;oo=9999999 | V | U2>>: Ansprechwert | Real | Setting |  |  |  | x3741 | NE | 0 |  | 3 | S | 9999999 | Voltage\U2>> | Usetr | Real | 1 | 0 | [6 empty] | 2 | Voltage\U2>> | outserv | Real | E | 1 | 0 | 9999999
[16 empty] | S | 9999999 | Voltage\U2>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\U2>> | Usetr | Real |  |  | 1 | 0
[16 empty] | E | 9999999 | Voltage\U2>> | outserv | Real | 0 | 1
x3745 | Spannungsschutz | 3745 | 0.00-100.00;oo=9999999 | sec | U2>>: Zeitverzögerung | Real | Setting | [10 empty] | Voltage\U2>> | Tdel | Real | 1 | 0 | [7 empty] | Voltage\U2>> | Tdel | Real |  |  | 1 | 0
x3751 | Spannungsschutz | 3751 | Aus¦23;Nur Meldung¦12700;Ein¦22;U< nur melden, U<< Auslösung¦25189 |  | Betriebsart Ph-E-Unterspannungsschutz | Enum | Setting | 0;1;2;3 | Real |  |  |  |  | 0 | 7 | E | 0 | Voltage\Uph-e<< | outserv | Real | 0 | 1 | 3 | Voltage\Uph-e<(<) | aDipset | String | E | 00 | 3 | Voltage\Uph-e< | outserv | Real | E | 0 | 0 | 1
[16 empty] | E | 0 | Voltage\Uph-e< | outserv | Real | 0 | 1 | [7 empty] | Voltage\Uph-e<< | outserv | Real | E | 0 | 0 | 1
[16 empty] | NE | 0 | Voltage\Uph-e<< | outserv | Real | 0 | 0 | [13 empty] | 0
[16 empty] | NE | 0 | Voltage\Uph-e< | outserv | Real | 0 | 0 |  | Voltage\Uph-e<(<) | aDipset | String | E | 11 | 3 | Voltage\Uph-e< | outserv | Real | E | 0 | 0 | 2
[16 empty] | E | 1 | Voltage\Uph-e<(<) | aDipset | String |  | 00 | [7 empty] | Voltage\Uph-e<< | outserv | Real | E | 0 | 0 | 2
[16 empty] | E | 2 | Voltage\Uph-e<(<) | aDipset | String |  | 11 | [13 empty] | 0
[16 empty] | E | 3 | Voltage\Uph-e<(<) | aDipset | String |  | 10 |  | Voltage\Uph-e<(<) | aDipset | String | E | 10 | 3 | Voltage\Uph-e< | outserv | Real | E | 0 | 0 | 3
[30 empty] | Voltage\Uph-e<< | outserv | Real | E | 0 | 0 | 3
0
x3752 | Spannungsschutz | 3752 | 1.0-100.0;0 | V | Uph<: Ansprechwert | Real | Setting |  |  |  | x3751 | NE | 0 |  | 3 | G | 0 | Voltage\Uph-e< | Usetr | Real | 1 | 0 | [6 empty] | 2 | Voltage\Uph-e< | outserv | Real | E | 1 | 0 | 0
[16 empty] | G | 0 | Voltage\Uph-e< | outserv | Real | 0 | 0 | [7 empty] | Voltage\Uph-e< | Usetr | Real |  |  | 1 | 0
[16 empty] | E | 0 | Voltage\Uph-e< | outserv | Real | 0 | 1
x3753 | Spannungsschutz | 3753 | 0.00-100.00;oo=9999999 | sec | Uph<: Zeitverzögerung | Real | Setting | [10 empty] | Voltage\Uph-e< | Tdel | Real | 1 | 0 | [7 empty] | Voltage\Uph-e< | Tdel | Real |  |  | 1 | 0
x3754 | Spannungsschutz | 3754 | 1.0-100.0;0 | V | Uph<<: Ansprechwert | Real | Setting |  |  |  | x3751 | NE | 0 |  | 3 | G | 0 | Voltage\Uph-e<< | Usetr | Real | 1 | 0 | [6 empty] | 2 | Voltage\Uph-e<< | outserv | Real | E | 1 | 0 | 0
[16 empty] | G | 0 | Voltage\Uph-e<< | outserv | Real | 0 | 0 | [7 empty] | Voltage\Uph-e<< | Usetr | Real |  |  | 1 | 0
[16 empty] | E | 0 | Voltage\Uph-e<< | outserv | Real | 0 | 1
x3755 | Spannungsschutz | 3755 | 0.00-100.00;oo=9999999 | sec | Uph<<: Zeitverzögerung | Real | Setting | [10 empty] | Voltage\Uph-e<< | Tdel | Real | 1 | 0 | [7 empty] | Voltage\Uph-e<< | Tdel | Real |  |  | 1 | 0
x3761 | Spannungsschutz | 3761 | Aus¦23;Nur Meldung¦12700;Ein¦22;U< nur melden, U<< Auslösung¦25189 |  | Betriebsart Ph-Ph-Unterspannungsschutz | Enum | Setting | 0;1;2;3 | Real |  |  |  |  | 0 | 7 | E | 0 | Voltage\Uph-ph<< | outserv | Real | 0 | 1 | 3 | Voltage\Uph-ph<(<) | aDipset | String | E | 00 | 3 | Voltage\Uph-ph< | outserv | Real | E | 0 | 0 | 1
[16 empty] | E | 0 | Voltage\Uph-ph< | outserv | Real | 0 | 1 | [7 empty] | Voltage\Uph-ph<< | outserv | Real | E | 0 | 0 | 1
[16 empty] | NE | 0 | Voltage\Uph-ph<< | outserv | Real | 0 | 0 | [13 empty] | 0
[16 empty] | NE | 0 | Voltage\Uph-ph< | outserv | Real | 0 | 0 |  | Voltage\Uph-ph<(<) | aDipset | String | E | 11 | 3 | Voltage\Uph-ph< | outserv | Real | E | 0 | 0 | 2
[16 empty] | E | 1 | Voltage\Uph-ph<(<) | aDipset | String |  | 00 | [7 empty] | Voltage\Uph-ph<< | outserv | Real | E | 0 | 0 | 2
[16 empty] | E | 2 | Voltage\Uph-ph<(<) | aDipset | String |  | 11 | [13 empty] | 0
[16 empty] | E | 3 | Voltage\Uph-ph<(<) | aDipset | String |  | 10 |  | Voltage\Uph-ph<(<) | aDipset | String | E | 10 | 3 | Voltage\Uph-ph< | outserv | Real | E | 0 | 0 | 3
[30 empty] | Voltage\Uph-ph<< | outserv | Real | E | 0 | 0 | 3
0
x3762 | Spannungsschutz | 3762 | 1.0-175.0;0 | V | Uphph<: Ansprechwert | Real | Setting |  |  |  | x3761 | NE | 0 |  | 3 | G | 0 | Voltage\Uph-ph< | Usetr | Real | 1 | 0 | [6 empty] | 2 | Voltage\Uph-ph< | outserv | Real | E | 1 | 0 | 0
[16 empty] | G | 0 | Voltage\Uph-ph< | outserv | Real | 0 | 0 | [7 empty] | Voltage\Uph-ph< | Usetr | Real |  |  | 1 | 0
[16 empty] | E | 0 | Voltage\Uph-ph< | outserv | Real | 0 | 1
x3763 | Spannungsschutz | 3763 | 0.00-100.00;oo=9999999 | sec | Uphph<: Zeitverzögerung | Real | Setting | [10 empty] | Voltage\Uph-ph< | Tdel | Real | 1 | 0 | [7 empty] | Voltage\Uph-ph< | Tdel | Real |  |  | 1 | 0
x3764 | Spannungsschutz | 3764 | 1.0-175.0;0 | V | Uphph<<: Ansprechwert | Real | Setting |  |  |  | x3761 | NE | 0 |  | 3 | G | 0 | Voltage\Uph-ph<< | Usetr | Real | 1 | 0 | [6 empty] | 2 | Voltage\Uph-ph<< | outserv | Real | E | 1 | 0 | 0
[16 empty] | G | 0 | Voltage\Uph-ph<< | outserv | Real | 0 | 0 | [7 empty] | Voltage\Uph-ph<< | Usetr | Real |  |  | 1 | 0
[16 empty] | E | 0 | Voltage\Uph-ph<< | outserv | Real | 0 | 1
x3765 | Spannungsschutz | 3765 | 0.00-100.00;oo=9999999 | sec | Uphph<<: Zeitverzögerung | Real | Setting | [10 empty] | Voltage\Uph-ph<< | Tdel | Real | 1 | 0 | [7 empty] | Voltage\Uph-ph<< | Tdel | Real |  |  | 1 | 0
x3771 | Spannungsschutz | 3771 | Aus¦23;Nur Meldung¦12700;Ein¦22;U< nur melden, U<< Auslösung¦25188 |  | Betriebsart Mitsystem-Übersp.-schutz | Enum | Setting | 0;1;2;3 | Real |  |  |  |  | 0 | 7 | E | 0 | Voltage\U1<< | outserv | Real | 0 | 1 | 3 | Voltage\U1<(<) | aDipset | String | E | 00 | 3 | Voltage\U1< | outserv | Real | E | 0 | 0 | 1
[16 empty] | E | 0 | Voltage\U1< | outserv | Real | 0 | 1 | [7 empty] | Voltage\U1<< | outserv | Real | E | 0 | 0 | 1
[16 empty] | NE | 0 | Voltage\U1<< | outserv | Real | 0 | 0 | [13 empty] | 0
[16 empty] | NE | 0 | Voltage\U1< | outserv | Real | 0 | 0 |  | Voltage\U1<(<) | aDipset | String | E | 11 | 3 | Voltage\U1< | outserv | Real | E | 0 | 0 | 2
[16 empty] | E | 1 | Voltage\U1<(<) | aDipset | String |  | 00 | [7 empty] | Voltage\U1<< | outserv | Real | E | 0 | 0 | 2
[16 empty] | E | 2 | Voltage\U1<(<) | aDipset | String |  | 11 | [13 empty] | 0
[16 empty] | E | 3 | Voltage\U1<(<) | aDipset | String |  | 10 |  | Voltage\U1<(<) | aDipset | String | E | 10 | 3 | Voltage\U1< | outserv | Real | E | 0 | 0 | 3
[30 empty] | Voltage\U1<< | outserv | Real | E | 0 | 0 | 3
0
x3772 | Spannungsschutz | 3772 | 1.0-100.0;0 | V | U1<: Ansprechwert | Real | Setting |  |  |  | x3771 | NE | 0 |  | 3 | G | 0 | Voltage\U1< | Usetr | Real | 1 | 0 | [6 empty] | 2 | Voltage\U1< | outserv | Real | E | 1 | 0 | 0
[16 empty] | G | 0 | Voltage\U1< | outserv | Real | 0 | 0 | [7 empty] | Voltage\U1< | Usetr | Real |  |  | 1 | 0
[16 empty] | E | 0 | Voltage\U1< | outserv | Real | 0 | 1
x3773 | Spannungsschutz | 3773 | 0.00-100.00;oo=9999999 | sec | U1<: Zeitverzögerung | Real | Setting | [10 empty] | Voltage\U1< | Tdel | Real | 1 | 0 | [7 empty] | Voltage\U1< | Tdel | Real |  |  | 1 | 0
x3774 | Spannungsschutz | 3774 | 1.0-100.0;0 | V | U1<<: Ansprechwert | Real | Setting |  |  |  | x3771 | NE | 0 |  | 3 | G | 0 | Voltage\U1<< | Usetr | Real | 1 | 0 | [6 empty] | 2 | Voltage\U1<< | outserv | Real | E | 1 | 0 | 0
[16 empty] | G | 0 | Voltage\U1<< | outserv | Real | 0 | 0 | [7 empty] | Voltage\U1<< | Usetr | Real |  |  | 1 | 0
[16 empty] | E | 0 | Voltage\U1<< | outserv | Real | 0 | 1
x3775 | Spannungsschutz | 3775 | 0.00-100.00;oo=9999999 | sec | U1<<: Zeitverzögerung | Real | Setting | [10 empty] | Voltage\U1<< | Tdel | Real | 1 | 0 | [7 empty] | Voltage\U1<< | Tdel | Real |  |  | 1 | 0
_END_