## Mapping
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37
StationWare | [6 empty] | Common |  |  | Import | [12 empty] | Export
[8 empty] | Enumeration |  | Pre-Condition |  |  |  |  | Instruction | [7 empty] | Pre-Condition | [5 empty] | Instruction
Key | Chapter | Display name | Range | Unit | Description | Type | Group | Mapping | Type |  | Setting | Operator | Value | Default |  | Operator | Value | Target | Parameter | Type | Scale | Offset |  | Source | Parameter | Type | Operator | Value |  | Source | Parameter | Type | Operator | Value | Scale | Offset
x112 | Funktionsumfang | 112 | vorhanden¦8;nicht vorhanden¦7 |  | Differentialschutz | Enum | Configuration | 0;1 | Real |  |  |  |  | 0 |  | E | 1 | Differential | outserv | Real | 0 | 1
x126 | Funktionsumfang | 126 | nicht vorhanden¦7;UMZ/AMZ (IEC-Kurven)¦25103 |  | Überstromzeitschutz | Enum | Configuration | 1;0 | Real |  |  |  |  | 0 |  | E | 1 | Overcurrent | outserv | Real | 0 | 1
x204 | Anlagendaten 1 | 204 | 80-125:1 | V | Wandler-Nennspannung, sekundär | Real | Configuration | [6 empty] | 100 |  |  |  | Measurement | Unom | Real | 1 | 0 | [7 empty] | Measurement | Unom | Real |  |  | 1 | 0
x1201 | Differentialschutz | 1201 | Aus¦23;Ein¦22 |  | Differentialschutz | Enum | Configuration | 1;0 | Real |  | x112 | E | 0 | 0 |  |  |  | Differential | outserv | Real | 1 | 0 |  | x112 |  |  | E | 0 |  | Differential | outserv | Real |  |  | 1 | 0
x1210 | Differentialschutz | 1210 | 0.50-100.00:0.01 | A | I-DIFF>: Ansprechwert | Real | Configuration | [6 empty] | 0.3 |  |  |  | Differential\Differential | Idiffr | Real | 1 | 0 |  | Differential;Differential\Differential;x112 | outserv;outserv | Real;Real | E;E;E | 0;0;0 |  | Differential\Differential | Idiffr | Real |  |  | 1 | 0
x1217A | Differentialschutz | 1217A | 0.00-60.00:0.01;oo=9999999 | s | T-I-DIF> : Zeitverzögerung | Real | Configuration | [6 empty] | 0 |  |  |  | Differential\Differential | Tset | Real | 1 | 0 |  | Differential;Differential\Differential;x112 | outserv;outserv | Real;Real | E;E;E | 0;0;0 |  | Differential\Differential | Tset | Real |  |  | 1 | 0
x1219A | Differentialschutz | 1219A | 0.50-100.00:0.01;0 | A | Min. lokaler Strom z. Freig. d. DIFF-AUS | Real | Configuration | [6 empty] | 0 | 3 | GE | 0.1 | Differential\Diff Release | Ipsetr | Real | 1 | 0 | 2 | Differential;Differential\Diff Release;x112 | outserv;outserv | Real;Real | E;E;E | 0;0;0 |  | Differential\Diff Release | Ipsetr | Real |  |  | 1 | 0
[16 empty] | GE | 0.1 | Differential\Diff Release | outserv | Real | 0 | 0 |  | Differential;Differential\Diff Release;x112 | outserv;outserv | Real;Real | E;E;E | 0;1;0 | [7 empty] | 0
[16 empty] | S | 0.1 | Differential\Diff Release | outserv | Real | 0 | 1
x1233 | Differentialschutz | 1233 | 4.0-500.0:0.1;oo=9999999 | A | I-DIFF>>: Ansprechwert | Real | Configuration | [6 empty] | 1.2 |  |  |  | Differential\Differential | Idiffunrestr | Real | 1 | 0 |  | Differential;Differential\Differential;x112 | outserv;outserv | Real;Real | E;E;E | 0;0;0 |  | Differential\Differential | Idiffunrestr | Real |  |  | 1 | 0
x2301 | Differentialschutz | 2301 | Aus¦23;Ein¦22 |  | Einschaltrush-Stabilisierung | Enum | Configuration | 1;0 | [5 empty] | 0 |  |  |  | Differential\Differential | harmblockdisable | Real | 1 | 0 |  | Differential;Differential\Differential;x112 | outserv;outserv | Real;Real | E;E;E | 0;0;0 |  | Differential\Differential | harmblockdisable | Real |  |  | 1 | 0
x2302 | Differentialschutz | 2302 | 10-45:1 | % | Anteil 2.Harmonische für Rusherkennung | Real | Configuration | [6 empty] | 15 |  |  |  | Differential\Differential | H2threshold | Real | 1 | 0 |  | Differential;Differential\Differential;x112 | outserv;outserv | Real;Real | E;E;E | 0;0;0 |  | Differential\Differential | H2threshold | Real |  |  | 1 | 0
x2303 | Differentialschutz | 2303 | Nein¦24;Ja¦25 |  | Blockieren durch Crossblock-Funktion | Enum | Configuration | 0;1 | [5 empty] | 0 |  |  |  | Differential\Differential | h2interblock | Real | 1 | 0 |  | Differential;Differential\Differential;x112 | outserv;outserv | Real;Real | E;E;E | 0;0;0 |  | Differential\Differential | h2interblock | Real |  |  | 1 | 0
x2305 | Differentialschutz | 2305 | 5.5-125.0:0.1 | A | Maximaler Inrush-Peak | Real | Configuration | [6 empty] | 15 |  |  |  | Differential\Differential | hblckdisthrr | Real | 1 | 0 |  | Differential;Differential\Differential;x112 | outserv;outserv | Real;Real | E;E;E | 0;0;0 |  | Differential\Differential | hblckdisthrr | Real |  |  | 1 | 0
x2601 | Überstromzeitschutz | 2601 | Ein¦22;Nur als Notfunktion¦25262;Aus¦23 |  | Betriebsart | Enum | Configuration | 0;1;2 | Real |  | x126 | E | 0 | 0 | 4 | NE | 2 | Overcurrent | outserv | Real | 0 | 0 | 2 | Overcurrent;x126 | outserv | Real | E;E | 0;0 | 2 | Overcurrent\Emergency Only | outserv | Real | E | 1 | 0 | 0
[16 empty] | E | 2 | Overcurrent | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\Emergency Only | outserv | Real | E | 1 | 0 | 1
[16 empty] | NE | 1 | Overcurrent\Emergency Only | outserv | Real | 0 | 1 |  | Overcurrent;x126 | outserv | Real | E;E | 1;0 | [7 empty] | 2
[16 empty] | E | 1 | Overcurrent\Emergency Only | outserv | Real | 0 | 0
x2610 | Überstromzeitschutz | 2610 | 0.25-250.00:0.01;oo=9999999 | A | Iph>>: Ansprechwert | Real | Configuration | [6 empty] | 2 | 3 | NE | 9999999 | Overcurrent\Iph>> | Ipsetr | Real | 1 | 0 |  | Overcurrent;x126 | outserv | Real | E;E | 0;0 | 2 | Overcurrent\Iph>> | outserv | Real | E | 1 |  | 9999999
[16 empty] | NE | 9999999 | Overcurrent\Iph>> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\Iph>> | Ipsetr | Real |  |  | 1 | 0
[16 empty] | E | 9999999 | Overcurrent\Iph>> | outserv | Real | 0 | 1
x2611 | Überstromzeitschutz | 2611 | 0.00-30.00:0.01;oo=9999999 | s | Iph>>: Zeitverzögerung | Real | Configuration | [6 empty] | 0.3 |  |  |  | Overcurrent\Iph>> | Tset | Real | 1 | 0 |  | Overcurrent;x126 | outserv | Real | E;E | 0;0 |  | Overcurrent\Iph>> | Tset | Real |  |  | 1 | 0
x2612 | Überstromzeitschutz | 2612 | 0.25-125.00:0.01;oo=9999999 | A | 3I0>>: Ansprechwert | Real | Configuration | [6 empty] | 0.5 | 3 | NE | 9999999 | Overcurrent\3I0>> | Ipsetr | Real | 1 | 0 |  | Overcurrent;x126 | outserv | Real | E;E | 0;0 | 2 | Overcurrent\3I0>> | outserv | Real | E | 1 |  | 9999999
[16 empty] | NE | 9999999 | Overcurrent\3I0>> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\3I0>> | Ipsetr | Real |  |  | 1 | 0
[16 empty] | E | 9999999 | Overcurrent\3I0>> | outserv | Real | 0 | 1
x2613 | Überstromzeitschutz | 2613 | 0.00-30.00:0.01;oo=9999999 | s | 3I0>>: Zeitverzögerung | Real | Configuration | [6 empty] | 2 |  |  |  | Overcurrent\3I0>> | Tset | Real | 1 | 0 |  | Overcurrent;x126 | outserv | Real | E;E | 0;0 |  | Overcurrent\3I0>> | Tset | Real |  |  | 1 | 0
x2620 | Überstromzeitschutz | 2620 | 0.25-250.00:0.01;oo=9999999 | A | Iph>: Ansprechwert | Real | Configuration | [6 empty] | 1.5 | 3 | NE | 9999999 | Overcurrent\Iph> | Ipsetr | Real | 1 | 0 |  | Overcurrent;x126 | outserv | Real | E;E | 0;0 | 2 | Overcurrent\Iph> | outserv | Real | E | 1 |  | 9999999
[16 empty] | NE | 9999999 | Overcurrent\Iph> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\Iph> | Ipsetr | Real |  |  | 1 | 0
[16 empty] | E | 9999999 | Overcurrent\Iph> | outserv | Real | 0 | 1
x2621 | Überstromzeitschutz | 2621 | 0.00-30.00:0.01;oo=9999999 | s | Iph>: Zeitverzögerung | Real | Configuration | [6 empty] | 0.5 |  |  |  | Overcurrent\Iph> | Tset | Real | 1 | 0 |  | Overcurrent;x126 | outserv | Real | E;E | 0;0 |  | Overcurrent\Iph> | Tset | Real |  |  | 1 | 0
x2622 | Überstromzeitschutz | 2622 | 0.25-125.00:0.01;oo=9999999 | A | 3I0>: Ansprechwert | Real | Configuration | [6 empty] | 0.2 | 3 | NE | 9999999 | Overcurrent\3I0> | Ipsetr | Real | 1 | 0 |  | Overcurrent;x126 | outserv | Real | E;E | 0;0 | 2 | Overcurrent\3I0> | outserv | Real | E | 1 |  | 9999999
[16 empty] | NE | 9999999 | Overcurrent\3I0> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\3I0> | Ipsetr | Real |  |  | 1 | 0
[16 empty] | E | 9999999 | Overcurrent\3I0> | outserv | Real | 0 | 1
x2623 | Überstromzeitschutz | 2623 | 0.00-30.00:0.01;oo=9999999 | s | 3I0>: Zeitverzögerung | Real | Configuration | [6 empty] | 2 |  |  |  | Overcurrent\3I0> | Tset | Real | 1 | 0 |  | Overcurrent;x126 | outserv | Real | E;E | 0;0 |  | Overcurrent\3I0> | Tset | Real |  |  | 1 | 0
x2640 | Überstromzeitschutz | 2640 | 0.50-20.00:0.01;oo=9999999 | A | IP: Ansprechwert | Real | Configuration | [6 empty] | 9999999 | 3 | NE | 9999999 | Overcurrent\Ip> | Ipsetr | Real | 1 | 0 |  | Overcurrent;x126 | outserv | Real | E;E | 0;0 | 2 | Overcurrent\Ip> | outserv | Real | E | 1 |  | 9999999
[16 empty] | NE | 9999999 | Overcurrent\Ip> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\Ip> | Ipsetr | Real |  |  | 1 | 0
[16 empty] | E | 9999999 | Overcurrent\Ip> | outserv | Real | 0 | 1
x2642 | Überstromzeitschutz | 2642 | 0.05-3.00:0.01;oo=9999999 | s | IP: AMZ-Zeit für IEC-Kennlinien T IP | Real | Configuration | [6 empty] | 0.5 |  |  |  | Overcurrent\Ip> | Tpset | Real | 1 | 0 |  | Overcurrent;x126 | outserv | Real | E;E | 0;0 |  | Overcurrent\Ip> | Tpset | Real |  |  | 1 | 0
x2646 | Überstromzeitschutz | 2646 | 0.00-30.00:0.01 | s | IP: AMZ-Zusatzverzögerung T IPverz | Real | Configuration | [6 empty] | 0 |  |  |  | Overcurrent\Ip> | Tadder | Real | 1 | 0 |  | Overcurrent;x126 | outserv | Real | E;E | 0;0 |  | Overcurrent\Ip> | Tadder | Real |  |  | 1 | 0
x2650 | Überstromzeitschutz | 2650 | 0.25-20.00:0.01;oo=9999999 | A | 3I0P: Ansprechwert | Real | Configuration | [6 empty] | 9999999 | 3 | NE | 9999999 | Overcurrent\3I0p | Ipsetr | Real | 1 | 0 |  | Overcurrent;x126 | outserv | Real | E;E | 0;0 | 2 | Overcurrent\3I0p | outserv | Real | E | 1 |  | 9999999
[16 empty] | NE | 9999999 | Overcurrent\3I0p | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\3I0p | Ipsetr | Real |  |  | 1 | 0
[16 empty] | E | 9999999 | Overcurrent\3I0p | outserv | Real | 0 | 1
x2652 | Überstromzeitschutz | 2652 | 0.05-3.00:0.01;oo=9999999 | s | 3I0P: AMZ-Zeit (IEC-Kennlinien) T 3I0P | Real | Configuration | [6 empty] | 0.5 |  |  |  | Overcurrent\3I0p | Tpset | Real | 1 | 0 |  | Overcurrent;x126 | outserv | Real | E;E | 0;0 |  | Overcurrent\3I0p | Tpset | Real |  |  | 1 | 0
x2656 | Überstromzeitschutz | 2656 | 0.00-30.00:0.01 | s | 3I0P: AMZ-Zusatzverzögerung T 3I0Pverz | Real | Configuration | [6 empty] | 0 |  |  |  | Overcurrent\3I0p | Tadder | Real | 1 | 0 |  | Overcurrent;x126 | outserv | Real | E;E | 0;0 |  | Overcurrent\3I0p | Tadder | Real |  |  | 1 | 0
x2660 | Überstromzeitschutz | 2660 | Invers¦12559;Stark invers¦12560;Extrem invers¦12561;AMZ Langzeit¦25126 |  | IEC-Kennlinie | Enum | Configuration | IEC Normal Inverse;IEC Very Inverse;IEC Extremely Inverse;IEC Long-Time Inverse | String | [5 empty] | 4 |  |  | Overcurrent\Ip> | pcharac |  |  |  | 4 | Overcurrent;Overcurrent\Ip>;x126 | outserv;outserv | Real;Real | E;E;E | 0;0;0 |  | Overcurrent\Ip> | pcharac |  | SW | IEC
[18 empty] | Overcurrent\Ip> Dir | pcharac |  |  |  |  | Overcurrent;Overcurrent\Ip> Dir;x126 | outserv;outserv | Real;Real | E;E;E | 0;0;0 |  | Overcurrent\Ip> Dir | pcharac |  | SW | IEC
[18 empty] | Overcurrent\3I0p | pcharac |  |  |  |  | Overcurrent;Overcurrent\3I0p;x126 | outserv;outserv | Real;Real | E;E;E | 0;0;0 |  | Overcurrent\3I0p | pcharac |  | SW | IEC
[18 empty] | Overcurrent\3I0p Dir | pcharac |  |  |  |  | Overcurrent;Overcurrent\3I0p Dir;x126 | outserv;outserv | Real;Real | E;E;E | 0;0;0 |  | Overcurrent\3I0p Dir | pcharac |  | SW | IEC
x2680 | Überstromzeitschutz | 2680 | ungerichtet¦12516;vorwärts¦12514;rückwärts¦12515 |  | Richtung der gerichteten Stufe Iph> | Enum | Configuration | 0;1;2 | Real |  |  |  |  | 0 |  |  |  | Overcurrent\Iph> Dir | idir | Real | 1 | 0 |  | Overcurrent;x126 | outserv | Real | E;E | 0;0 |  | Overcurrent\Iph> Dir | idir | Real |  |  | 1 | 0
x2681 | Überstromzeitschutz | 2681 | 0.25-250.00:0.01;oo=9999999 | A | Iph> gerichtet: Ansprechwert | Real | Configuration | [6 empty] | 1.5 | 3 | NE | 9999999 | Overcurrent\Iph> Dir | Ipsetr | Real | 1 | 0 |  | Overcurrent;x126 | outserv | Real | E;E | 0;0 | 2 | Overcurrent\Iph> Dir | outserv | Real | E | 1 |  | 9999999
[16 empty] | NE | 9999999 | Overcurrent\Iph> Dir | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\Iph> Dir | Ipsetr | Real |  |  | 1 | 0
[16 empty] | E | 9999999 | Overcurrent\Iph> Dir | outserv | Real | 0 | 1
x2682 | Überstromzeitschutz | 2682 | 0.00-30.00:0.01;oo=9999999 | s | Iph> gerichtet: Zeitverzögerung | Real | Configuration | [6 empty] | 0.5 |  |  |  | Overcurrent\Iph> Dir | Tset | Real | 1 | 0 |  | Overcurrent;x126 | outserv | Real | E;E | 0;0 |  | Overcurrent\Iph> Dir | Tset | Real |  |  | 1 | 0
x2683 | Überstromzeitschutz | 2683 | ungerichtet¦12516;vorwärts¦12514;rückwärts¦12515 |  | Richtung der gerichteten Stufe 3I0> | Enum | Configuration | 0;1;2 | Real |  |  |  |  | 0 |  |  |  | Overcurrent\3I0> Dir | idir | Real | 1 | 0 |  | Overcurrent;x126 | outserv | Real | E;E | 0;0 |  | Overcurrent\3I0> Dir | idir | Real |  |  | 1 | 0
x2684 | Überstromzeitschutz | 2684 | 0.25-125.00:0.01;oo=9999999 | A | 3I0> gerichtet: Ansprechwert | Real | Configuration | [6 empty] | 0.2 | 3 | NE | 9999999 | Overcurrent\3I0> Dir | Ipsetr | Real | 1 | 0 |  | Overcurrent;x126 | outserv | Real | E;E | 0;0 | 2 | Overcurrent\3I0> Dir | outserv | Real | E | 1 |  | 9999999
[16 empty] | NE | 9999999 | Overcurrent\3I0> Dir | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\3I0> Dir | Ipsetr | Real |  |  | 1 | 0
[16 empty] | E | 9999999 | Overcurrent\3I0> Dir | outserv | Real | 0 | 1
x2685 | Überstromzeitschutz | 2685 | 0.00-30.00:0.01;oo=9999999 | s | 3I0> gerichtet: Zeitverzögerung | Real | Configuration | [6 empty] | 2 |  |  |  | Overcurrent\3I0> Dir | Tset | Real | 1 | 0 |  | Overcurrent;x126 | outserv | Real | E;E | 0;0 |  | Overcurrent\3I0> Dir | Tset | Real |  |  | 1 | 0
x2688 | Überstromzeitschutz | 2688 | vorwärts¦12514;rückwärts¦12515 |  | Richtung der gerichteten Stufe IP | Enum | Configuration | 1;2 | Real |  |  |  |  | 1 |  |  |  | Overcurrent\Ip> Dir | idir | Real | 1 | 0 |  | Overcurrent;x126 | outserv | Real | E;E | 0;0 |  | Overcurrent\Ip> Dir | idir | Real |  |  | 1 | 0
x2689 | Überstromzeitschutz | 2689 | 0.50-20.00:0.01;oo=9999999 | A | IP ger.: Ansprechwert | Real | Configuration | [6 empty] | 9999999 | 3 | NE | 9999999 | Overcurrent\Ip> Dir | Ipsetr | Real | 1 | 0 |  | Overcurrent;x126 | outserv | Real | E;E | 0;0 | 2 | Overcurrent\Ip> Dir | outserv | Real | E | 1 |  | 9999999
[16 empty] | NE | 9999999 | Overcurrent\Ip> Dir | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\Ip> Dir | Ipsetr | Real |  |  | 1 | 0
[16 empty] | E | 9999999 | Overcurrent\Ip> Dir | outserv | Real | 0 | 1
x2690 | Überstromzeitschutz | 2690 | 0.05-3.00:0.01;oo=9999999 | s | IP ger.: AMZ-Zeit für IEC-Kennl. T IP | Real | Configuration | [6 empty] | 0.5 |  |  |  | Overcurrent\Ip> Dir | Tpset | Real | 1 | 0 |  | Overcurrent;x126 | outserv | Real | E;E | 0;0 |  | Overcurrent\Ip> Dir | Tpset | Real |  |  | 1 | 0
x2692 | Überstromzeitschutz | 2692 | 0.00-30.00:0.01 | s | IP ger.: AMZ-Zusatzverzögerung T IPverz | Real | Configuration | [6 empty] | 0 |  |  |  | Overcurrent\Ip> Dir | Tadder | Real | 1 | 0 |  | Overcurrent;x126 | outserv | Real | E;E | 0;0 |  | Overcurrent\Ip> Dir | Tadder | Real |  |  | 1 | 0
x2693 | Überstromzeitschutz | 2693 | vorwärts¦12514;rückwärts¦12515 |  | Richtung der gerichteten Stufe 3I0P | Enum | Configuration | 1;2 | Real |  |  |  |  | 1 |  |  |  | Overcurrent\3I0p Dir | idir | Real | 1 | 0 |  | Overcurrent;x126 | outserv | Real | E;E | 0;0 |  | Overcurrent\3I0p Dir | idir | Real |  |  | 1 | 0
x2694 | Überstromzeitschutz | 2694 | 0.25-20.00:0.01;oo=9999999 | A | 3I0P ger.: Ansprechwert | Real | Configuration | [6 empty] | 9999999 | 3 | NE | 9999999 | Overcurrent\3I0p Dir | Ipsetr | Real | 1 | 0 |  | Overcurrent;x126 | outserv | Real | E;E | 0;0 | 2 | Overcurrent\3I0p Dir | outserv | Real | E | 1 |  | 9999999
[16 empty] | NE | 9999999 | Overcurrent\3I0p Dir | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\3I0p Dir | Ipsetr | Real |  |  | 1 | 0
[16 empty] | E | 9999999 | Overcurrent\3I0p Dir | outserv | Real | 0 | 1
x2695 | Überstromzeitschutz | 2695 | 0.05-3.00:0.01;oo=9999999 | s | 3I0P ger: AMZ-Zeit für IEC-Kennl. T 3I0P | Real | Configuration | [6 empty] | 0.5 |  |  |  | Overcurrent\3I0p Dir | Tpset | Real | 1 | 0 |  | Overcurrent;x126 | outserv | Real | E;E | 0;0 |  | Overcurrent\3I0p Dir | Tpset | Real |  |  | 1 | 0
x2697 | Überstromzeitschutz | 2697 | 0.00-30.00:0.01 | s | 3I0P ger.: AMZ-Zusatzverzög. T 3I0Pverz | Real | Configuration | [6 empty] | 0 |  |  |  | Overcurrent\3I0p Dir | Tadder | Real | 1 | 0 |  | Overcurrent;x126 | outserv | Real | E;E | 0;0 |  | Overcurrent\3I0p Dir | Tadder | Real |  |  | 1 | 0
_END_