## Mapping
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37
StationWare | [6 empty] | Common |  |  | Import | [12 empty] | Export
[8 empty] | Enumeration |  | Pre-Condition |  |  |  |  | Instruction | [7 empty] | Pre-Condition | [5 empty] | Instruction
Key | Chapter | Display name | Range | Unit | Description | Type | Group | Mapping | Type |  | Setting | Operator | Value | Default |  | Operator | Value | Target | Parameter | Type | Scale | Offset |  | Source | Parameter | Type | Operator | Value |  | Source | Parameter | Type | Operator | Value | Scale | Offset
Setting_u007C_11_u002E_931_u002E_8881_u002E_115 | Power system->Meas.point I-3ph 1->CT 3-phase->General | 11.931.8881.115 | not assigned¦not assigned;3-phase + IN¦3-phase + IN;3-phase¦3-phase;3-phase + IN-separate¦3-phase + IN-separate;3-phase, 2 primary CT¦3-phase, 2 primary CT;3ph,2prim.CT + IN-sep¦3ph,2prim.CT + IN-sep;2ph, 2p. CT + IN-sep¦2ph, 2p. CT + IN-sep;2 phase + IN¦2-phase + IN |  | CT connection [read-only] | Enum | Configuration | 0;0;0;1;0;1;1;0 | Real
Setting_u007C_11_u002E_931_u002E_8881_u002E_101 | Power system->Meas.point I-3ph 1->CT 3-phase->CT phases | 11.931.8881.101 | 1-100000:0.1 | A | Rated primary current [read-only] | Real | Configuration
Setting_u007C_11_u002E_931_u002E_8881_u002E_102 | Power system->Meas.point I-3ph 1->CT 3-phase->CT phases | 11.931.8881.102 | 1 A¦1A;5 A¦5A |  | Rated secondary current | Enum | Configuration | 1;5 | Real | 2 | Setting_u007C_11_u002E_931_u002E_8881_u002E_115 | E | 1 |  |  |  |  | Measurement | Inom | Real | 1 | 0 | [7 empty] | Measurement | Inom | Real |  |  | 1 | 0
[11 empty] | Setting_u007C_11_u002E_931_u002E_8881_u002E_115 | E | 0 |  | 2 |  |  | Measurement | Inom | Real | 1 | 0
[18 empty] | Measure IGnd | Inom | Real | 1 | 0
Setting_u007C_11_u002E_931_u002E_8881_u002E_104 | Power system->Meas.point I-3ph 1->CT 3-phase->CT IN | 11.931.8881.104 | 1-100000:0.1 | A | Rated primary current [read-only] | Real | Configuration
Setting_u007C_11_u002E_931_u002E_8881_u002E_105 | Power system->Meas.point I-3ph 1->CT 3-phase->CT IN | 11.931.8881.105 | 1 A¦1A;5 A¦5A |  | Rated secondary current | Enum | Configuration | 1;5 | Real |  | Setting_u007C_11_u002E_931_u002E_8881_u002E_115 | E | 1 |  |  |  |  | Measure IGnd | Inom | Real | 1 | 0 | [7 empty] | Measure IGnd | Inom | Real |  |  | 1 | 0
Setting_u007C_11_u002E_941_u002E_8911_u002E_102 | Power system->Meas.point V-3ph 1->VT 3-phase | 11.941.8911.102 | 80-230:1 | V | Rated secondary voltage [read-only] | Real | Configuration | [10 empty] | Measurement | Unom | Real | 1 | 0 | [7 empty] | Measurement | Unom | Real |  |  | 1 | 0
Setting_u007C_821_u002E_1941_u002E_661_u002E_1 | VI 3ph 1->50/51 OC-3ph-B1->Definite-T 1 | 821.1941.661.1 | off¦Off;on¦On;test¦Test |  | Mode | Enum | SettingsGroups | 0;1;2 | Real | [5 empty] | 3 | E | 0 | Overcurrent Phases\Definite-T 1 | outserv | Real | 0 | 1 | [6 empty] | 2 | Overcurrent Phases\Definite-T 1 | outserv | Real | E | 0 | 0 | 1
[16 empty] | E | 1 | Overcurrent Phases\Definite-T 1 | outserv | Real | 0 | 0 | [7 empty] | Overcurrent Phases\Definite-T 1 | outserv | Real | E | 1 | 0 | 0
[16 empty] | E | 2 | Overcurrent Phases\Definite-T 1 | outserv | Real | 0 | 0
Setting_u007C_821_u002E_1941_u002E_661_u002E_3 | VI 3ph 1->50/51 OC-3ph-B1->Definite-T 1 | 821.1941.661.3 | 30-35000:1 | A | Threshold | Real | SettingsGroups | [10 empty] | Overcurrent Phases\Definite-T 1 | Ipset | Real | /Setting_u007C_11_u002E_931_u002E_8881_u002E_101 | 0 | [7 empty] | Overcurrent Phases\Definite-T 1 | cpIpset | Real |  |  | 1 | 0
Setting_u007C_821_u002E_1941_u002E_661_u002E_6 | VI 3ph 1->50/51 OC-3ph-B1->Definite-T 1 | 821.1941.661.6 | 0-60:0.01 | s | Operate delay | Real | SettingsGroups | [10 empty] | Overcurrent Phases\Definite-T 1 | Tset | Real | 1 | 0 | [7 empty] | Overcurrent Phases\Definite-T 1 | Tset | Real |  |  | 1 | 0
Setting_u007C_821_u002E_1941_u002E_662_u002E_1 | VI 3ph 1->50/51 OC-3ph-B1->Definite-T 2 | 821.1941.662.1 | off¦Off;on¦On;test¦Test |  | Mode | Enum | SettingsGroups | 0;1;2 | Real | [5 empty] | 3 | E | 0 | Overcurrent Phases\Definite-T 2 | outserv | Real | 0 | 1 | [6 empty] | 2 | Overcurrent Phases\Definite-T 2 | outserv | Real | E | 0 | 0 | 1
[16 empty] | E | 1 | Overcurrent Phases\Definite-T 2 | outserv | Real | 0 | 0 | [7 empty] | Overcurrent Phases\Definite-T 2 | outserv | Real | E | 1 | 0 | 0
[16 empty] | E | 2 | Overcurrent Phases\Definite-T 2 | outserv | Real | 0 | 0
Setting_u007C_821_u002E_1941_u002E_662_u002E_3 | VI 3ph 1->50/51 OC-3ph-B1->Definite-T 2 | 821.1941.662.3 | 30-35000:1 | A | Threshold | Real | SettingsGroups | [10 empty] | Overcurrent Phases\Definite-T 2 | Ipset | Real | /Setting_u007C_11_u002E_931_u002E_8881_u002E_101 | 0 | [7 empty] | Overcurrent Phases\Definite-T 2 | cpIpset | Real |  |  | 1 | 0
Setting_u007C_821_u002E_1941_u002E_662_u002E_6 | VI 3ph 1->50/51 OC-3ph-B1->Definite-T 2 | 821.1941.662.6 | 0-60:0.01 | s | Operate delay | Real | SettingsGroups | [10 empty] | Overcurrent Phases\Definite-T 2 | Tset | Real | 1 | 0 | [7 empty] | Overcurrent Phases\Definite-T 2 | Tset | Real |  |  | 1 | 0
Setting_u007C_821_u002E_1941_u002E_663_u002E_1 | VI 3ph 1->50/51 OC-3ph-B1->Definite-T 3 | 821.1941.663.1 | off¦Off;on¦On;test¦Test |  | Mode | Enum | SettingsGroups | 0;1;2 | Real | [5 empty] | 3 | E | 0 | Overcurrent Phases\Definite-T 3 | outserv | Real | 0 | 1 | [6 empty] | 2 | Overcurrent Phases\Definite-T 3 | outserv | Real | E | 0 | 0 | 1
[16 empty] | E | 1 | Overcurrent Phases\Definite-T 3 | outserv | Real | 0 | 0 | [7 empty] | Overcurrent Phases\Definite-T 3 | outserv | Real | E | 1 | 0 | 0
[16 empty] | E | 2 | Overcurrent Phases\Definite-T 3 | outserv | Real | 0 | 0
Setting_u007C_821_u002E_1941_u002E_663_u002E_3 | VI 3ph 1->50/51 OC-3ph-B1->Definite-T 3 | 821.1941.663.3 | 30-35000:1 | A | Threshold | Real | SettingsGroups | [10 empty] | Overcurrent Phases\Definite-T 3 | Ipset | Real | /Setting_u007C_11_u002E_931_u002E_8881_u002E_101 | 0 | [7 empty] | Overcurrent Phases\Definite-T 3 | cpIpset | Real |  |  | 1 | 0
Setting_u007C_821_u002E_1941_u002E_663_u002E_6 | VI 3ph 1->50/51 OC-3ph-B1->Definite-T 3 | 821.1941.663.6 | 0-60:0.01 | s | Operate delay | Real | SettingsGroups | [10 empty] | Overcurrent Phases\Definite-T 3 | Tset | Real | 1 | 0 | [7 empty] | Overcurrent Phases\Definite-T 3 | Tset | Real |  |  | 1 | 0
Setting_u007C_821_u002E_1941_u002E_664_u002E_1 | VI 3ph 1->50/51 OC-3ph-B1->Definite-T 4 | 821.1941.664.1 | off¦Off;on¦On;test¦Test |  | Mode | Enum | SettingsGroups | 0;1;2 | Real | [5 empty] | 3 | E | 0 | Overcurrent Phases\Definite-T 4 | outserv | Real | 0 | 1 | [6 empty] | 2 | Overcurrent Phases\Definite-T 4 | outserv | Real | E | 0 | 0 | 1
[16 empty] | E | 1 | Overcurrent Phases\Definite-T 4 | outserv | Real | 0 | 0 | [7 empty] | Overcurrent Phases\Definite-T 4 | outserv | Real | E | 1 | 0 | 0
[16 empty] | E | 2 | Overcurrent Phases\Definite-T 4 | outserv | Real | 0 | 0
Setting_u007C_821_u002E_1941_u002E_664_u002E_3 | VI 3ph 1->50/51 OC-3ph-B1->Definite-T 4 | 821.1941.664.3 | 30-35000:1 | A | Threshold | Real | SettingsGroups | [10 empty] | Overcurrent Phases\Definite-T 4 | Ipset | Real | /Setting_u007C_11_u002E_931_u002E_8881_u002E_101 | 0 | [7 empty] | Overcurrent Phases\Definite-T 4 | cpIpset | Real |  |  | 1 | 0
Setting_u007C_821_u002E_1941_u002E_664_u002E_6 | VI 3ph 1->50/51 OC-3ph-B1->Definite-T 4 | 821.1941.664.6 | 0-60:0.01 | s | Operate delay | Real | SettingsGroups | [10 empty] | Overcurrent Phases\Definite-T 4 | Tset | Real | 1 | 0 | [7 empty] | Overcurrent Phases\Definite-T 4 | Tset | Real |  |  | 1 | 0
Setting_u007C_821_u002E_1941_u002E_691_u002E_1 | VI 3ph 1->50/51 OC-3ph-B1->Inverse-T 1 | 821.1941.691.1 | off¦Off;on¦On;test¦Test |  | Mode | Enum | SettingsGroups | 0;1;2 | Real | [5 empty] | 3 | E | 0 | Overcurrent Phases\Inverse-T 1 | outserv | Real | 0 | 1 | [6 empty] | 2 | Overcurrent Phases\Inverse-T 1 | outserv | Real | E | 0 | 0 | 1
[16 empty] | E | 1 | Overcurrent Phases\Inverse-T 1 | outserv | Real | 0 | 0 | [7 empty] | Overcurrent Phases\Inverse-T 1 | outserv | Real | E | 1 | 0 | 0
[16 empty] | E | 2 | Overcurrent Phases\Inverse-T 1 | outserv | Real | 0 | 0
Setting_u007C_821_u002E_1941_u002E_691_u002E_3 | VI 3ph 1->50/51 OC-3ph-B1->Inverse-T 1 | 821.1941.691.3 | 30-35000:1 | A | Threshold | Real | SettingsGroups | [10 empty] | Overcurrent Phases\Inverse-T 1 | Ipset | Real | /Setting_u007C_11_u002E_931_u002E_8881_u002E_101 | 0 | [7 empty] | Overcurrent Phases\Inverse-T 1 | cpIpset | Real |  |  | 1 | 0
Setting_u007C_821_u002E_1941_u002E_691_u002E_130 | VI 3ph 1->50/51 OC-3ph-B1->Inverse-T 1 | 821.1941.691.130 | ANSI long-time inv.¦ANSI Long-Time Inverse;ANSI short-time inv.¦ANSI Short-Time Inverse;ANSI extremely inv.¦ANSI Extremely Inverse;ANSI very inverse¦ANSI Very Inverse;ANSI normal inverse¦ANSI Normal Inverse;ANSI moderately inv.¦ANSI Moderate Inverse;ANSI definite inverse¦ANSI Definite Time;IEC normal inverse¦IEC Normal Inverse;IEC very inverse¦IEC Very Inverse;IEC extremely inv.¦IEC Extremely Inverse;IEC long-time inverse¦IEC Long-Time Inverse |  | Type of character. curve | Enum | SettingsGroups | ANSI/IEEE long inverse;ANSI/IEEE short inverse;ANSI/IEEE extremely inverse;ANSI/IEEE very inverse;ANSI/IEEE inverse;ANSI/IEEE moderately inverse;ANSI/IEEE definite inverse;IEC 255-3 normal inverse;IEC 255-3 very inverse;IEC 255-3 extremely inverse;IEC 255-3 long inverse | String | [8 empty] | Overcurrent Phases\Inverse-T 1 | pcharac | [10 empty] | Overcurrent Phases\Inverse-T 1 | pcharac
Setting_u007C_821_u002E_1941_u002E_691_u002E_131 | VI 3ph 1->50/51 OC-3ph-B1->Inverse-T 1 | 821.1941.691.131 | instantaneous¦None;disk emulation¦Inverse Reset |  | Reset | Enum | SettingsGroups | 0;1 | Real | [8 empty] | Overcurrent Phases\Inverse-T 1 | resetdis | Real | 1 | 0 | [7 empty] | Overcurrent Phases\Inverse-T 1 | resetdis | Real |  |  | 1 | 0
Setting_u007C_821_u002E_1941_u002E_691_u002E_101 | VI 3ph 1->50/51 OC-3ph-B1->Inverse-T 1 | 821.1941.691.101 | 0.05-15:0.01 |  | Time dial | Real | SettingsGroups | [10 empty] | Overcurrent Phases\Inverse-T 1 | Tpset | Real | 1 | 0 | [7 empty] | Overcurrent Phases\Inverse-T 1 | Tpset | Real |  |  | 1 | 0
Setting_u007C_821_u002E_1731_u002E_751_u002E_1 | VI 3ph 1->50N/51N OC-gnd-B1->Definite-T 1 | 821.1731.751.1 | off¦Off;on¦On;test¦Test |  | Mode | Enum | SettingsGroups | 0;1;2 | Real | [5 empty] | 3 | E | 0 | Overcurrent Ground\Definite-T 1 | outserv | Real | 0 | 1 | [6 empty] | 2 | Overcurrent Ground\Definite-T 1 | outserv | Real | E | 0 | 0 | 1
[16 empty] | E | 1 | Overcurrent Ground\Definite-T 1 | outserv | Real | 0 | 0 | [7 empty] | Overcurrent Ground\Definite-T 1 | outserv | Real | E | 1 | 0 | 0
[16 empty] | E | 2 | Overcurrent Ground\Definite-T 1 | outserv | Real | 0 | 0
Setting_u007C_821_u002E_1731_u002E_751_u002E_3 | VI 3ph 1->50N/51N OC-gnd-B1->Definite-T 1 | 821.1731.751.3 | 30-35000:1 | A | Threshold | Real | SettingsGroups |  |  | 2 | Setting_u007C_11_u002E_931_u002E_8881_u002E_115 | E | 1 |  |  |  |  | Overcurrent Ground\Definite-T 1 | Ipset | Real | /Setting_u007C_11_u002E_931_u002E_8881_u002E_104 | 0 | [7 empty] | Overcurrent Ground\Definite-T 1 | cpIpset | Real |  |  | 1 | 0
[11 empty] | Setting_u007C_11_u002E_931_u002E_8881_u002E_115 | E | 0 |  |  |  |  | Overcurrent Ground\Definite-T 1 | Ipset | Real | /Setting_u007C_11_u002E_931_u002E_8881_u002E_101 | 0
Setting_u007C_821_u002E_1731_u002E_751_u002E_6 | VI 3ph 1->50N/51N OC-gnd-B1->Definite-T 1 | 821.1731.751.6 | 0-60:0.01 | s | Operate delay | Real | SettingsGroups | [10 empty] | Overcurrent Ground\Definite-T 1 | Tset | Real | 1 | 0 | [7 empty] | Overcurrent Ground\Definite-T 1 | Tset | Real |  |  | 1 | 0
Setting_u007C_821_u002E_1731_u002E_752_u002E_1 | VI 3ph 1->50N/51N OC-gnd-B1->Definite-T 2 | 821.1731.752.1 | off¦Off;on¦On;test¦Test |  | Mode | Enum | SettingsGroups | 0;1;2 | Real | [5 empty] | 3 | E | 0 | Overcurrent Ground\Definite-T 2 | outserv | Real | 0 | 1 | [6 empty] | 2 | Overcurrent Ground\Definite-T 2 | outserv | Real | E | 0 | 0 | 1
[16 empty] | E | 1 | Overcurrent Ground\Definite-T 2 | outserv | Real | 0 | 0 | [7 empty] | Overcurrent Ground\Definite-T 2 | outserv | Real | E | 1 | 0 | 0
[16 empty] | E | 2 | Overcurrent Ground\Definite-T 2 | outserv | Real | 0 | 0
Setting_u007C_821_u002E_1731_u002E_752_u002E_3 | VI 3ph 1->50N/51N OC-gnd-B1->Definite-T 2 | 821.1731.752.3 | 30-35000:1 | A | Threshold | Real | SettingsGroups |  |  | 2 | Setting_u007C_11_u002E_931_u002E_8881_u002E_115 | E | 1 |  |  |  |  | Overcurrent Ground\Definite-T 2 | Ipset | Real | /Setting_u007C_11_u002E_931_u002E_8881_u002E_104 | 0 | [7 empty] | Overcurrent Ground\Definite-T 2 | cpIpset | Real |  |  | 1 | 0
[11 empty] | Setting_u007C_11_u002E_931_u002E_8881_u002E_115 | E | 0 |  |  |  |  | Overcurrent Ground\Definite-T 2 | Ipset | Real | /Setting_u007C_11_u002E_931_u002E_8881_u002E_101 | 0
Setting_u007C_821_u002E_1731_u002E_752_u002E_6 | VI 3ph 1->50N/51N OC-gnd-B1->Definite-T 2 | 821.1731.752.6 | 0-60:0.01 | s | Operate delay | Real | SettingsGroups | [10 empty] | Overcurrent Ground\Definite-T 2 | Tset | Real | 1 | 0 | [7 empty] | Overcurrent Ground\Definite-T 2 | Tset | Real |  |  | 1 | 0
Setting_u007C_821_u002E_1731_u002E_753_u002E_1 | VI 3ph 1->50N/51N OC-gnd-B1->Definite-T 3 | 821.1731.753.1 | off¦Off;on¦On;test¦Test |  | Mode | Enum | SettingsGroups | 0;1;2 | Real | [5 empty] | 3 | E | 0 | Overcurrent Ground\Definite-T 3 | outserv | Real | 0 | 1 | [6 empty] | 2 | Overcurrent Ground\Definite-T 3 | outserv | Real | E | 0 | 0 | 1
[16 empty] | E | 1 | Overcurrent Ground\Definite-T 3 | outserv | Real | 0 | 0 | [7 empty] | Overcurrent Ground\Definite-T 3 | outserv | Real | E | 1 | 0 | 0
[16 empty] | E | 2 | Overcurrent Ground\Definite-T 3 | outserv | Real | 0 | 0
Setting_u007C_821_u002E_1731_u002E_753_u002E_3 | VI 3ph 1->50N/51N OC-gnd-B1->Definite-T 3 | 821.1731.753.3 | 30-35000:1 | A | Threshold | Real | SettingsGroups |  |  | 2 | Setting_u007C_11_u002E_931_u002E_8881_u002E_115 | E | 1 |  |  |  |  | Overcurrent Ground\Definite-T 3 | Ipset | Real | /Setting_u007C_11_u002E_931_u002E_8881_u002E_104 | 0 | [7 empty] | Overcurrent Ground\Definite-T 3 | cpIpset | Real |  |  | 1 | 0
[11 empty] | Setting_u007C_11_u002E_931_u002E_8881_u002E_115 | E | 0 |  |  |  |  | Overcurrent Ground\Definite-T 3 | Ipset | Real | /Setting_u007C_11_u002E_931_u002E_8881_u002E_101 | 0
Setting_u007C_821_u002E_1731_u002E_753_u002E_6 | VI 3ph 1->50N/51N OC-gnd-B1->Definite-T 3 | 821.1731.753.6 | 0-60:0.01 | s | Operate delay | Real | SettingsGroups | [10 empty] | Overcurrent Ground\Definite-T 3 | Tset | Real | 1 | 0 | [7 empty] | Overcurrent Ground\Definite-T 3 | Tset | Real |  |  | 1 | 0
Setting_u007C_821_u002E_1731_u002E_781_u002E_1 | VI 3ph 1->50N/51N OC-gnd-B1->Inverse-T 1 | 821.1731.781.1 | off¦Off;on¦On;test¦Test |  | Mode | Enum | SettingsGroups | 0;1;2 | Real | [5 empty] | 3 | E | 0 | Overcurrent Ground\Inverse-T 1 | outserv | Real | 0 | 1 | [6 empty] | 2 | Overcurrent Ground\Inverse-T 1 | outserv | Real | E | 0 | 0 | 1
[16 empty] | E | 1 | Overcurrent Ground\Inverse-T 1 | outserv | Real | 0 | 0 | [7 empty] | Overcurrent Ground\Inverse-T 1 | outserv | Real | E | 1 | 0 | 0
[16 empty] | E | 2 | Overcurrent Ground\Inverse-T 1 | outserv | Real | 0 | 0
Setting_u007C_821_u002E_1731_u002E_781_u002E_3 | VI 3ph 1->50N/51N OC-gnd-B1->Inverse-T 1 | 821.1731.781.3 | 30-35000:1 | A | Threshold | Real | SettingsGroups |  |  | 2 | Setting_u007C_11_u002E_931_u002E_8881_u002E_115 | E | 1 |  |  |  |  | Overcurrent Ground\Inverse-T 1 | Ipset | Real | /Setting_u007C_11_u002E_931_u002E_8881_u002E_104 | 0 | [7 empty] | Overcurrent Ground\Inverse-T 1 | cpIpset | Real |  |  | 1 | 0
[11 empty] | Setting_u007C_11_u002E_931_u002E_8881_u002E_115 | E | 0 |  |  |  |  | Overcurrent Ground\Inverse-T 1 | Ipset | Real | /Setting_u007C_11_u002E_931_u002E_8881_u002E_101 | 0
Setting_u007C_821_u002E_1731_u002E_781_u002E_108 | VI 3ph 1->50N/51N OC-gnd-B1->Inverse-T 1 | 821.1731.781.108 | ANSI long-time inv.¦ANSI Long-Time Inverse;ANSI short-time inv.¦ANSI Short-Time Inverse;ANSI extremely inv.¦ANSI Extremely Inverse;ANSI very inverse¦ANSI Very Inverse;ANSI normal inverse¦ANSI Normal Inverse;ANSI moderately inv.¦ANSI Moderate Inverse;ANSI definite inverse¦ANSI Definite Time;IEC normal inverse¦IEC Normal Inverse;IEC very inverse¦IEC Very Inverse;IEC extremely inv.¦IEC Extremely Inverse;IEC long-time inverse¦IEC Long-Time Inverse |  | Type of character. curve | Enum | SettingsGroups | ANSI/IEEE long inverse;ANSI/IEEE short inverse;ANSI/IEEE extremely inverse;ANSI/IEEE very inverse;ANSI/IEEE inverse;ANSI/IEEE moderately inverse;ANSI/IEEE definite inverse;IEC 255-3 normal inverse;IEC 255-3 very inverse;IEC 255-3 extremely inverse;IEC 255-3 long inverse | String | [8 empty] | Overcurrent Ground\Inverse-T 1 | pcharac | [10 empty] | Overcurrent Ground\Inverse-T 1 | pcharac
Setting_u007C_821_u002E_1731_u002E_781_u002E_109 | VI 3ph 1->50N/51N OC-gnd-B1->Inverse-T 1 | 821.1731.781.109 | instantaneous¦None;disk emulation¦Inverse Reset |  | Reset | Enum | SettingsGroups | 0;1 | Real | [8 empty] | Overcurrent Ground\Inverse-T 1 | resetdis | Real | 1 | 0 | [7 empty] | Overcurrent Ground\Inverse-T 1 | resetdis | Real |  |  | 1 | 0
Setting_u007C_821_u002E_1731_u002E_781_u002E_101 | VI 3ph 1->50N/51N OC-gnd-B1->Inverse-T 1 | 821.1731.781.101 | 0.05-15:0.01 |  | Time dial | Real | SettingsGroups | [10 empty] | Overcurrent Ground\Inverse-T 1 | Tpset | Real | 1 | 0 | [7 empty] | Overcurrent Ground\Inverse-T 1 | Tpset | Real |  |  | 1 | 0
Setting_u007C_821_u002E_1971_u002E_2311_u002E_102 | VI 3ph 1->67 Dir.OC-3ph-B1->General | 821.1971.2311.102 | -180-180:1 | ° | Rotation angle of ref. volt. | Real | SettingsGroups | [10 empty] | Directional Overcurrent Phases\Direction Determination | mtau | Real | 1 | 0 | [7 empty] | Directional Overcurrent Phases\Direction Determination | mtau | Real |  |  | 1 | 0
Setting_u007C_821_u002E_1971_u002E_8131_u002E_1 | VI 3ph 1->67 Dir.OC-3ph-B1->Definite-T 1 | 821.1971.8131.1 | off¦Off;on¦On;test¦Test |  | Mode | Enum | SettingsGroups | 0;1;2 | Real | [5 empty] | 3 | E | 0 | Directional Overcurrent Phases\Definite-T 1 | outserv | Real | 0 | 1 | [6 empty] | 2 | Directional Overcurrent Phases\Definite-T 1 | outserv | Real | E | 0 | 0 | 1
[16 empty] | E | 1 | Directional Overcurrent Phases\Definite-T 1 | outserv | Real | 0 | 0 | [7 empty] | Directional Overcurrent Phases\Definite-T 1 | outserv | Real | E | 1 | 0 | 0
[16 empty] | E | 2 | Directional Overcurrent Phases\Definite-T 1 | outserv | Real | 0 | 0
Setting_u007C_821_u002E_1971_u002E_8131_u002E_105 | VI 3ph 1->67 Dir.OC-3ph-B1->Definite-T 1 | 821.1971.8131.105 | forward¦Forward;reverse¦Reverse |  | Directional mode | Enum | SettingsGroups | 1;2 | Real | [8 empty] | Directional Overcurrent Phases\Definite-T 1 | idir | Real | 1 | 0 | [7 empty] | Directional Overcurrent Phases\Definite-T 1 | idir | Real |  |  | 1 | 0
Setting_u007C_821_u002E_1971_u002E_8131_u002E_3 | VI 3ph 1->67 Dir.OC-3ph-B1->Definite-T 1 | 821.1971.8131.3 | 30-35000:1 | A | Threshold | Real | SettingsGroups | [10 empty] | Directional Overcurrent Phases\Definite-T 1 | Ipset | Real | /Setting_u007C_11_u002E_931_u002E_8881_u002E_101 | 0 | [7 empty] | Directional Overcurrent Phases\Definite-T 1 | cpIpset | Real |  |  | 1 | 0
Setting_u007C_821_u002E_1971_u002E_8131_u002E_6 | VI 3ph 1->67 Dir.OC-3ph-B1->Definite-T 1 | 821.1971.8131.6 | 0-60:0.01 | s | Operate delay | Real | SettingsGroups | [10 empty] | Directional Overcurrent Phases\Definite-T 1 | Tset | Real | 1 | 0 | [7 empty] | Directional Overcurrent Phases\Definite-T 1 | Tset | Real |  |  | 1 | 0
Setting_u007C_821_u002E_1971_u002E_8132_u002E_1 | VI 3ph 1->67 Dir.OC-3ph-B1->Definite-T 2 | 821.1971.8132.1 | off¦Off;on¦On;test¦Test |  | Mode | Enum | SettingsGroups | 0;1;2 | Real | [5 empty] | 3 | E | 0 | Directional Overcurrent Phases\Definite-T 2 | outserv | Real | 0 | 1 | [6 empty] | 2 | Directional Overcurrent Phases\Definite-T 2 | outserv | Real | E | 0 | 0 | 1
[16 empty] | E | 1 | Directional Overcurrent Phases\Definite-T 2 | outserv | Real | 0 | 0 | [7 empty] | Directional Overcurrent Phases\Definite-T 2 | outserv | Real | E | 1 | 0 | 0
[16 empty] | E | 2 | Directional Overcurrent Phases\Definite-T 2 | outserv | Real | 0 | 0
Setting_u007C_821_u002E_1971_u002E_8132_u002E_105 | VI 3ph 1->67 Dir.OC-3ph-B1->Definite-T 2 | 821.1971.8132.105 | forward¦Forward;reverse¦Reverse |  | Directional mode | Enum | SettingsGroups | 1;2 | Real | [8 empty] | Directional Overcurrent Phases\Definite-T 2 | idir | Real | 1 | 0 | [7 empty] | Directional Overcurrent Phases\Definite-T 2 | idir | Real |  |  | 1 | 0
Setting_u007C_821_u002E_1971_u002E_8132_u002E_3 | VI 3ph 1->67 Dir.OC-3ph-B1->Definite-T 2 | 821.1971.8132.3 | 30-35000:1 | A | Threshold | Real | SettingsGroups | [10 empty] | Directional Overcurrent Phases\Definite-T 2 | Ipset | Real | /Setting_u007C_11_u002E_931_u002E_8881_u002E_101 | 0 | [7 empty] | Directional Overcurrent Phases\Definite-T 2 | cpIpset | Real |  |  | 1 | 0
Setting_u007C_821_u002E_1971_u002E_8132_u002E_6 | VI 3ph 1->67 Dir.OC-3ph-B1->Definite-T 2 | 821.1971.8132.6 | 0-60:0.01 | s | Operate delay | Real | SettingsGroups | [10 empty] | Directional Overcurrent Phases\Definite-T 2 | Tset | Real | 1 | 0 | [7 empty] | Directional Overcurrent Phases\Definite-T 2 | Tset | Real |  |  | 1 | 0
Setting_u007C_821_u002E_1971_u002E_8133_u002E_1 | VI 3ph 1->67 Dir.OC-3ph-B1->Definite-T 3 | 821.1971.8133.1 | off¦Off;on¦On;test¦Test |  | Mode | Enum | SettingsGroups | 0;1;2 | Real | [5 empty] | 3 | E | 0 | Directional Overcurrent Phases\Definite-T 3 | outserv | Real | 0 | 1 | [6 empty] | 2 | Directional Overcurrent Phases\Definite-T 3 | outserv | Real | E | 0 | 0 | 1
[16 empty] | E | 1 | Directional Overcurrent Phases\Definite-T 3 | outserv | Real | 0 | 0 | [7 empty] | Directional Overcurrent Phases\Definite-T 3 | outserv | Real | E | 1 | 0 | 0
[16 empty] | E | 2 | Directional Overcurrent Phases\Definite-T 3 | outserv | Real | 0 | 0
Setting_u007C_821_u002E_1971_u002E_8133_u002E_105 | VI 3ph 1->67 Dir.OC-3ph-B1->Definite-T 3 | 821.1971.8133.105 | forward¦Forward;reverse¦Reverse |  | Directional mode | Enum | SettingsGroups | 1;2 | Real | [8 empty] | Directional Overcurrent Phases\Definite-T 3 | idir | Real | 1 | 0 | [7 empty] | Directional Overcurrent Phases\Definite-T 3 | idir | Real |  |  | 1 | 0
Setting_u007C_821_u002E_1971_u002E_8133_u002E_3 | VI 3ph 1->67 Dir.OC-3ph-B1->Definite-T 3 | 821.1971.8133.3 | 30-35000:1 | A | Threshold | Real | SettingsGroups | [10 empty] | Directional Overcurrent Phases\Definite-T 3 | Ipset | Real | /Setting_u007C_11_u002E_931_u002E_8881_u002E_101 | 0 | [7 empty] | Directional Overcurrent Phases\Definite-T 3 | cpIpset | Real |  |  | 1 | 0
Setting_u007C_821_u002E_1971_u002E_8133_u002E_6 | VI 3ph 1->67 Dir.OC-3ph-B1->Definite-T 3 | 821.1971.8133.6 | 0-60:0.01 | s | Operate delay | Real | SettingsGroups | [10 empty] | Directional Overcurrent Phases\Definite-T 3 | Tset | Real | 1 | 0 | [7 empty] | Directional Overcurrent Phases\Definite-T 3 | Tset | Real |  |  | 1 | 0
Setting_u007C_821_u002E_1971_u002E_8134_u002E_1 | VI 3ph 1->67 Dir.OC-3ph-B1->Definite-T 4 | 821.1971.8134.1 | off¦Off;on¦On;test¦Test |  | Mode | Enum | SettingsGroups | 0;1;2 | Real | [5 empty] | 3 | E | 0 | Directional Overcurrent Phases\Definite-T 4 | outserv | Real | 0 | 1 | [6 empty] | 2 | Directional Overcurrent Phases\Definite-T 4 | outserv | Real | E | 0 | 0 | 1
[16 empty] | E | 1 | Directional Overcurrent Phases\Definite-T 4 | outserv | Real | 0 | 0 | [7 empty] | Directional Overcurrent Phases\Definite-T 4 | outserv | Real | E | 1 | 0 | 0
[16 empty] | E | 2 | Directional Overcurrent Phases\Definite-T 4 | outserv | Real | 0 | 0
Setting_u007C_821_u002E_1971_u002E_8134_u002E_105 | VI 3ph 1->67 Dir.OC-3ph-B1->Definite-T 4 | 821.1971.8134.105 | forward¦Forward;reverse¦Reverse |  | Directional mode | Enum | SettingsGroups | 1;2 | Real | [8 empty] | Directional Overcurrent Phases\Definite-T 4 | idir | Real | 1 | 0 | [7 empty] | Directional Overcurrent Phases\Definite-T 4 | idir | Real |  |  | 1 | 0
Setting_u007C_821_u002E_1971_u002E_8134_u002E_3 | VI 3ph 1->67 Dir.OC-3ph-B1->Definite-T 4 | 821.1971.8134.3 | 30-35000:1 | A | Threshold | Real | SettingsGroups | [10 empty] | Directional Overcurrent Phases\Definite-T 4 | Ipset | Real | /Setting_u007C_11_u002E_931_u002E_8881_u002E_101 | 0 | [7 empty] | Directional Overcurrent Phases\Definite-T 4 | cpIpset | Real |  |  | 1 | 0
Setting_u007C_821_u002E_1971_u002E_8134_u002E_6 | VI 3ph 1->67 Dir.OC-3ph-B1->Definite-T 4 | 821.1971.8134.6 | 0-60:0.01 | s | Operate delay | Real | SettingsGroups | [10 empty] | Directional Overcurrent Phases\Definite-T 4 | Tset | Real | 1 | 0 | [7 empty] | Directional Overcurrent Phases\Definite-T 4 | Tset | Real |  |  | 1 | 0
Setting_u007C_821_u002E_1971_u002E_8161_u002E_1 | VI 3ph 1->67 Dir.OC-3ph-B1->Inverse-T 1 | 821.1971.8161.1 | off¦Off;on¦On;test¦Test |  | Mode | Enum | SettingsGroups | 0;1;2 | Real | [5 empty] | 3 | E | 0 | Directional Overcurrent Phases\Inverse-T 1 | outserv | Real | 0 | 1 | [6 empty] | 2 | Directional Overcurrent Phases\Inverse-T 1 | outserv | Real | E | 0 | 0 | 1
[16 empty] | E | 1 | Directional Overcurrent Phases\Inverse-T 1 | outserv | Real | 0 | 0 | [7 empty] | Directional Overcurrent Phases\Inverse-T 1 | outserv | Real | E | 1 | 0 | 0
[16 empty] | E | 2 | Directional Overcurrent Phases\Inverse-T 1 | outserv | Real | 0 | 0
Setting_u007C_821_u002E_1971_u002E_8161_u002E_111 | VI 3ph 1->67 Dir.OC-3ph-B1->Inverse-T 1 | 821.1971.8161.111 | forward¦Forward;reverse¦Reverse |  | Directional mode | Enum | SettingsGroups | 1;2 | Real | [8 empty] | Directional Overcurrent Phases\Inverse-T 1 | idir | Real | 1 | 0 | [7 empty] | Directional Overcurrent Phases\Inverse-T 1 | idir | Real |  |  | 1 | 0
Setting_u007C_821_u002E_1971_u002E_8161_u002E_3 | VI 3ph 1->67 Dir.OC-3ph-B1->Inverse-T 1 | 821.1971.8161.3 | 30-35000:1 | A | Threshold | Real | SettingsGroups | [10 empty] | Directional Overcurrent Phases\Inverse-T 1 | Ipset | Real | /Setting_u007C_11_u002E_931_u002E_8881_u002E_101 | 0 | [7 empty] | Directional Overcurrent Phases\Inverse-T 1 | cpIpset | Real |  |  | 1 | 0
Setting_u007C_821_u002E_1971_u002E_8161_u002E_130 | VI 3ph 1->67 Dir.OC-3ph-B1->Inverse-T 1 | 821.1971.8161.130 | ANSI long-time inv.¦ANSI Long-Time Inverse;ANSI short-time inv.¦ANSI Short-Time Inverse;ANSI extremely inv.¦ANSI Extremely Inverse;ANSI very inverse¦ANSI Very Inverse;ANSI normal inverse¦ANSI Normal Inverse;ANSI moderately inv.¦ANSI Moderate Inverse;ANSI definite inverse¦ANSI Definite Time;IEC normal inverse¦IEC Normal Inverse;IEC very inverse¦IEC Very Inverse;IEC extremely inv.¦IEC Extremely Inverse;IEC long-time inverse¦IEC Long-Time Inverse |  | Type of character. curve | Enum | SettingsGroups | ANSI/IEEE long inverse;ANSI/IEEE short inverse;ANSI/IEEE extremely inverse;ANSI/IEEE very inverse;ANSI/IEEE inverse;ANSI/IEEE moderately inverse;ANSI/IEEE definite inverse;IEC 255-3 normal inverse;IEC 255-3 very inverse;IEC 255-3 extremely inverse;IEC 255-3 long inverse | String | [8 empty] | Directional Overcurrent Phases\Inverse-T 1 | pcharac | [10 empty] | Directional Overcurrent Phases\Inverse-T 1 | pcharac
Setting_u007C_821_u002E_1971_u002E_8161_u002E_131 | VI 3ph 1->67 Dir.OC-3ph-B1->Inverse-T 1 | 821.1971.8161.131 | instantaneous¦None;disk emulation¦Inverse Reset |  | Reset | Enum | SettingsGroups | 0;1 | Real | [8 empty] | Directional Overcurrent Phases\Inverse-T 1 | resetdis | Real | 1 | 0 | [7 empty] | Directional Overcurrent Phases\Inverse-T 1 | resetdis | Real |  |  | 1 | 0
Setting_u007C_821_u002E_1971_u002E_8161_u002E_101 | VI 3ph 1->67 Dir.OC-3ph-B1->Inverse-T 1 | 821.1971.8161.101 | 0.05-15:0.01 |  | Time dial | Real | SettingsGroups | [10 empty] | Directional Overcurrent Phases\Inverse-T 1 | Tpset | Real | 1 | 0 | [7 empty] | Directional Overcurrent Phases\Inverse-T 1 | Tpset | Real |  |  | 1 | 0
_END_