## Mapping
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37
StationWare | [6 empty] | Common |  |  | Import | [12 empty] | Export
[8 empty] | Enumeration |  | Pre-Condition |  |  |  |  | Instruction | [7 empty] | Pre-Condition | [5 empty] | Instruction
Key | Chapter | Display name | Range | Unit | Description | Type | Group | Mapping | Type |  | Setting | Operator | Value | Default |  | Operator | Value | Target | Parameter | Type | Scale | Offset |  | Source | Parameter | Type | Operator | Value |  | Source | Parameter | Type | Operator | Value | Scale | Offset
ObjektanpassungWandleranpassungNennstrom_u002D_Leiterstromwandler | Transformer setting | Rated current for phase transformer | In=1A¦In_1A;In=5A¦In_5A |  | LS | Enum | Objektanpassung | 1;5 | Real |  |  |  |  | 1 |  |  |  | Measurement | Inom | Real | 1 | 0 | [7 empty] | Measurement | Inom | Real |  |  | 1 | 0
_u00DC_berstromschutz_u002D_1_u00DC_I1_u002D__u00DC_berstromschutz_u002D_aktiv | Overcurrent prot. 1 IL> | Overcurrent prot. 1 IL> | Active¦aktiv;Inactive¦inaktiv |  | IL> | Enum | Schutzfunktionen | 0;1 | Real |  |  |  |  | 0 | 2 | E | 1 | Overcurrent\IL> DT | outserv | Real | 0 | 1 |  | Overcurrent | outserv | Real | E | 0 | 2 | Overcurrent\IL> DT | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\IL> IDMT | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\IL> IDMT | outserv | Real |  |  | 1 | 0
_u00DC_berstromschutz_u002D_1_u00DC_I1_u002D_Zeit_u002D_Kennlinie | Overcurrent prot. 1 IL> | Delay curve tIL> | Independent¦unabhängig;Inverse¦invers;Very inverse¦very_invers;Extremely inverse¦extremly_invers |  | IL>AU | Enum | Schutzfunktionen | Definite;IEC 255-3 Inverse;IEC 255-3 Very Inverse;IEC 255-3 Extremely Inverse | String |  | _u00DC_berstromschutz_u002D_1_u00DC_I1_u002D__u00DC_berstromschutz_u002D_aktiv | E | 0 | Definite | 4 | E | Definite | Overcurrent\IL> DT | outserv | Real | 0 | 0 | 2 | Overcurrent;Overcurrent\IL> IDMT | outserv;outserv | Real;Real | E;E | 0;0 |  | Overcurrent\IL> IDMT | pcharac
[16 empty] | E | Definite | Overcurrent\IL> IDMT | outserv | Real | 0 | 1 | [13 empty] | Definite
[16 empty] | NE | Definite | Overcurrent\IL> DT | outserv | Real | 0 | 1
[16 empty] | NE | Definite | Overcurrent\IL> IDMT | outserv | Real | 0 | 0
_u00DC_berstromschutz_u002D_1_u00DC_I1_u002D_Anregeschwelle_u002D_unabh_u00E4_ngig | Overcurrent prot. 1 IL> | Threshold independent IL> | 0.08-40.00:0.01 | In | IL>ANR | Real | Schutzfunktionen | [6 empty] | 2 |  |  |  | Overcurrent\IL> DT | Ipset | Real | 1 | 0 |  | Overcurrent;Overcurrent\IL> DT | outserv;outserv | Real;Real | E;E | 0;0 |  | Overcurrent\IL> DT | Ipset | Real |  |  | 1 | 0
_u00DC_berstromschutz_u002D_1_u00DC_I1_u002D_Zeitstufe_u002D_ungerichtet | Overcurrent prot. 1 IL> | Delay nondirectional IL> | 0.01-9.99:0.01 | s | tIL> | Real | Schutzfunktionen | [6 empty] | 1 |  |  |  | Overcurrent\IL> DT | Tset | Real | 1 | 0 |  | Overcurrent;Overcurrent\IL> DT | outserv;outserv | Real;Real | E;E | 0;0 |  | Overcurrent\IL> DT | Tset | Real |  |  | 1 | 0
_u00DC_berstromschutz_u002D_1_u00DC_I1_u002D_Anregeschwelle_u002D_abh_u00E4_ngig | Overcurrent prot. 1 IL> | Threshold inverse IL> | 0.20-4.00:0.01 | In | IL>AMZ | Real | Schutzfunktionen | [6 empty] | 2 |  |  |  | Overcurrent\IL> IDMT | Ipset | Real | 1 | 0 |  | Overcurrent;Overcurrent\IL> IDMT | outserv;outserv | Real;Real | E;E | 0;0 |  | Overcurrent\IL> IDMT | Ipset | Real |  |  | 1 | 0
_u00DC_berstromschutz_u002D_1_u00DC_I1_u002D_Zeitfaktor_u002D_ungerichtet | Overcurrent prot. 1 IL> | Time factor nondirectional IL> | 0.05-2.00:0.01 | s | IL>AMZt | Real | Schutzfunktionen | [6 empty] | 0.2 |  |  |  | Overcurrent\IL> IDMT | Tpset | Real | 1 | 0 |  | Overcurrent;Overcurrent\IL> IDMT | outserv;outserv | Real;Real | E;E | 0;0 |  | Overcurrent\IL> IDMT | Tpset | Real |  |  | 1 | 0
_u00DC_berstromschutz_u002D_1_u00DC_I1_u002D_Maximale_u002D_Verz_u00F6_gerung | Overcurrent prot. 1 IL> | Maximum delay IL> | 10.00-60.00:0.01 | s | IL>AMZv | Real | Schutzfunktionen | [6 empty] | 60 |  |  |  | Overcurrent\IL> IDMT | udeftmax | Real | 1 | 0 |  | Overcurrent;Overcurrent\IL> IDMT | outserv;outserv | Real;Real | E;E | 0;0 |  | Overcurrent\IL> IDMT | udeftmax | Real |  |  | 1 | 0
_u00DC_berstromschutz_u002D_2_u00DC_I2_u002D__u00DC_berstromschutz_u002D_aktiv | Overcurrent prot. 2 IL>> | Overcurrent prot. 2 IL>> | Active¦aktiv;Inactive¦inaktiv |  | IL>> | Enum | Schutzfunktionen | 0;1 | Real |  |  |  |  | 0 | 2 | E | 1 | Overcurrent\IL>> DT | outserv | Real | 0 | 1 |  | Overcurrent | outserv | Real | E | 0 | 2 | Overcurrent\IL>> DT | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\IL>> IDMT | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\IL>> IDMT | outserv | Real |  |  | 1 | 0
_u00DC_berstromschutz_u002D_2_u00DC_I2_u002D_Zeit_u002D_Kennlinie | Overcurrent prot. 2 IL>> | Delay curve tIL>> | Independent¦unabhängig;Inverse¦invers;Very inverse¦very_invers;Extremely inverse¦extremly_invers |  | IL>>AU | Enum | Schutzfunktionen | Definite;IEC 255-3 Inverse;IEC 255-3 Very Inverse;IEC 255-3 Extremely Inverse | String |  | _u00DC_berstromschutz_u002D_2_u00DC_I2_u002D__u00DC_berstromschutz_u002D_aktiv | E | 0 | Definite | 4 | E | Definite | Overcurrent\IL>> DT | outserv | Real | 0 | 0 | 2 | Overcurrent;Overcurrent\IL>> IDMT | outserv;outserv | Real;Real | E;E | 0;0 |  | Overcurrent\IL>> IDMT | pcharac
[16 empty] | E | Definite | Overcurrent\IL>> IDMT | outserv | Real | 0 | 1 | [13 empty] | Definite
[16 empty] | NE | Definite | Overcurrent\IL>> DT | outserv | Real | 0 | 1
[16 empty] | NE | Definite | Overcurrent\IL>> IDMT | outserv | Real | 0 | 0
_u00DC_berstromschutz_u002D_2_u00DC_I2_u002D_Anregeschwelle_u002D_unabh_u00E4_ngig | Overcurrent prot. 2 IL>> | Threshold independent IL>> | 0.08-40.00:0.01 | In | IL>>ANR | Real | Schutzfunktionen | [6 empty] | 2 |  |  |  | Overcurrent\IL>> DT | Ipset | Real | 1 | 0 |  | Overcurrent;Overcurrent\IL>> DT | outserv;outserv | Real;Real | E;E | 0;0 |  | Overcurrent\IL>> DT | Ipset | Real |  |  | 1 | 0
_u00DC_berstromschutz_u002D_2_u00DC_I2_u002D_Zeitstufe_u002D_ungerichtet | Overcurrent prot. 2 IL>> | Delay nondirectional IL>> | 0.01-9.99:0.01 | s | tIL>> | Real | Schutzfunktionen | [6 empty] | 1 |  |  |  | Overcurrent\IL>> DT | Tset | Real | 1 | 0 |  | Overcurrent;Overcurrent\IL>> DT | outserv;outserv | Real;Real | E;E | 0;0 |  | Overcurrent\IL>> DT | Tset | Real |  |  | 1 | 0
_u00DC_berstromschutz_u002D_2_u00DC_I2_u002D_Anregeschwelle_u002D_abh_u00E4_ngig | Overcurrent prot. 2 IL>> | Threshold inverse IL>> | 0.20-10.00:0.01 | In | IL>>AMZ | Real | Schutzfunktionen | [6 empty] | 2 |  |  |  | Overcurrent\IL>> IDMT | Ipset | Real | 1 | 0 |  | Overcurrent;Overcurrent\IL>> IDMT | outserv;outserv | Real;Real | E;E | 0;0 |  | Overcurrent\IL>> IDMT | Ipset | Real |  |  | 1 | 0
_u00DC_berstromschutz_u002D_2_u00DC_I2_u002D_Zeitfaktor_u002D_ungerichtet | Overcurrent prot. 2 IL>> | Time factor nondirectional IL>> | 0.05-2.00:0.01 | s | IL>>AMZt | Real | Schutzfunktionen | [6 empty] | 0.2 |  |  |  | Overcurrent\IL>> IDMT | Tpset | Real | 1 | 0 |  | Overcurrent;Overcurrent\IL>> IDMT | outserv;outserv | Real;Real | E;E | 0;0 |  | Overcurrent\IL>> IDMT | Tpset | Real |  |  | 1 | 0
_u00DC_berstromschutz_u002D_2_u00DC_I2_u002D_Maximale_u002D_Verz_u00F6_gerung | Overcurrent prot. 2 IL>> | Maximum delay IL>> | 10.00-80.00:0.01 | s | IL>>AMZv | Real | Schutzfunktionen | [6 empty] | 60 |  |  |  | Overcurrent\IL>> IDMT | udeftmax | Real | 1 | 0 |  | Overcurrent;Overcurrent\IL>> IDMT | outserv;outserv | Real;Real | E;E | 0;0 |  | Overcurrent\IL>> IDMT | udeftmax | Real |  |  | 1 | 0
_END_