## Mapping
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37
StationWare | [6 empty] | Common |  |  | Import | [12 empty] | Export
[8 empty] | Enumeration |  | Pre-Condition |  |  |  |  | Instruction | [7 empty] | Pre-Condition | [5 empty] | Instruction
Key | Chapter | Display name | Range | Unit | Description | Type | Group | Mapping | Type |  | Setting | Operator | Value | Default |  | Operator | Value | Target | Parameter | Type | Scale | Offset |  | Source | Parameter | Type | Operator | Value |  | Source | Parameter | Type | Operator | Value | Scale | Offset
ObjektanpassungAnpassung_u002D_StromwandlerPri_u002D_Nennstrom_u002D_Leiterstromwandler_u002D_S1 | Current transformer setting | Rated primary current for phase curr. transf. side 1 | 0.050-20.000:0.001 | kA | WaILPriS1 | Real | Objektanpassung | [6 empty] | 0.2 |  |  |  | Differential\CT Adaption Side 1 | CTratio | Real | 1000/ObjektanpassungAnpassung_u002D_StromwandlerSek_u002D_Nennstrom_u002D_Leiterstromwandler_u002D_S1 | 0 |  | Differential;Differential\CT Adaption Side 1 | outserv;outserv | Real;Real | E;E | 0;0 |  | Differential\CT Adaption Side 1 | CTratio | Real |  |  | Measurement Side 1:e:Inom/1000 | 0
ObjektanpassungAnpassung_u002D_StromwandlerSek_u002D_Nennstrom_u002D_Leiterstromwandler_u002D_S1 | Current transformer setting | Rated secondary current for phase curr. transf. side 1 | In=1A¦In_1A;In=5A¦In_5A |  | WaILSekS1 | Enum | Objektanpassung | 1;5 | Real |  |  |  |  | 1 | 2 |  |  | Measurement Side 1 | Inom | Real | 1 | 0 | [7 empty] | Measurement Side 1 | Inom | Real |  |  | 1 | 0
[18 empty] | Differential\Measurement Diff | Inom | Real | 1 | 0
ObjektanpassungAnpassung_u002D_StromwandlerPri_u002D_Nennstrom_u002D_Leiterstromwandler_u002D_S2 | Current transformer setting | Rated primary current for phase curr. transf. side 2 | 0.050-20.000:0.001 | kA | WaILPriS2 | Real | Objektanpassung | [6 empty] | 1.2 |  |  |  | Differential\CT Adaption Side 2 | CTratio | Real | 1000/ObjektanpassungAnpassung_u002D_StromwandlerSek_u002D_Nennstrom_u002D_Leiterstromwandler_u002D_S2 | 0 |  | Differential;Differential\CT Adaption Side 2 | outserv;outserv | Real;Real | E;E | 0;0 |  | Differential\CT Adaption Side 2 | CTratio | Real |  |  | Measurement Side 2:e:Inom/1000 | 0
ObjektanpassungAnpassung_u002D_StromwandlerSek_u002D_Nennstrom_u002D_Leiterstromwandler_u002D_S2 | Current transformer setting | Rated secondary current for phase curr. transf. side 2 | In=1A¦In_1A;In=5A¦In_5A |  | WaILSekS2 | Enum | Objektanpassung | 1;5 | Real |  |  |  |  | 1 |  |  |  | Measurement Side 2 | Inom | Real | 1 | 0 | [7 empty] | Measurement Side 2 | Inom | Real |  |  | 1 | 0
ObjektanpassungTransformatorNennspannung_u002D_Trafo_u002D_Seite1 | Power transformer | Rated voltage side 1 | 0.03-420.00:0.01 | kV | TrUnS1 | Real | Objektanpassung | [6 empty] | 110 |  |  |  | Differential\CT Adaption Side 1 | LLVolt | Real | 1 | 0 |  | Differential;Differential\CT Adaption Side 1 | outserv;outserv | Real;Real | E;E | 0;0 |  | Differential\CT Adaption Side 1 | LLVolt | Real |  |  | 1 | 0
ObjektanpassungTransformatorNennspannung_u002D_Trafo_u002D_Seite2 | Power transformer | Rated voltage side 2 | 0.03-420.00:0.01 | kV | TrUnS2 | Real | Objektanpassung | [6 empty] | 20 |  |  |  | Differential\CT Adaption Side 2 | LLVolt | Real | 1 | 0 |  | Differential;Differential\CT Adaption Side 2 | outserv;outserv | Real;Real | E;E | 0;0 |  | Differential\CT Adaption Side 2 | LLVolt | Real |  |  | 1 | 0
ObjektanpassungTransformatorSchaltgruppe_u002D_Trafo_u002D_Seite1_u002D_Seite2 | Power transformer | Vector group | Yy0¦Yy0;Yy6¦Yy6;Yd1¦Yd1;Yd5¦Yd5;Yd7¦Yd7;Yd11¦Yd11;Yz1¦Yz1;Yz5¦Yz5;Yz7¦Yz7;Yz11¦Yz11;Dy1¦Dy1;Dy5¦Dy5;Dy7¦Dy7;Dy11¦Dy11;Dd0¦Dd0;Dd6¦Dd6 |  | TrSG | Enum | Objektanpassung | 0;1;2;3;4;5;6;7;8;9;10;11;12;13;14;15 | Real |  |  |  |  | 0 | 25 | SE | 5 | Differential\CT Adaption Side 1 | icontype | Real | 0 | 2 | 4 | Differential;Differential\CT Adaption Side 1;Differential\CT Adaption Side 2;Differential\CT Adaption Side 1;Differential\CT Adaption Side 2 | outserv;outserv;outserv;icontype;icontype | Real;Real;Real;Real;Real | E;E;E;E;E | 0;0;0;2;2 | 2 | Differential\CT Adaption Side 2 | trasfgroup | Real | E | 0 | 0 | 0
[16 empty] | GE | 10 | Differential\CT Adaption Side 1 | icontype | Real | 0 | 1 | [7 empty] | Differential\CT Adaption Side 2 | trasfgroup | Real | E | 6 | 0 | 1
[16 empty] | E | 0 | Differential\CT Adaption Side 2 | icontype | Real | 0 | 2 |  | Differential;Differential\CT Adaption Side 1;Differential\CT Adaption Side 2;Differential\CT Adaption Side 1;Differential\CT Adaption Side 2 | outserv;outserv;outserv;icontype;icontype | Real;Real;Real;Real;Real | E;E;E;E;E | 0;0;0;2;1 | 4 | Differential\CT Adaption Side 2 | trasfgroup | Real | E | 1 | 0 | 2
[16 empty] | E | 1 | Differential\CT Adaption Side 2 | icontype | Real | 0 | 2 | [7 empty] | Differential\CT Adaption Side 2 | trasfgroup | Real | E | 5 | 0 | 3
[16 empty] | E | 2 | Differential\CT Adaption Side 2 | icontype | Real | 0 | 1 | [7 empty] | Differential\CT Adaption Side 2 | trasfgroup | Real | E | 7 | 0 | 4
[16 empty] | E | 3 | Differential\CT Adaption Side 2 | icontype | Real | 0 | 1 | [7 empty] | Differential\CT Adaption Side 2 | trasfgroup | Real | E | 11 | 0 | 5
[16 empty] | E | 4 | Differential\CT Adaption Side 2 | icontype | Real | 0 | 1 |  | Differential;Differential\CT Adaption Side 1;Differential\CT Adaption Side 2;Differential\CT Adaption Side 1;Differential\CT Adaption Side 2 | outserv;outserv;outserv;icontype;icontype | Real;Real;Real;Real;Real | E;E;E;E;E | 0;0;0;1;2 | 4 | Differential\CT Adaption Side 2 | trasfgroup | Real | E | 1 | 0 | 10
[16 empty] | E | 5 | Differential\CT Adaption Side 2 | icontype | Real | 0 | 1 | [7 empty] | Differential\CT Adaption Side 2 | trasfgroup | Real | E | 5 | 0 | 11
[16 empty] | E | 10 | Differential\CT Adaption Side 2 | icontype | Real | 0 | 2 | [7 empty] | Differential\CT Adaption Side 2 | trasfgroup | Real | E | 7 | 0 | 12
[16 empty] | E | 11 | Differential\CT Adaption Side 2 | icontype | Real | 0 | 2 | [7 empty] | Differential\CT Adaption Side 2 | trasfgroup | Real | E | 11 | 0 | 13
[16 empty] | E | 12 | Differential\CT Adaption Side 2 | icontype | Real | 0 | 2 |  | Differential;Differential\CT Adaption Side 1;Differential\CT Adaption Side 2;Differential\CT Adaption Side 1;Differential\CT Adaption Side 2 | outserv;outserv;outserv;icontype;icontype | Real;Real;Real;Real;Real | E;E;E;E;E | 0;0;0;1;1 | 2 | Differential\CT Adaption Side 2 | trasfgroup | Real | E | 0 | 0 | 14
[16 empty] | E | 13 | Differential\CT Adaption Side 2 | icontype | Real | 0 | 2 | [7 empty] | Differential\CT Adaption Side 2 | trasfgroup | Real | E | 6 | 0 | 15
[16 empty] | E | 14 | Differential\CT Adaption Side 2 | icontype | Real | 0 | 1
[16 empty] | E | 15 | Differential\CT Adaption Side 2 | icontype | Real | 0 | 1
[16 empty] | E | 0 | Differential\CT Adaption Side 2 | trasfgroup | Real | 0 | 0
[16 empty] | E | 14 | Differential\CT Adaption Side 2 | trasfgroup | Real | 0 | 0
[16 empty] | E | 1 | Differential\CT Adaption Side 2 | trasfgroup | Real | 0 | 6
[16 empty] | E | 15 | Differential\CT Adaption Side 2 | trasfgroup | Real | 0 | 6
[16 empty] | E | 2 | Differential\CT Adaption Side 2 | trasfgroup | Real | 0 | 1
[16 empty] | E | 10 | Differential\CT Adaption Side 2 | trasfgroup | Real | 0 | 1
[16 empty] | E | 3 | Differential\CT Adaption Side 2 | trasfgroup | Real | 0 | 5
[16 empty] | E | 11 | Differential\CT Adaption Side 2 | trasfgroup | Real | 0 | 5
[16 empty] | E | 4 | Differential\CT Adaption Side 2 | trasfgroup | Real | 0 | 7
[16 empty] | E | 12 | Differential\CT Adaption Side 2 | trasfgroup | Real | 0 | 7
[16 empty] | E | 5 | Differential\CT Adaption Side 2 | trasfgroup | Real | 0 | 11
_u00DC_berstromschutz_u00DC_berstromschutz_u002D_S1_u002D_1_u00DC_I1_u002D__u00DC_berstromschutz_u002D_S1_u002D_aktiv | Overcurrent protection -> Overcurrent prot. 1 IL> side 1 | Overcurrent prot. 1 IL> side 1 | Active¦aktiv;Inactive¦inaktiv |  | IL>S1 | Enum | Schutzfunktionen | 0;1 | Real |  |  |  |  | 0 | 2 | E | 1 | Overcurrent Side 1\IL> DT | outserv | Real | 0 | 1 |  | Overcurrent Side 1 | outserv | Real | E | 0 | 2 | Overcurrent Side 1\IL> DT | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent Side 1\IL> IDMT | outserv | Real | 0 | 1 | [7 empty] | Overcurrent Side 1\IL> IDMT | outserv | Real |  |  | 1 | 0
_u00DC_berstromschutz_u00DC_berstromschutz_u002D_S1_u002D_1_u00DC_I1_u002D_Zeit_u002D_Kennlinie | Overcurrent protection -> Overcurrent prot. 1 IL> side 1 | Delay curve tIL> | Independent¦unabhängig;Inverse¦invers;Very inverse¦very_invers;Extremely inverse¦extremly_invers |  | IL>AUS1 | Enum | Schutzfunktionen | Definite;IEC 255-3 Inverse;IEC 255-3 Very Inverse;IEC 255-3 Extremely Inverse | String |  | _u00DC_berstromschutz_u00DC_berstromschutz_u002D_S1_u002D_1_u00DC_I1_u002D__u00DC_berstromschutz_u002D_S1_u002D_aktiv | E | 0 | Definite | 4 | E | Definite | Overcurrent Side 1\IL> DT | outserv | Real | 0 | 0 | 2 | Overcurrent Side 1;Overcurrent Side 1\IL> IDMT | outserv;outserv | Real;Real | E;E | 0;0 |  | Overcurrent Side 1\IL> IDMT | pcharac
[16 empty] | E | Definite | Overcurrent Side 1\IL> IDMT | outserv | Real | 0 | 1 | [13 empty] | Definite
[16 empty] | NE | Definite | Overcurrent Side 1\IL> DT | outserv | Real | 0 | 1
[16 empty] | NE | Definite | Overcurrent Side 1\IL> IDMT | outserv | Real | 0 | 0
_u00DC_berstromschutz_u00DC_berstromschutz_u002D_S1_u002D_1_u00DC_I1_u002D_Anregeschwelle_u002D_unabh_u00E4_ngig | Overcurrent protection -> Overcurrent prot. 1 IL> side 1 | Threshold independent IL> | 0.08-40.00:0.01 | In | IL>ANRS1 | Real | Schutzfunktionen | [6 empty] | 2 |  |  |  | Overcurrent Side 1\IL> DT | Ipset | Real | 1 | 0 |  | Overcurrent Side 1;Overcurrent Side 1\IL> DT | outserv;outserv | Real;Real | E;E | 0;0 |  | Overcurrent Side 1\IL> DT | Ipset | Real |  |  | 1 | 0
_u00DC_berstromschutz_u00DC_berstromschutz_u002D_S1_u002D_1_u00DC_I1_u002D_Zeitstufe_u002D_ungerichtet | Overcurrent protection -> Overcurrent prot. 1 IL> side 1 | Delay nondirectional IL> | 0.01-9.99:0.01 | s | tIL>S1 | Real | Schutzfunktionen | [6 empty] | 1 |  |  |  | Overcurrent Side 1\IL> DT | Tset | Real | 1 | 0 |  | Overcurrent Side 1;Overcurrent Side 1\IL> DT | outserv;outserv | Real;Real | E;E | 0;0 |  | Overcurrent Side 1\IL> DT | Tset | Real |  |  | 1 | 0
_u00DC_berstromschutz_u00DC_berstromschutz_u002D_S1_u002D_1_u00DC_I1_u002D_Anregeschwelle_u002D_abh_u00E4_ngig | Overcurrent protection -> Overcurrent prot. 1 IL> side 1 | Threshold inverse IL> | 0.20-4.00:0.01 | In | IL>AMZS1 | Real | Schutzfunktionen | [6 empty] | 2 |  |  |  | Overcurrent Side 1\IL> IDMT | Ipset | Real | 1 | 0 |  | Overcurrent Side 1;Overcurrent Side 1\IL> IDMT | outserv;outserv | Real;Real | E;E | 0;0 |  | Overcurrent Side 1\IL> IDMT | Ipset | Real |  |  | 1 | 0
_u00DC_berstromschutz_u00DC_berstromschutz_u002D_S1_u002D_1_u00DC_I1_u002D_Zeitfaktor_u002D_ungerichtet | Overcurrent protection -> Overcurrent prot. 1 IL> side 1 | Time factor nondirectional IL> | 0.05-2.00:0.01 | s | IL>AMZtS1 | Real | Schutzfunktionen | [6 empty] | 0.2 |  |  |  | Overcurrent Side 1\IL> IDMT | Tpset | Real | 1 | 0 |  | Overcurrent Side 1;Overcurrent Side 1\IL> IDMT | outserv;outserv | Real;Real | E;E | 0;0 |  | Overcurrent Side 1\IL> IDMT | Tpset | Real |  |  | 1 | 0
_u00DC_berstromschutz_u00DC_berstromschutz_u002D_S1_u002D_1_u00DC_I1_u002D_Maximale_u002D_Verz_u00F6_gerung | Overcurrent protection -> Overcurrent prot. 1 IL> side 1 | Maximum delay IL> | 10.00-60.00:0.01 | s | IL>AMZvS1 | Real | Schutzfunktionen | [6 empty] | 60 |  |  |  | Overcurrent Side 1\IL> IDMT | udeftmax | Real | 1 | 0 |  | Overcurrent Side 1;Overcurrent Side 1\IL> IDMT | outserv;outserv | Real;Real | E;E | 0;0 |  | Overcurrent Side 1\IL> IDMT | udeftmax | Real |  |  | 1 | 0
_u00DC_berstromschutz_u00DC_berstromschutz_u002D_S1_u002D_2_u00DC_I2_u002D__u00DC_berstromschutz_u002D_S1_u002D_aktiv | Overcurrent protection -> Overcurrent prot. 2 IL>> side 1 | Overcurrent prot. 2 IL>> side 1 | Active¦aktiv;Inactive¦inaktiv |  | IL>>S1 | Enum | Schutzfunktionen | 0;1 | Real |  |  |  |  | 0 | 2 | E | 1 | Overcurrent Side 1\IL>> DT | outserv | Real | 0 | 1 |  | Overcurrent Side 1 | outserv | Real | E | 0 | 2 | Overcurrent Side 1\IL>> DT | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent Side 1\IL>> IDMT | outserv | Real | 0 | 1 | [7 empty] | Overcurrent Side 1\IL>> IDMT | outserv | Real |  |  | 1 | 0
_u00DC_berstromschutz_u00DC_berstromschutz_u002D_S1_u002D_2_u00DC_I2_u002D_Zeit_u002D_Kennlinie | Overcurrent protection -> Overcurrent prot. 2 IL>> side 1 | Delay curve tIL>> | Independent¦unabhängig;Inverse¦invers;Very inverse¦very_invers;Extremely inverse¦extremly_invers |  | IL>>AUS1 | Enum | Schutzfunktionen | Definite;IEC 255-3 Inverse;IEC 255-3 Very Inverse;IEC 255-3 Extremely Inverse | String |  | _u00DC_berstromschutz_u00DC_berstromschutz_u002D_S1_u002D_2_u00DC_I2_u002D__u00DC_berstromschutz_u002D_S1_u002D_aktiv | E | 0 | Definite | 4 | E | Definite | Overcurrent Side 1\IL>> DT | outserv | Real | 0 | 0 | 2 | Overcurrent Side 1;Overcurrent Side 1\IL>> IDMT | outserv;outserv | Real;Real | E;E | 0;0 |  | Overcurrent Side 1\IL>> IDMT | pcharac
[16 empty] | E | Definite | Overcurrent Side 1\IL>> IDMT | outserv | Real | 0 | 1 | [13 empty] | Definite
[16 empty] | NE | Definite | Overcurrent Side 1\IL>> DT | outserv | Real | 0 | 1
[16 empty] | NE | Definite | Overcurrent Side 1\IL>> IDMT | outserv | Real | 0 | 0
_u00DC_berstromschutz_u00DC_berstromschutz_u002D_S1_u002D_2_u00DC_I2_u002D_Anregeschwelle_u002D_unabh_u00E4_ngig | Overcurrent protection -> Overcurrent prot. 2 IL>> side 1 | Threshold independent IL>> | 0.08-40.00:0.01 | In | IL>>ANRS1 | Real | Schutzfunktionen | [6 empty] | 2 |  |  |  | Overcurrent Side 1\IL>> DT | Ipset | Real | 1 | 0 |  | Overcurrent Side 1;Overcurrent Side 1\IL>> DT | outserv;outserv | Real;Real | E;E | 0;0 |  | Overcurrent Side 1\IL>> DT | Ipset | Real |  |  | 1 | 0
_u00DC_berstromschutz_u00DC_berstromschutz_u002D_S1_u002D_2_u00DC_I2_u002D_Zeitstufe_u002D_ungerichtet | Overcurrent protection -> Overcurrent prot. 2 IL>> side 1 | Delay nondirectional IL>> | 0.01-9.99:0.01 | s | tIL>>S1 | Real | Schutzfunktionen | [6 empty] | 1 |  |  |  | Overcurrent Side 1\IL>> DT | Tset | Real | 1 | 0 |  | Overcurrent Side 1;Overcurrent Side 1\IL>> DT | outserv;outserv | Real;Real | E;E | 0;0 |  | Overcurrent Side 1\IL>> DT | Tset | Real |  |  | 1 | 0
_u00DC_berstromschutz_u00DC_berstromschutz_u002D_S1_u002D_2_u00DC_I2_u002D_Anregeschwelle_u002D_abh_u00E4_ngig | Overcurrent protection -> Overcurrent prot. 2 IL>> side 1 | Threshold inverse IL>> | 0.20-10.00:0.01 | In | IL>>AMZS1 | Real | Schutzfunktionen | [6 empty] | 2 |  |  |  | Overcurrent Side 1\IL>> IDMT | Ipset | Real | 1 | 0 |  | Overcurrent Side 1;Overcurrent Side 1\IL>> IDMT | outserv;outserv | Real;Real | E;E | 0;0 |  | Overcurrent Side 1\IL>> IDMT | Ipset | Real |  |  | 1 | 0
_u00DC_berstromschutz_u00DC_berstromschutz_u002D_S1_u002D_2_u00DC_I2_u002D_Zeitfaktor_u002D_ungerichtet | Overcurrent protection -> Overcurrent prot. 2 IL>> side 1 | Time factor nondirectional IL>> | 0.05-2.00:0.01 | s | IL>>AMZtS1 | Real | Schutzfunktionen | [6 empty] | 0.2 |  |  |  | Overcurrent Side 1\IL>> IDMT | Tpset | Real | 1 | 0 |  | Overcurrent Side 1;Overcurrent Side 1\IL>> IDMT | outserv;outserv | Real;Real | E;E | 0;0 |  | Overcurrent Side 1\IL>> IDMT | Tpset | Real |  |  | 1 | 0
_u00DC_berstromschutz_u00DC_berstromschutz_u002D_S1_u002D_2_u00DC_I2_u002D_Maximale_u002D_Verz_u00F6_gerung | Overcurrent protection -> Overcurrent prot. 2 IL>> side 1 | Maximum delay IL>> | 10.00-80.00:0.01 | s | IL>>AMZvS1 | Real | Schutzfunktionen | [6 empty] | 60 |  |  |  | Overcurrent Side 1\IL>> IDMT | udeftmax | Real | 1 | 0 |  | Overcurrent Side 1;Overcurrent Side 1\IL>> IDMT | outserv;outserv | Real;Real | E;E | 0;0 |  | Overcurrent Side 1\IL>> IDMT | udeftmax | Real |  |  | 1 | 0
_u00DC_berstromschutz_u00DC_berstromschutz_u002D_S2_u002D_1_u00DC_I1_u002D__u00DC_berstromschutz_u002D_S2_u002D_aktiv | Overcurrent protection -> Overcurrent prot. 1 IL> side 2 | Overcurrent prot. 1 IL> side 2 | Active¦aktiv;Inactive¦inaktiv |  | IL>S2 | Enum | Schutzfunktionen | 0;1 | Real |  |  |  |  | 0 | 2 | E | 1 | Overcurrent Side 2\IL> DT | outserv | Real | 0 | 1 |  | Overcurrent Side 2 | outserv | Real | E | 0 | 2 | Overcurrent Side 2\IL> DT | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent Side 2\IL> IDMT | outserv | Real | 0 | 1 | [7 empty] | Overcurrent Side 2\IL> IDMT | outserv | Real |  |  | 1 | 0
_u00DC_berstromschutz_u00DC_berstromschutz_u002D_S2_u002D_1_u00DC_I1_u002D_Zeit_u002D_Kennlinie | Overcurrent protection -> Overcurrent prot. 1 IL> side 2 | Delay curve tIL> | Independent¦unabhängig;Inverse¦invers;Very inverse¦very_invers;Extremely inverse¦extremly_invers |  | IL>AUS2 | Enum | Schutzfunktionen | Definite;IEC 255-3 Inverse;IEC 255-3 Very Inverse;IEC 255-3 Extremely Inverse | String |  | _u00DC_berstromschutz_u00DC_berstromschutz_u002D_S2_u002D_1_u00DC_I1_u002D__u00DC_berstromschutz_u002D_S2_u002D_aktiv | E | 0 | Definite | 4 | E | Definite | Overcurrent Side 2\IL> DT | outserv | Real | 0 | 0 | 2 | Overcurrent Side 2;Overcurrent Side 2\IL> IDMT | outserv;outserv | Real;Real | E;E | 0;0 |  | Overcurrent Side 2\IL> IDMT | pcharac
[16 empty] | E | Definite | Overcurrent Side 2\IL> IDMT | outserv | Real | 0 | 1 | [13 empty] | Definite
[16 empty] | NE | Definite | Overcurrent Side 2\IL> DT | outserv | Real | 0 | 1
[16 empty] | NE | Definite | Overcurrent Side 2\IL> IDMT | outserv | Real | 0 | 0
_u00DC_berstromschutz_u00DC_berstromschutz_u002D_S2_u002D_1_u00DC_I1_u002D_Anregeschwelle_u002D_unabh_u00E4_ngig | Overcurrent protection -> Overcurrent prot. 1 IL> side 2 | Threshold independent IL> | 0.08-40.00:0.01 | In | IL>ANRS2 | Real | Schutzfunktionen | [6 empty] | 2 |  |  |  | Overcurrent Side 2\IL> DT | Ipset | Real | 1 | 0 |  | Overcurrent Side 2;Overcurrent Side 2\IL> DT | outserv;outserv | Real;Real | E;E | 0;0 |  | Overcurrent Side 2\IL> DT | Ipset | Real |  |  | 1 | 0
_u00DC_berstromschutz_u00DC_berstromschutz_u002D_S2_u002D_1_u00DC_I1_u002D_Zeitstufe_u002D_ungerichtet | Overcurrent protection -> Overcurrent prot. 1 IL> side 2 | Delay nondirectional IL> | 0.01-9.99:0.01 | s | tIL>S2 | Real | Schutzfunktionen | [6 empty] | 1 |  |  |  | Overcurrent Side 2\IL> DT | Tset | Real | 1 | 0 |  | Overcurrent Side 2;Overcurrent Side 2\IL> DT | outserv;outserv | Real;Real | E;E | 0;0 |  | Overcurrent Side 2\IL> DT | Tset | Real |  |  | 1 | 0
_u00DC_berstromschutz_u00DC_berstromschutz_u002D_S2_u002D_1_u00DC_I1_u002D_Anregeschwelle_u002D_abh_u00E4_ngig | Overcurrent protection -> Overcurrent prot. 1 IL> side 2 | Threshold inverse IL> | 0.20-4.00:0.01 | In | IL>AMZS2 | Real | Schutzfunktionen | [6 empty] | 2 |  |  |  | Overcurrent Side 2\IL> IDMT | Ipset | Real | 1 | 0 |  | Overcurrent Side 2;Overcurrent Side 2\IL> IDMT | outserv;outserv | Real;Real | E;E | 0;0 |  | Overcurrent Side 2\IL> IDMT | Ipset | Real |  |  | 1 | 0
_u00DC_berstromschutz_u00DC_berstromschutz_u002D_S2_u002D_1_u00DC_I1_u002D_Zeitfaktor_u002D_ungerichtet | Overcurrent protection -> Overcurrent prot. 1 IL> side 2 | Time factor nondirectional IL> | 0.05-2.00:0.01 | s | IL>AMZtS2 | Real | Schutzfunktionen | [6 empty] | 0.2 |  |  |  | Overcurrent Side 2\IL> IDMT | Tpset | Real | 1 | 0 |  | Overcurrent Side 2;Overcurrent Side 2\IL> IDMT | outserv;outserv | Real;Real | E;E | 0;0 |  | Overcurrent Side 2\IL> IDMT | Tpset | Real |  |  | 1 | 0
_u00DC_berstromschutz_u00DC_berstromschutz_u002D_S2_u002D_1_u00DC_I1_u002D_Maximale_u002D_Verz_u00F6_gerung | Overcurrent protection -> Overcurrent prot. 1 IL> side 2 | Maximum delay IL> | 10.00-60.00:0.01 | s | IL>AMZvS2 | Real | Schutzfunktionen | [6 empty] | 60 |  |  |  | Overcurrent Side 2\IL> IDMT | udeftmax | Real | 1 | 0 |  | Overcurrent Side 2;Overcurrent Side 2\IL> IDMT | outserv;outserv | Real;Real | E;E | 0;0 |  | Overcurrent Side 2\IL> IDMT | udeftmax | Real |  |  | 1 | 0
_u00DC_berstromschutz_u00DC_berstromschutz_u002D_S2_u002D_2_u00DC_I2_u002D__u00DC_berstromschutz_u002D_S2_u002D_aktiv | Overcurrent protection -> Overcurrent prot. 2 IL>> side 2 | Overcurrent prot. 2 IL>> side 2 | Active¦aktiv;Inactive¦inaktiv |  | IL>>S2 | Enum | Schutzfunktionen | 0;1 | Real |  |  |  |  | 0 | 2 | E | 1 | Overcurrent Side 2\IL>> DT | outserv | Real | 0 | 1 |  | Overcurrent Side 2 | outserv | Real | E | 0 | 2 | Overcurrent Side 2\IL>> DT | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent Side 2\IL>> IDMT | outserv | Real | 0 | 1 | [7 empty] | Overcurrent Side 2\IL>> IDMT | outserv | Real |  |  | 1 | 0
_u00DC_berstromschutz_u00DC_berstromschutz_u002D_S2_u002D_2_u00DC_I2_u002D_Zeit_u002D_Kennlinie | Overcurrent protection -> Overcurrent prot. 2 IL>> side 2 | Delay curve tIL>> | Independent¦unabhängig;Inverse¦invers;Very inverse¦very_invers;Extremely inverse¦extremly_invers |  | IL>>AUS2 | Enum | Schutzfunktionen | Definite;IEC 255-3 Inverse;IEC 255-3 Very Inverse;IEC 255-3 Extremely Inverse | String |  | _u00DC_berstromschutz_u00DC_berstromschutz_u002D_S2_u002D_2_u00DC_I2_u002D__u00DC_berstromschutz_u002D_S2_u002D_aktiv | E | 0 | Definite | 4 | E | Definite | Overcurrent Side 2\IL>> DT | outserv | Real | 0 | 0 | 2 | Overcurrent Side 2;Overcurrent Side 2\IL>> IDMT | outserv;outserv | Real;Real | E;E | 0;0 |  | Overcurrent Side 2\IL>> IDMT | pcharac
[16 empty] | E | Definite | Overcurrent Side 2\IL>> IDMT | outserv | Real | 0 | 1 | [13 empty] | Definite
[16 empty] | NE | Definite | Overcurrent Side 2\IL>> DT | outserv | Real | 0 | 1
[16 empty] | NE | Definite | Overcurrent Side 2\IL>> IDMT | outserv | Real | 0 | 0
_u00DC_berstromschutz_u00DC_berstromschutz_u002D_S2_u002D_2_u00DC_I2_u002D_Anregeschwelle_u002D_unabh_u00E4_ngig | Overcurrent protection -> Overcurrent prot. 2 IL>> side 2 | Threshold independent IL>> | 0.08-40.00:0.01 | In | IL>>ANRS2 | Real | Schutzfunktionen | [6 empty] | 2 |  |  |  | Overcurrent Side 2\IL>> DT | Ipset | Real | 1 | 0 |  | Overcurrent Side 2;Overcurrent Side 2\IL>> DT | outserv;outserv | Real;Real | E;E | 0;0 |  | Overcurrent Side 2\IL>> DT | Ipset | Real |  |  | 1 | 0
_u00DC_berstromschutz_u00DC_berstromschutz_u002D_S2_u002D_2_u00DC_I2_u002D_Zeitstufe_u002D_ungerichtet | Overcurrent protection -> Overcurrent prot. 2 IL>> side 2 | Delay nondirectional IL>> | 0.01-9.99:0.01 | s | tIL>>S2 | Real | Schutzfunktionen | [6 empty] | 1 |  |  |  | Overcurrent Side 2\IL>> DT | Tset | Real | 1 | 0 |  | Overcurrent Side 2;Overcurrent Side 2\IL>> DT | outserv;outserv | Real;Real | E;E | 0;0 |  | Overcurrent Side 2\IL>> DT | Tset | Real |  |  | 1 | 0
_u00DC_berstromschutz_u00DC_berstromschutz_u002D_S2_u002D_2_u00DC_I2_u002D_Anregeschwelle_u002D_abh_u00E4_ngig | Overcurrent protection -> Overcurrent prot. 2 IL>> side 2 | Threshold inverse IL>> | 0.20-10.00:0.01 | In | IL>>AMZS2 | Real | Schutzfunktionen | [6 empty] | 2 |  |  |  | Overcurrent Side 2\IL>> IDMT | Ipset | Real | 1 | 0 |  | Overcurrent Side 2;Overcurrent Side 2\IL>> IDMT | outserv;outserv | Real;Real | E;E | 0;0 |  | Overcurrent Side 2\IL>> IDMT | Ipset | Real |  |  | 1 | 0
_u00DC_berstromschutz_u00DC_berstromschutz_u002D_S2_u002D_2_u00DC_I2_u002D_Zeitfaktor_u002D_ungerichtet | Overcurrent protection -> Overcurrent prot. 2 IL>> side 2 | Time factor nondirectional IL>> | 0.05-2.00:0.01 | s | IL>>AMZtS2 | Real | Schutzfunktionen | [6 empty] | 0.2 |  |  |  | Overcurrent Side 2\IL>> IDMT | Tpset | Real | 1 | 0 |  | Overcurrent Side 2;Overcurrent Side 2\IL>> IDMT | outserv;outserv | Real;Real | E;E | 0;0 |  | Overcurrent Side 2\IL>> IDMT | Tpset | Real |  |  | 1 | 0
_u00DC_berstromschutz_u00DC_berstromschutz_u002D_S2_u002D_2_u00DC_I2_u002D_Maximale_u002D_Verz_u00F6_gerung | Overcurrent protection -> Overcurrent prot. 2 IL>> side 2 | Maximum delay IL>> | 10.00-80.00:0.01 | s | IL>>AMZvS2 | Real | Schutzfunktionen | [6 empty] | 60 |  |  |  | Overcurrent Side 2\IL>> IDMT | udeftmax | Real | 1 | 0 |  | Overcurrent Side 2;Overcurrent Side 2\IL>> IDMT | outserv;outserv | Real;Real | E;E | 0;0 |  | Overcurrent Side 2\IL>> IDMT | udeftmax | Real |  |  | 1 | 0
DifferentialschutzDIFF_u002D_Differentialschutz_u002D_aktiv | Differential protection | Differential protection | Active¦aktiv;Inactive¦inaktiv |  | DIFF | Enum | Schutzfunktionen | 0;1 | Real |  |  |  |  | 0 |  |  |  | Differential | outserv | Real | 1 | 0 | [7 empty] | Differential | outserv | Real |  |  | 1 | 0
DifferentialschutzDIFF_u002D_Differentialschutz_u002D_Idiff_u002D_Grundwert | Differential protection | Starting value | 0.01-0.50:0.01 | In S1 | DIFFIdiff> | Real | Schutzfunktionen | [6 empty] | 0.2 | 2 |  |  | Differential\Differential | Idiff | Real | 1 | 0 |  | Differential;Differential\Differential | outserv;outserv | Real;Real | E;E | 0;0 |  | Differential\Differential | Idiff | Real |  |  | 1 | 0
[18 empty] | Differential\Differential | Ipset1 | Real | /DifferentialschutzDIFF_u002D_Differentialschutz_u002D_Anstieg_u002D_Kennlinie | 0
DifferentialschutzDIFF_u002D_Differentialschutz_u002D_Idiff_u002D_Ende_u002D_Stabilisierung | Differential protection | Starting without stabilization | 10-20:1 | In S1 | DIFFIdiff>> | Real | Schutzfunktionen | [6 empty] | 18 |  |  |  | Differential\Differential | Idiffunrest | Real | 1 | 0 |  | Differential;Differential\Differential | outserv;outserv | Real;Real | E;E | 0;0 |  | Differential\Differential | Idiffunrest | Real |  |  | 1 | 0
DifferentialschutzDIFF_u002D_Differentialschutz_u002D_Anstieg_u002D_Kennlinie | Differential protection | Slope | 0.20-1.00:0.01 |  | DIFFmDiff | Real | Schutzfunktionen | [6 empty] | 0.5 | 2 |  |  | Differential\Differential | Irestrpercent1 | Real | 100 | 0 |  | Differential;Differential\Differential | outserv;outserv | Real;Real | E;E | 0;0 |  | Differential\Differential | Irestrpercent1 | Real |  |  | 0.01 | 0
[18 empty] | Differential\Differential | Irestrpercent2 | Real | 100 | 0
DifferentialschutzDIFF_u002D_Differentialschutz_u002D_Zusatzstabilisierung | Differential protection | Additional stabilization | 1.25-5.00:0.01 | In S1 | DIFFbStab | Real | Schutzfunktionen | [6 empty] | 1.5 |  |  |  | Differential\Differential | Ipset2 | Real | 1 | 0 |  | Differential;Differential\Differential | outserv;outserv | Real;Real | E;E | 0;0 |  | Differential\Differential | Ipset2 | Real |  |  | 1 | 0
DifferentialschutzDIFF_u002D_Differentialschutz_u002D_Ausl_u00F6_sezeit | Differential protection | Trip delay | 0.00-9.99:0.01 | s | tDIFF | Real | Schutzfunktionen | [6 empty] | 0 |  |  |  | Differential\Differential | Tset | Real | 1 | 0 |  | Differential;Differential\Differential | outserv;outserv | Real;Real | E;E | 0;0 |  | Differential\Differential | Tset | Real |  |  | 1 | 0
DifferentialschutzDIFF_u002D_Differentialschutz_u002D_Inrush_u002D_Max | Differential protection | IRushMax | 2.0-8.0:0.1 | In S1 | DIFFIRushMax | Real | Schutzfunktionen | [6 empty] | 3 |  |  |  | Differential\Differential | hblckdisthr | Real | 1 | 0 |  | Differential;Differential\Differential | outserv;outserv | Real;Real | E;E | 0;0 |  | Differential\Differential | hblckdisthr | Real |  |  | 1 | 0
DifferentialschutzDIFF_u002D_Differentialschutz_u002D_Inrush_u002D_H21 | Differential protection | Threshold for 2nd to 1st harmonic | 0.05-0.20:0.01 |  | DIFFInrushH21 | Real | Schutzfunktionen | [6 empty] | 0.15 |  |  |  | Differential\Differential | H2threshold | Real | 100 | 0 |  | Differential;Differential\Differential | outserv;outserv | Real;Real | E;E | 0;0 |  | Differential\Differential | H2threshold | Real |  |  | 0.01 | 0
DifferentialschutzDIFF_u002D_Differentialschutz_u002D_Uebererregung_u002D_H51 | Differential protection | Threshold for 5th to 1st harmonic | 0.10-0.80:0.01 |  | DIFFUebererrH51 | Real | Schutzfunktionen | [6 empty] | 0.3 |  |  |  | Differential\Differential | H5threshold | Real | 100 | 0 |  | Differential;Differential\Differential | outserv;outserv | Real;Real | E;E | 0;0 |  | Differential\Differential | H5threshold | Real |  |  | 0.01 | 0
DifferentialschutzDIFF_u002D_Differentialschutz_u002D_Nullstromelimination_u002D_SPB_u002D_in_u002D_SZ | Differential protection | Zero seq. elim. with earthing transf. in prot. zone | Active¦aktiv;Inactive¦inaktiv |  | DIFFINE | Enum | Schutzfunktionen | 1;0 | Real |  |  |  |  | 0 | 2 |  |  | Differential\CT Adaption Side 1 | iremoveI0 | Real | 1 | 0 |  | Differential;Differential\CT Adaption Side 1 | outserv;outserv | Real;Real | E;E | 0;0 |  | Differential\CT Adaption Side 1 | iremoveI0 | Real |  |  | 1 | 0
_END_ | [17 empty] | Differential\CT Adaption Side 2 | iremoveI0 | Real | 1 | 0 |  | Differential;Differential\CT Adaption Side 2 | outserv;outserv | Real;Real | E;E | 0;0 |  | Differential\CT Adaption Side 2 | iremoveI0 | Real |  |  | 1 | 0