## Mapping
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37
StationWare | [6 empty] | Common |  |  | Import | [12 empty] | Export
[8 empty] | Enumeration |  | Pre-Condition |  |  |  |  | Instruction | [7 empty] | Pre-Condition | [5 empty] | Instruction
Key | Chapter | Display name | Range | Unit | Description | Type | Group | Mapping | Type |  | Setting | Operator | Value | Default |  | Operator | Value | Target | Parameter | Type | Scale | Offset |  | Source | Parameter | Type | Operator | Value |  | Source | Parameter | Type | Operator | Value | Scale | Offset
x010_u002E_003 | Global->GRUND | 010.003 | 1.0 A¦0;5.0 A¦1 | A | Inom Gerät | Enum | Parameter__Funktionsparameter | 1;5 | Real |  |  |  |  | 1 | 2 |  |  | Measure Ph | Inom | Real | 1 | 0 | [6 empty] | 1 | Measure Ph | Inom | Real |  |  | 1 | 0
[18 empty] | Measure Seq | Inom | Real | 1 | 0
x010_u002E_026 | Global->GRUND | 010.026 | 1.0 A¦0;5.0 A¦1 | A | IE,nom Gerät | Enum | Parameter__Funktionsparameter | 1;5 | Real |  |  |  |  | 1 | 1 |  |  | Measure Zero | Inom | Real | 1 | 0 | [6 empty] | 1 | Measure Zero | Inom | Real |  |  | 1 | 0
x010_u002E_009 | Global->GRUND | 010.009 | 50-130:1 | V | Unom Wandler sek. | Real | Parameter__Funktionsparameter | [6 empty] | 100 | 4 |  |  | Measure Ph | Unom | Real | 1 | 0 | [6 empty] | 1 | Measure Ph | Unom | Real |  |  | 1 | 0
[18 empty] | Measure Delta | Unom | Real | 1 | 0
[18 empty] | Measure Seq | Unom | Real | 1 | 0
[18 empty] | Measure Freq | Unom | Real | 1 | 0
x010_u002E_028 | Global->GRUND | 010.028 | 50-130:1 | V | UNE,nom Wandler sek. | Real | Parameter__Funktionsparameter | [6 empty] | 100 | 1 |  |  | Measure Zero | Unom | Real | 1 | 0 | [6 empty] | 1 | Measure Zero | Unom | Real |  |  | 1 | 0
x003_u002E_060 | Global->PSU | 003.060 | Parametersatz 1¦0;Parametersatz 2¦1;Parametersatz 3¦2;Parametersatz 4¦3 |  | Auswahl PS BED | Enum | Parameter__Funktionsparameter | Parameter subset 1;Parameter subset 2;Parameter subset 3;Parameter subset 4 | String
x018_u002E_202 | Hauptfunktionen->f<> | 018.202 | Spannung U1E¦0;Spannung U2E¦1;Spannung U3E¦2;Spannung U12¦3;Spannung U23¦4;Spannung U31¦5 |  | Meßspannungsauswahl | Enum | Parameter__Funktionsparameter | 3;4;5;0;1;2 | Real |  |  |  |  | 0 | 1 |  |  | Measure Freq | imeasv | Real | 1 | 0 | [6 empty] | 1 | Measure Freq | imeasv | Real |  |  | 1 | 0
x018_u002E_201 | Hauptfunktionen->f<> | 018.201 | 3-6:1 | Perioden | Auswertezeit | Real | Parameter__Funktionsparameter | [6 empty] | 5 | 1 |  |  | Measure Freq | Tfe | Real | 0.02 | 0 | [6 empty] | 1 | Measure Freq | Tfe | Real |  |  | 50 | 0
x022_u002E_075 | Hauptfunktionen->UMZ | 022.075 | nein¦0;ja¦1 |  | eingeschaltet BED | Enum | Parameter__Funktionsparameter | 1;0 | Real |  |  |  |  | 1 | 13 | E | 1 | Overcurrent\DTOC I> | outserv | Real | 0 | 1 | [6 empty] | 13 | Overcurrent | outserv | Real | E | 1 | 0 | 1
[16 empty] | E | 1 | Overcurrent\DTOC I>> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC I> | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\DTOC I>>> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC I>> | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\DTOC Ineg> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC I>>> | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\DTOC Ineg>> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC I>>>> | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\DTOC Ineg>>> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC Ineg> | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\DTOC IN> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC Ineg>> | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\DTOC IN>> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC Ineg>>> | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\DTOC IN>>> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC Ineg>>>> | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\DTOC IN>>>> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC IN> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\DTOC IN>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\DTOC I>>>> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC IN>>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\DTOC Ineg>>>> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC IN>>>> | outserv | Real | E | 0 | 0 | 0
x017_u002E_096 | Hauptfunktionen->AMZ_1 | 017.096 | nein¦0;ja¦1 |  | eingeschaltet BED | Enum | Parameter__Funktionsparameter | 1;0 | Real |  |  |  |  | 1 | 3 | E | 1 | Overcurrent\IDMT1 P | outserv | Real | 0 | 1 | [6 empty] | 4 | Overcurrent | outserv | Real | E | 1 | 0 | 1
[16 empty] | E | 1 | Overcurrent\IDMT1 neg | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\IDMT1 P | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\IDMT1 N | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\IDMT1 neg | outserv | Real | E | 0 | 0 | 0
[30 empty] | Overcurrent\IDMT1 N | outserv | Real | E | 0 | 0 | 0
x017_u002E_052 | Hauptfunktionen->AMZ_2 | 017.052 | nein¦0;ja¦1 |  | eingeschaltet BED | Enum | Parameter__Funktionsparameter | 1;0 | Real |  |  |  |  | 1 | 3 | E | 1 | Overcurrent\IDMT2 P | outserv | Real | 0 | 1 | [6 empty] | 4 | Overcurrent | outserv | Real | E | 1 | 0 | 1
[16 empty] | E | 1 | Overcurrent\IDMT2 neg | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\IDMT2 P | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\IDMT2 N | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\IDMT2 neg | outserv | Real | E | 0 | 0 | 0
[30 empty] | Overcurrent\IDMT2 N | outserv | Real | E | 0 | 0 | 0
x017_u002E_070 | Hauptfunktionen->KURI | 017.070 | nein¦0;ja¦1 |  | eingeschaltet BED | Enum | Parameter__Funktionsparameter | 1;0 | Real |  |  |  |  | 1 | 2 | E | 1 | Overcurrent\Directional P | outserv | Real | 0 | 1 | [6 empty] | 3 | Overcurrent | outserv | Real | E | 1 | 0 | 1
[16 empty] | E | 1 | Overcurrent\Directional N | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\Directional P | outserv | Real | E | 0 | 0 | 0
[30 empty] | Overcurrent\Directional N | outserv | Real | E | 0 | 0 | 0
x023_u002E_030 | Hauptfunktionen->U<> | 023.030 | nein¦0;ja¦1 |  | eingeschaltet BED | Enum | Parameter__Funktionsparameter | 1;0 | Real |  |  |  |  | 1 | 7 | E | 1 | Voltage | outserv | Real | 0 | 1 | [6 empty] | 1 | Voltage | outserv | Real |  |  | 1 | 0
[18 empty] | Voltage\V>>> | outserv | Real | 0 | 1
[18 empty] | Voltage\V<<< | outserv | Real | 0 | 1
[18 empty] | Voltage\tV>> 3-pole | outserv | Real | 0 | 1
[18 empty] | Voltage\tV<< 3-pole | outserv | Real | 0 | 1
[18 empty] | Voltage\tV>>> 3-pole | outserv | Real | 0 | 1
[18 empty] | Voltage\tV<<< 3-pole | outserv | Real | 0 | 1
x023_u002E_031 | Hauptfunktionen->f<> | 023.031 | nein¦0;ja¦1 |  | eingeschaltet BED | Enum | Parameter__Funktionsparameter | 1;0 | Real |  |  |  |  | 1 | 3 | E | 1 | Frequency | outserv | Real | 0 | 1 | [6 empty] | 1 | Frequency | outserv | Real |  |  | 1 | 0
[18 empty] | Frequency\df5/dt | outserv | Real | 0 | 1
[18 empty] | Frequency\f5 | outserv | Real | 0 | 1
x072_u002E_098 | Parametersatz 1->UMZ | 072.098 | nein¦0;ja¦1 |  | Freigabe PS1 | Enum | Parameter__Funktionsparameter | 1;0 | Real | 1 | x003_u002E_060;x022_u002E_075 | E;NE | Parameter subset 1;1 | 1 | 10 | E | 1 | Overcurrent\DTOC I> | outserv | Real | 0 | 1 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 10 | Overcurrent\DTOC I> | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\DTOC I>> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC I>> | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\DTOC I>>> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC I>>> | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\DTOC Ineg> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC Ineg> | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\DTOC Ineg>> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC Ineg>> | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\DTOC Ineg>>> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC Ineg>>> | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\DTOC Ineg>>>> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC Ineg>>>> | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\DTOC IN> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC IN> | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\DTOC IN>> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC IN>> | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\DTOC IN>>> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC IN>>> | outserv | Real | E | 0 | 0 | 0
x017_u002E_000 | Parametersatz 1->UMZ | 017.000 | 0.1-40:0.01;blockiert=40.02 | Inom | I> PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x072_u002E_098 | E;NE;NE | Parameter subset 1;1;1 | 1 | 3 | SE | 40 | Overcurrent\DTOC I> | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Overcurrent\DTOC I> | outserv | Real | E | 1 | 0 | 40.02
[16 empty] | SE | 40 | Overcurrent\DTOC I> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\DTOC I> | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 40.02 | Overcurrent\DTOC I> | outserv | Real | 0 | 1
x017_u002E_001 | Parametersatz 1->UMZ | 017.001 | 0.1-40:0.01;blockiert=40.02 | Inom | I>> PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x072_u002E_098 | E;NE;NE | Parameter subset 1;1;1 | 4 | 3 | SE | 40 | Overcurrent\DTOC I>> | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Overcurrent\DTOC I>> | outserv | Real | E | 1 | 0 | 40.02
[16 empty] | SE | 40 | Overcurrent\DTOC I>> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\DTOC I>> | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 40.02 | Overcurrent\DTOC I>> | outserv | Real | 0 | 1
x017_u002E_002 | Parametersatz 1->UMZ | 017.002 | 0.1-40:0.01;blockiert=40.02 | Inom | I>>> PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x072_u002E_098 | E;NE;NE | Parameter subset 1;1;1 | 40.02 | 4 | SE | 40 | Overcurrent\DTOC I>>> | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Overcurrent\DTOC I>>> | outserv | Real | E | 1 | 0 | 40.02
[16 empty] | SE | 40 | Overcurrent\DTOC I>>> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\DTOC I>>> | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 40.02 | Overcurrent\DTOC I>>> | outserv | Real | 0 | 1
[18 empty] | Overcurrent\DTOC I>>> | idir | Real | 0 | 0
x017_u002E_004 | Parametersatz 1->UMZ | 017.004 | 0-100:0.01;blockiert=100.02 | s | tI> PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x072_u002E_098 | E;NE;NE | Parameter subset 1;1;1 | 1 | 2 | SE | 100 | Overcurrent\DTOC I> | Tset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Overcurrent\DTOC I> | Tset | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Overcurrent\DTOC I> | Tset | Real | 0 | 9999999 | [7 empty] | Overcurrent\DTOC I> | Tset | Real |  |  | 0 | 100.02
x017_u002E_006 | Parametersatz 1->UMZ | 017.006 | 0-100:0.01;blockiert=100.02 | s | tI>> PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x072_u002E_098 | E;NE;NE | Parameter subset 1;1;1 | 0.5 | 2 | SE | 100 | Overcurrent\DTOC I>> | Tset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Overcurrent\DTOC I>> | Tset | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Overcurrent\DTOC I>> | Tset | Real | 0 | 9999999 | [7 empty] | Overcurrent\DTOC I>> | Tset | Real |  |  | 0 | 100.02
x017_u002E_007 | Parametersatz 1->UMZ | 017.007 | 0-100:0.01;blockiert=100.02 | s | tI>>> PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x072_u002E_098 | E;NE;NE | Parameter subset 1;1;1 | 0.5 | 2 | SE | 100 | Overcurrent\DTOC I>>> | Tset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Overcurrent\DTOC I>>> | Tset | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Overcurrent\DTOC I>>> | Tset | Real | 0 | 9999999 | [7 empty] | Overcurrent\DTOC I>>> | Tset | Real |  |  | 0 | 100.02
x072_u002E_011 | Parametersatz 1->UMZ | 072.011 | 0.1-25:0.01;blockiert=25.02 | Inom | Igegen> PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x072_u002E_098 | E;NE;NE | Parameter subset 1;1;1 | 1 | 3 | SE | 25 | Overcurrent\DTOC Ineg> | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Overcurrent\DTOC Ineg> | outserv | Real | E | 1 | 0 | 25.02
[16 empty] | SE | 25 | Overcurrent\DTOC Ineg> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\DTOC Ineg> | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 25.02 | Overcurrent\DTOC Ineg> | outserv | Real | 0 | 1
x072_u002E_012 | Parametersatz 1->UMZ | 072.012 | 0.1-25:0.01;blockiert=25.02 | Inom | Igegen>> PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x072_u002E_098 | E;NE;NE | Parameter subset 1;1;1 | 4 | 3 | SE | 25 | Overcurrent\DTOC Ineg>> | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Overcurrent\DTOC Ineg>> | outserv | Real | E | 1 | 0 | 25.02
[16 empty] | SE | 25 | Overcurrent\DTOC Ineg>> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\DTOC Ineg>> | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 25.02 | Overcurrent\DTOC Ineg>> | outserv | Real | 0 | 1
x072_u002E_013 | Parametersatz 1->UMZ | 072.013 | 0.1-25:0.01;blockiert=25.02 | Inom | Igegen>>> PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x072_u002E_098 | E;NE;NE | Parameter subset 1;1;1 | 25.02 | 3 | SE | 25 | Overcurrent\DTOC Ineg>>> | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Overcurrent\DTOC Ineg>>> | outserv | Real | E | 1 | 0 | 25.02
[16 empty] | SE | 25 | Overcurrent\DTOC Ineg>>> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\DTOC Ineg>>> | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 25.02 | Overcurrent\DTOC Ineg>>> | outserv | Real | 0 | 1
x072_u002E_023 | Parametersatz 1->UMZ | 072.023 | 0-100:0.01;blockiert=100.02 | s | tIgegen> PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x072_u002E_098 | E;NE;NE | Parameter subset 1;1;1 | 1 | 2 | SE | 100 | Overcurrent\DTOC Ineg> | Tset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Overcurrent\DTOC Ineg> | Tset | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Overcurrent\DTOC Ineg> | Tset | Real | 0 | 9999999 | [7 empty] | Overcurrent\DTOC Ineg> | Tset | Real |  |  | 0 | 100.02
x072_u002E_024 | Parametersatz 1->UMZ | 072.024 | 0-100:0.01;blockiert=100.02 | s | tIgegen>> PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x072_u002E_098 | E;NE;NE | Parameter subset 1;1;1 | 0.5 | 2 | SE | 100 | Overcurrent\DTOC Ineg>> | Tset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Overcurrent\DTOC Ineg>> | Tset | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Overcurrent\DTOC Ineg>> | Tset | Real | 0 | 9999999 | [7 empty] | Overcurrent\DTOC Ineg>> | Tset | Real |  |  | 0 | 100.02
x072_u002E_025 | Parametersatz 1->UMZ | 072.025 | 0-100:0.01;blockiert=100.02 | s | tIgegen>>> PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x072_u002E_098 | E;NE;NE | Parameter subset 1;1;1 | 100.02 | 2 | SE | 100 | Overcurrent\DTOC Ineg>>> | Tset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Overcurrent\DTOC Ineg>>> | Tset | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Overcurrent\DTOC Ineg>>> | Tset | Real | 0 | 9999999 | [7 empty] | Overcurrent\DTOC Ineg>>> | Tset | Real |  |  | 0 | 100.02
x017_u002E_003 | Parametersatz 1->UMZ | 017.003 | 0.002-8:0.001;blockiert=8.002 | Inom | IE> PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x072_u002E_098 | E;NE;NE | Parameter subset 1;1;1 | 0.25 | 3 | SE | 8 | Overcurrent\DTOC IN> | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Overcurrent\DTOC IN> | outserv | Real | E | 1 | 0 | 8.002
[16 empty] | SE | 8 | Overcurrent\DTOC IN> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\DTOC IN> | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 8.002 | Overcurrent\DTOC IN> | outserv | Real | 0 | 1
x017_u002E_009 | Parametersatz 1->UMZ | 017.009 | 0.002-8:0.001;blockiert=8.002 | Inom | IE>> PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x072_u002E_098 | E;NE;NE | Parameter subset 1;1;1 | 8.002 | 3 | SE | 8 | Overcurrent\DTOC IN>> | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Overcurrent\DTOC IN>> | outserv | Real | E | 1 | 0 | 8.002
[16 empty] | SE | 8 | Overcurrent\DTOC IN>> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\DTOC IN>> | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 8.002 | Overcurrent\DTOC IN>> | outserv | Real | 0 | 1
x017_u002E_018 | Parametersatz 1->UMZ | 017.018 | 0.002-8:0.001;blockiert=8.002 | Inom | IE>>> PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x072_u002E_098 | E;NE;NE | Parameter subset 1;1;1 | 8.002 | 4 | SE | 8 | Overcurrent\DTOC IN>>> | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Overcurrent\DTOC IN>>> | outserv | Real | E | 1 | 0 | 8.002
[16 empty] | SE | 8 | Overcurrent\DTOC IN>>> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\DTOC IN>>> | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 8.002 | Overcurrent\DTOC IN>>> | outserv | Real | 0 | 1
[18 empty] | Overcurrent\DTOC IN>>> | idir | Real | 0 | 0
x072_u002E_018 | Parametersatz 1->UMZ | 072.018 | 0.1-40:0.01;blockiert=40.02 | Inom | IE>>>> PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x072_u002E_098 | E;NE;NE | Parameter subset 1;1;1 | 40.02 | 3 | SE | 40 | Overcurrent\DTOC IN>>>> | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Overcurrent\DTOC IN>>>> | outserv | Real | E | 1 | 0 | 40.02
[16 empty] | SE | 40 | Overcurrent\DTOC IN>>>> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\DTOC IN>>>> | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 40.02 | Overcurrent\DTOC IN>>>> | outserv | Real | 0 | 1
x017_u002E_008 | Parametersatz 1->UMZ | 017.008 | 0-100:0.01;blockiert=100.02 | s | tIE> PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x072_u002E_098 | E;NE;NE | Parameter subset 1;1;1 | 1 | 2 | SE | 100 | Overcurrent\DTOC IN> | Tset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Overcurrent\DTOC IN> | Tset | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Overcurrent\DTOC IN> | Tset | Real | 0 | 9999999 | [7 empty] | Overcurrent\DTOC IN> | Tset | Real |  |  | 0 | 100.02
x017_u002E_010 | Parametersatz 1->UMZ | 017.010 | 0-100:0.01;blockiert=100.02 | s | tIE>> PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x072_u002E_098 | E;NE;NE | Parameter subset 1;1;1 | 0.5 | 2 | SE | 100 | Overcurrent\DTOC IN>> | Tset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Overcurrent\DTOC IN>> | Tset | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Overcurrent\DTOC IN>> | Tset | Real | 0 | 9999999 | [7 empty] | Overcurrent\DTOC IN>> | Tset | Real |  |  | 0 | 100.02
x017_u002E_019 | Parametersatz 1->UMZ | 017.019 | 0-100:0.01;blockiert=100.02 | s | tIE>>> PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x072_u002E_098 | E;NE;NE | Parameter subset 1;1;1 | 0.5 | 2 | SE | 100 | Overcurrent\DTOC IN>>> | Tset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Overcurrent\DTOC IN>>> | Tset | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Overcurrent\DTOC IN>>> | Tset | Real | 0 | 9999999 | [7 empty] | Overcurrent\DTOC IN>>> | Tset | Real |  |  | 0 | 100.02
x072_u002E_030 | Parametersatz 1->UMZ | 072.030 | 0-100:0.01;blockiert=100.02 | s | tIE>>>> PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x072_u002E_098 | E;NE;NE | Parameter subset 1;1;1 | 0.5 | 2 | SE | 100 | Overcurrent\DTOC IN>>>> | Tset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Overcurrent\DTOC IN>>>> | Tset | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Overcurrent\DTOC IN>>>> | Tset | Real | 0 | 9999999 | [7 empty] | Overcurrent\DTOC IN>>>> | Tset | Real |  |  | 0 | 100.02
x072_u002E_070 | Parametersatz 1->AMZ_1 | 072.070 | nein¦0;ja¦1 |  | Freigabe PS1 | Enum | Parameter__Funktionsparameter | 1;0 | Real | 1 | x003_u002E_060;x017_u002E_096 | E;NE | Parameter subset 1;1 | 1 | 6 | E | 1 | Overcurrent\IDMT1 P | outserv | Real | 0 | 1 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 3 | Overcurrent\IDMT1 P | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\IDMT1 neg | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\IDMT1 neg | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\IDMT1 N | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\IDMT1 N | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 0 | Overcurrent\IDMT1 P | ModFrame | Real | 0 | 1
[16 empty] | E | 0 | Overcurrent\IDMT1 neg | ModFrame | Real | 0 | 1
[16 empty] | E | 0 | Overcurrent\IDMT1 N | ModFrame | Real | 0 | 1
x072_u002E_050 | Parametersatz 1->AMZ_1 | 072.050 | 0.1-4:0.01;blockiert=4.02 | Inom | IB,L PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x017_u002E_096;x072_u002E_070 | E;NE;NE | Parameter subset 1;1;1 | 1 | 4 | SE | 4 | Overcurrent\IDMT1 P | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Overcurrent\IDMT1 P | outserv | Real | E | 1 | 0 | 4.02
[16 empty] | SE | 4 | Overcurrent\IDMT1 P | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\IDMT1 P | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 4.02 | Overcurrent\IDMT1 P | outserv | Real | 0 | 1
[18 empty] | Overcurrent\IDMT1 KI P | outserv | Real | 0 | 1
x072_u002E_056 | Parametersatz 1->AMZ_1 | 072.056 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Kennlinientyp L PS1 | Enum | Parameter__Funktionsparameter | Definite Time;IEC Standard Inverse;IEC Very Inverse;IEC Extremely Inverse;IEC Long Time Inverse;IEEE Moderately Inverse;IEEE Very Inverse;IEEE Extremely Inverse;ANSI Normally Inverse;ANSI Short Time Inverse;ANSI Long Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | 1 | x003_u002E_060 | E | Parameter subset 1 | Definite Time | 1 |  |  | Overcurrent\IDMT1 P | pcharac | String |  |  | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 1 | Overcurrent\IDMT1 P | pcharac | String
x072_u002E_053 | Parametersatz 1->AMZ_1 | 072.053 | 0.05-10:0.01 |  | Kennl.fakt. kt,L PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 1 | 1 | 2 |  |  | Overcurrent\IDMT1 P | Tpset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 1 | Overcurrent\IDMT1 P | Tpset | Real |  |  | 1 | 0
[18 empty] | Overcurrent\IDMT1 P | Tadder | Real | 0 | 0
x072_u002E_077 | Parametersatz 1->AMZ_1 | 072.077 | 0-10:0.001 | s | min. Auslösez. L PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 1 | 0 | 1 |  |  | Overcurrent\IDMT1 P | minresptime | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 1 | Overcurrent\IDMT1 P | minresptime | Real |  |  | 1 | 0
x072_u002E_059 | Parametersatz 1->AMZ_1 | 072.059 | unverzögert¦0;verzögert gem. Kennl¦1 |  | Rückfallen L PS1 | Enum | Parameter__Funktionsparameter | 0;1 | Real | 3 | x003_u002E_060;x072_u002E_056 | E;SW | Parameter subset 1;IEEE | 0 | 1 |  |  | Overcurrent\IDMT1 P | resetdis | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 1 | Overcurrent\IDMT1 P | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x072_u002E_056 | E;SW | Parameter subset 1;ANSI |  | 1 |  |  | Overcurrent\IDMT1 P | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | Parameter subset 1 |  | 1 |  |  | Overcurrent\IDMT1 P | resetdis | Real | 0 | 0
x072_u002E_051 | Parametersatz 1->AMZ_1 | 072.051 | 0.01-4:0.01;blockiert=4.02 | Inom | IB,gegen PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x017_u002E_096;x072_u002E_070 | E;NE;NE | Parameter subset 1;1;1 | 1 | 4 | SE | 4 | Overcurrent\IDMT1 neg | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Overcurrent\IDMT1 neg | outserv | Real | E | 1 | 0 | 4.02
[16 empty] | SE | 4 | Overcurrent\IDMT1 neg | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\IDMT1 neg | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 4.02 | Overcurrent\IDMT1 neg | outserv | Real | 0 | 1
[18 empty] | Overcurrent\IDMT1 KI neg | outserv | Real | 0 | 1
x072_u002E_057 | Parametersatz 1->AMZ_1 | 072.057 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Kennl.typ gegen PS1 | Enum | Parameter__Funktionsparameter | Definite Time;IEC Standard Inverse;IEC Very Inverse;IEC Extremely Inverse;IEC Long Time Inverse;IEEE Moderately Inverse;IEEE Very Inverse;IEEE Extremely Inverse;ANSI Normally Inverse;ANSI Short Time Inverse;ANSI Long Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | 1 | x003_u002E_060 | E | Parameter subset 1 | Definite Time | 1 |  |  | Overcurrent\IDMT1 neg | pcharac | String |  |  | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 1 | Overcurrent\IDMT1 neg | pcharac | String
x072_u002E_054 | Parametersatz 1->AMZ_1 | 072.054 | 0.05-10:0.01 |  | Kennl.f. kt,gegn PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 1 | 1 | 2 |  |  | Overcurrent\IDMT1 neg | Tpset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 1 | Overcurrent\IDMT1 neg | Tpset | Real |  |  | 1 | 0
[18 empty] | Overcurrent\IDMT1 neg | Tadder | Real | 0 | 0
x072_u002E_078 | Parametersatz 1->AMZ_1 | 072.078 | 0-10:0.001 | s | min.Auslösez.geg PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 1 | 0 | 1 |  |  | Overcurrent\IDMT1 neg | minresptime | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 1 | Overcurrent\IDMT1 neg | minresptime | Real |  |  | 1 | 0
x072_u002E_060 | Parametersatz 1->AMZ_1 | 072.060 | unverzögert¦0;verzögert gem. Kennl¦1 |  | Rückfallen gegen PS1 | Enum | Parameter__Funktionsparameter | 0;1 | Real | 3 | x003_u002E_060;x072_u002E_057 | E;SW | Parameter subset 1;IEEE | 0 | 1 |  |  | Overcurrent\IDMT1 neg | resetdis | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 1 | Overcurrent\IDMT1 neg | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x072_u002E_057 | E;SW | Parameter subset 1;ANSI |  | 1 |  |  | Overcurrent\IDMT1 neg | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | Parameter subset 1 |  | 1 |  |  | Overcurrent\IDMT1 neg | resetdis | Real | 0 | 0
x072_u002E_052 | Parametersatz 1->AMZ_1 | 072.052 | 0.01-4:0.01;blockiert=4.02 | Inom | IB,E PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x017_u002E_096;x072_u002E_070 | E;NE;NE | Parameter subset 1;1;1 | 1 | 4 | SE | 4 | Overcurrent\IDMT1 N | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Overcurrent\IDMT1 N | outserv | Real | E | 1 | 0 | 4.02
[16 empty] | SE | 4 | Overcurrent\IDMT1 N | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\IDMT1 N | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 4.02 | Overcurrent\IDMT1 N | outserv | Real | 0 | 1
[18 empty] | Overcurrent\IDMT1 KI N | outserv | Real | 0 | 1
x072_u002E_058 | Parametersatz 1->AMZ_1 | 072.058 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Kennlinientyp E PS1 | Enum | Parameter__Funktionsparameter | Definite Time;IEC Standard Inverse;IEC Very Inverse;IEC Extremely Inverse;IEC Long Time Inverse;IEEE Moderately Inverse;IEEE Very Inverse;IEEE Extremely Inverse;ANSI Normally Inverse;ANSI Short Time Inverse;ANSI Long Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | 1 | x003_u002E_060 | E | Parameter subset 1 | Definite Time | 1 |  |  | Overcurrent\IDMT1 N | pcharac | String |  |  | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 1 | Overcurrent\IDMT1 N | pcharac | String
x072_u002E_055 | Parametersatz 1->AMZ_1 | 072.055 | 0.05-10:0.01 |  | Kennl.f. kt,E PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 1 | 1 | 2 |  |  | Overcurrent\IDMT1 N | Tpset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 1 | Overcurrent\IDMT1 N | Tpset | Real |  |  | 1 | 0
[18 empty] | Overcurrent\IDMT1 N | Tadder | Real | 0 | 0
x072_u002E_079 | Parametersatz 1->AMZ_1 | 072.079 | 0-10:0.001 | s | min. Auslösez.E PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 1 | 0 | 1 |  |  | Overcurrent\IDMT1 N | minresptime | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 1 | Overcurrent\IDMT1 N | minresptime | Real |  |  | 1 | 0
x072_u002E_061 | Parametersatz 1->AMZ_1 | 072.061 | unverzögert¦0;verzögert gem. Kennl¦1 |  | Rückfallen E PS1 | Enum | Parameter__Funktionsparameter | 0;1 | Real | 3 | x003_u002E_060;x072_u002E_058 | E;SW | Parameter subset 1;IEEE | 0 | 1 |  |  | Overcurrent\IDMT1 N | resetdis | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 1 | Overcurrent\IDMT1 N | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x072_u002E_058 | E;SW | Parameter subset 1;ANSI |  | 1 |  |  | Overcurrent\IDMT1 N | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | Parameter subset 1 |  | 1 |  |  | Overcurrent\IDMT1 N | resetdis | Real | 0 | 0
x076_u002E_042 | Parametersatz 1->AMZ_2 | 076.042 | nein¦0;ja¦1 |  | Freigabe PS1 | Enum | Parameter__Funktionsparameter | 1;0 | Real | 1 | x003_u002E_060;x017_u002E_052 | E;NE | Parameter subset 1;1 | 1 | 6 | E | 1 | Overcurrent\IDMT2 P | outserv | Real | 0 | 1 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 3 | Overcurrent\IDMT2 P | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\IDMT2 neg | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\IDMT2 neg | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\IDMT2 N | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\IDMT2 N | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 0 | Overcurrent\IDMT2 P | ModFrame | Real | 0 | 1
[16 empty] | E | 0 | Overcurrent\IDMT2 neg | ModFrame | Real | 0 | 1
[16 empty] | E | 0 | Overcurrent\IDMT2 N | ModFrame | Real | 0 | 1
x076_u002E_236 | Parametersatz 1->AMZ_2 | 076.236 | 0.1-4:0.01;blockiert=4.02 | Inom | IB,L PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x017_u002E_052;x076_u002E_042 | E;NE;NE | Parameter subset 1;1;1 | 1 | 3 | SE | 4 | Overcurrent\IDMT2 P | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Overcurrent\IDMT2 P | outserv | Real | E | 1 | 0 | 4.02
[16 empty] | SE | 4 | Overcurrent\IDMT2 P | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\IDMT2 P | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 4.02 | Overcurrent\IDMT2 P | outserv | Real | 0 | 1
x071_u002E_004 | Parametersatz 1->AMZ_2 | 071.004 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Kennlinientyp L PS1 | Enum | Parameter__Funktionsparameter | Definite Time;IEC Standard Inverse;IEC Very Inverse;IEC Extremely Inverse;IEC Long Time Inverse;IEEE Moderately Inverse;IEEE Very Inverse;IEEE Extremely Inverse;ANSI Normally Inverse;ANSI Short Time Inverse;ANSI Long Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | 1 | x003_u002E_060 | E | Parameter subset 1 | Definite Time | 1 |  |  | Overcurrent\IDMT2 P | pcharac | String |  |  | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 1 | Overcurrent\IDMT2 P | pcharac | String
x078_u002E_250 | Parametersatz 1->AMZ_2 | 078.250 | 0.05-10:0.01 |  | Kennl.fakt. kt,L PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 1 | 1 | 1 |  |  | Overcurrent\IDMT2 P | Tpset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 1 | Overcurrent\IDMT2 P | Tpset | Real |  |  | 1 | 0
x071_u002E_044 | Parametersatz 1->AMZ_2 | 071.044 | 0-10:0.001 | s | min. Auslösez. L PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 1 | 0 | 1 |  |  | Overcurrent\IDMT2 P | minresptime | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 1 | Overcurrent\IDMT2 P | minresptime | Real |  |  | 1 | 0
x071_u002E_016 | Parametersatz 1->AMZ_2 | 071.016 | unverzögert¦0;verzögert gem. Kennl¦1 |  | Rückfallen L PS1 | Enum | Parameter__Funktionsparameter | 0;1 | Real | 3 | x003_u002E_060;x071_u002E_004 | E;SW | Parameter subset 1;IEEE | 0 | 1 |  |  | Overcurrent\IDMT2 P | resetdis | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 1 | Overcurrent\IDMT2 P | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x071_u002E_004 | E;SW | Parameter subset 1;ANSI |  | 1 |  |  | Overcurrent\IDMT2 P | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | Parameter subset 1 |  | 1 |  |  | Overcurrent\IDMT2 P | resetdis | Real | 0 | 0
x076_u002E_250 | Parametersatz 1->AMZ_2 | 076.250 | 0.01-4:0.01;blockiert=4.02 | Inom | IB,gegen PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x017_u002E_052;x076_u002E_042 | E;NE;NE | Parameter subset 1;1;1 | 1 | 3 | SE | 4 | Overcurrent\IDMT2 neg | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Overcurrent\IDMT2 neg | outserv | Real | E | 1 | 0 | 4.02
[16 empty] | SE | 4 | Overcurrent\IDMT2 neg | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\IDMT2 neg | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 4.02 | Overcurrent\IDMT2 neg | outserv | Real | 0 | 1
x071_u002E_008 | Parametersatz 1->AMZ_2 | 071.008 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Kennl.typ gegen PS1 | Enum | Parameter__Funktionsparameter | Definite Time;IEC Standard Inverse;IEC Very Inverse;IEC Extremely Inverse;IEC Long Time Inverse;IEEE Moderately Inverse;IEEE Very Inverse;IEEE Extremely Inverse;ANSI Normally Inverse;ANSI Short Time Inverse;ANSI Long Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | 1 | x003_u002E_060 | E | Parameter subset 1 | Definite Time | 1 |  |  | Overcurrent\IDMT2 neg | pcharac | String |  |  | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 1 | Overcurrent\IDMT2 neg | pcharac | String
x079_u002E_250 | Parametersatz 1->AMZ_2 | 079.250 | 0.05-10:0.01 |  | Kennl.f. kt,gegn PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 1 | 1 | 1 |  |  | Overcurrent\IDMT2 neg | Tpset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 1 | Overcurrent\IDMT2 neg | Tpset | Real |  |  | 1 | 0
x071_u002E_048 | Parametersatz 1->AMZ_2 | 071.048 | 0-10:0.001 | s | min.Auslösez.geg PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 1 | 0 | 1 |  |  | Overcurrent\IDMT2 neg | minresptime | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 1 | Overcurrent\IDMT2 neg | minresptime | Real |  |  | 1 | 0
x071_u002E_020 | Parametersatz 1->AMZ_2 | 071.020 | unverzögert¦0;verzögert gem. Kennl¦1 |  | Rückfallen gegen PS1 | Enum | Parameter__Funktionsparameter | 0;1 | Real | 1 | x003_u002E_060;x071_u002E_008 | E;SW | Parameter subset 1;IEEE | 0 | 1 |  |  | Overcurrent\IDMT2 neg | resetdis | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 1 | Overcurrent\IDMT2 neg | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x071_u002E_008 | E;SW | Parameter subset 1;ANSI |  | 1 |  |  | Overcurrent\IDMT2 neg | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | Parameter subset 1 |  | 1 |  |  | Overcurrent\IDMT2 neg | resetdis | Real | 0 | 0
x077_u002E_250 | Parametersatz 1->AMZ_2 | 077.250 | 0.01-4:0.01;blockiert=4.02 | Inom | IB,E PS1 | Real | Parameter__Funktionsparameter |  |  | 3 | x003_u002E_060;x017_u002E_052;x076_u002E_042 | E;NE;NE | Parameter subset 1;1;1 | 1 | 3 | SE | 4 | Overcurrent\IDMT2 N | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Overcurrent\IDMT2 N | outserv | Real | E | 1 | 0 | 4.02
[16 empty] | SE | 4 | Overcurrent\IDMT2 N | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\IDMT2 N | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 4.02 | Overcurrent\IDMT2 N | outserv | Real | 0 | 1
x071_u002E_012 | Parametersatz 1->AMZ_2 | 071.012 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Kennlinientyp E PS1 | Enum | Parameter__Funktionsparameter | Definite Time;IEC Standard Inverse;IEC Very Inverse;IEC Extremely Inverse;IEC Long Time Inverse;IEEE Moderately Inverse;IEEE Very Inverse;IEEE Extremely Inverse;ANSI Normally Inverse;ANSI Short Time Inverse;ANSI Long Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | 1 | x003_u002E_060 | E | Parameter subset 1 | Definite Time | 1 |  |  | Overcurrent\IDMT2 N | pcharac | String |  |  | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 1 | Overcurrent\IDMT2 N | pcharac | String
x071_u002E_000 | Parametersatz 1->AMZ_2 | 071.000 | 0.05-10:0.01 |  | Kennl.f. kt,E PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 1 | 1 | 1 |  |  | Overcurrent\IDMT2 N | Tpset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 1 | Overcurrent\IDMT2 N | Tpset | Real |  |  | 1 | 0
x071_u002E_052 | Parametersatz 1->AMZ_2 | 071.052 | 0-10:0.001 | s | min. Auslösez.E PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 1 | 0 | 1 |  |  | Overcurrent\IDMT2 N | minresptime | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 1 | Overcurrent\IDMT2 N | minresptime | Real |  |  | 1 | 0
x071_u002E_024 | Parametersatz 1->AMZ_2 | 071.024 | unverzögert¦0;verzögert gem. Kennl¦1 |  | Rückfallen E PS1 | Enum | Parameter__Funktionsparameter | 0;1 | Real | 3 | x003_u002E_060;x071_u002E_012 | E;SW | Parameter subset 1;IEEE | 0 | 1 |  |  | Overcurrent\IDMT2 N | resetdis | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 1 | Overcurrent\IDMT2 N | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x071_u002E_012 | E;SW | Parameter subset 1;ANSI |  | 1 |  |  | Overcurrent\IDMT2 N | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | Parameter subset 1 |  | 1 |  |  | Overcurrent\IDMT2 N | resetdis | Real | 0 | 0
x076_u002E_235 | Parametersatz 1->KURI | 076.235 | nein¦0;ja¦1 |  | Freigabe PS1 | Enum | Parameter__Funktionsparameter | 1;0 | Real | 1 | x003_u002E_060;x017_u002E_070 | E;NE | Parameter subset 1;1 | 1 | 2 |  |  | Overcurrent\Directional P | outserv | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Overcurrent\Directional P | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\Directional N | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\Directional N | outserv | Real | E | 0 | 0 | 0
x017_u002E_071 | Parametersatz 1->KURI | 017.071 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung tI> PS1 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real | 1 | x003_u002E_060;x017_u002E_070;x076_u002E_235 | E;NE;NE | Parameter subset 1;1;1 | 1 | 1 |  |  | Overcurrent\DTOC I> | idir | Real | 1 | 0 | 1 | Overcurrent\Directional P;x003_u002E_060 | outserv | Real | E;E | 0;Parameter subset 1 | 1 | Overcurrent\DTOC I> | idir | Real |  |  | 1 | 0
x017_u002E_072 | Parametersatz 1->KURI | 017.072 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung tI>> PS1 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real | 1 | x003_u002E_060;x017_u002E_070;x076_u002E_235 | E;NE;NE | Parameter subset 1;1;1 | 1 | 1 |  |  | Overcurrent\DTOC I>> | idir | Real | 1 | 0 | 1 | Overcurrent\Directional P;x003_u002E_060 | outserv | Real | E;E | 0;Parameter subset 1 | 1 | Overcurrent\DTOC I>> | idir | Real |  |  | 1 | 0
x017_u002E_073 | Parametersatz 1->KURI | 017.073 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung tIE> PS1 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real | 1 | x003_u002E_060;x017_u002E_070;x076_u002E_235 | E;NE;NE | Parameter subset 1;1;1 | 1 | 1 |  |  | Overcurrent\DTOC IN> | idir | Real | 1 | 0 | 1 | Overcurrent\Directional N;x003_u002E_060 | outserv | Real | E;E | 0;Parameter subset 1 | 1 | Overcurrent\DTOC IN> | idir | Real |  |  | 1 | 0
x017_u002E_075 | Parametersatz 1->KURI | 017.075 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung tIE>> PS1 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real | 1 | x003_u002E_060;x017_u002E_070;x076_u002E_235 | E;NE;NE | Parameter subset 1;1;1 | 1 | 1 |  |  | Overcurrent\DTOC IN>> | idir | Real | 1 | 0 | 1 | Overcurrent\Directional N;x003_u002E_060 | outserv | Real | E;E | 0;Parameter subset 1 | 1 | Overcurrent\DTOC IN>> | idir | Real |  |  | 1 | 0
x017_u002E_066 | Parametersatz 1->KURI | 017.066 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung tIB,L> PS1 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real | 1 | x003_u002E_060;x017_u002E_070;x076_u002E_235 | E;NE;NE | Parameter subset 1;1;1 | 1 | 1 |  |  | Overcurrent\IDMT1 P | idir | Real | 1 | 0 | 1 | Overcurrent\Directional P;x003_u002E_060 | outserv | Real | E;E | 0;Parameter subset 1 | 1 | Overcurrent\IDMT1 P | idir | Real |  |  | 1 | 0
x017_u002E_067 | Parametersatz 1->KURI | 017.067 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung tIB,E> PS1 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real | 1 | x003_u002E_060;x017_u002E_070;x076_u002E_235 | E;NE;NE | Parameter subset 1;1;1 | 1 | 1 |  |  | Overcurrent\IDMT1 N | idir | Real | 1 | 0 | 1 | Overcurrent\Directional N;x003_u002E_060 | outserv | Real | E;E | 0;Parameter subset 1 | 1 | Overcurrent\IDMT1 N | idir | Real |  |  | 1 | 0
x017_u002E_076 | Parametersatz 1->KURI | 017.076 | -90-90:0.1 | ° | charakt.Winkel E PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 1 | -45 | 1 |  |  | Overcurrent\Directional N | mtau | Real | 1 | 0 | 1 | Overcurrent\Directional N;x003_u002E_060 | outserv | Real | E;E | 0;Parameter subset 1 | 1 | Overcurrent\Directional N | mtau | Real |  |  | 1 | 0
x017_u002E_077 | Parametersatz 1->KURI | 017.077 | 0.015-0.6:0.001 | Unom(/©3) | UNE> PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 1 | 0.1 | 1 |  |  | Overcurrent\Directional N | upolur | Real | 1 | 0 | 1 | Overcurrent\Directional N;x003_u002E_060 | outserv | Real | E;E | 0;Parameter subset 1 | 1 | Overcurrent\Directional N | upolur | Real |  |  | 1 | 0
x076_u002E_246 | Parametersatz 1->U<> | 076.246 | nein¦0;ja¦1 |  | Freigabe PS1 | Enum | Parameter__Funktionsparameter | 1;0 | Real | 1 | x003_u002E_060;x023_u002E_030 | E;NE | Parameter subset 1;1 | 1 | 1 |  |  | Voltage | outserv | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 1 | Voltage | outserv | Real | E | 0 | 0 | 0
x076_u002E_001 | Parametersatz 1->U<> | 076.001 | Dreieck¦0;Stern¦1 |  | Betriebsart PS1 | Enum | Parameter__Funktionsparameter | Delta;Star | String | 1 | x003_u002E_060 | E | Parameter subset 1 | Delta | 8 | E | Star | Voltage\V> | outserv | Real | 0 | 1
[16 empty] | E | Star | Voltage\V>> | outserv | Real | 0 | 1
[16 empty] | E | Star | Voltage\V< | outserv | Real | 0 | 1
[16 empty] | E | Star | Voltage\V<< | outserv | Real | 0 | 1
[16 empty] | E | Star | Voltage\VNG> | outserv | Real | 0 | 1
[16 empty] | E | Star | Voltage\VNG>> | outserv | Real | 0 | 1
x076_u002E_003 | Parametersatz 1->U<> | 076.003 | 0.2-1.5:0.01;blockiert=1.52 | Unom(/©3) | U> PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x076_u002E_001 | E;E | Parameter subset 1;Delta | 1.1 | 3 | SE | 1.5 | Voltage\V> | Uset | Real | 1 | 0 | 1 | x003_u002E_060;x076_u002E_001 |  |  | E;E | Parameter subset 1;Delta | 2 | Voltage\V> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V> | outserv | Real | 0 | 0 | [7 empty] | Voltage\V> | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.52 | Voltage\V> | outserv | Real | 0 | 1
x076_u002E_004 | Parametersatz 1->U<> | 076.004 | 0.2-1.5:0.01;blockiert=1.52 | Unom(/©3) | U>> PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x076_u002E_001 | E;E | Parameter subset 1;Delta | 1.1 | 3 | SE | 1.5 | Voltage\V>> | Uset | Real | 1 | 0 | 1 | x003_u002E_060;x076_u002E_001 |  |  | E;E | Parameter subset 1;Delta | 2 | Voltage\V>> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\V>> | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.52 | Voltage\V>> | outserv | Real | 0 | 1
x076_u002E_005 | Parametersatz 1->U<> | 076.005 | 0-100:0.01;blockiert=100.02 | s | tU> PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 1 | 1 | 2 | SE | 100 | Voltage\V> | Tdel | Real | 1 | 0 | 1 | x003_u002E_060;x076_u002E_001 |  |  | E;E | Parameter subset 1;Delta | 2 | Voltage\V> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\V> | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\V> | Tdel | Real |  |  | 0 | 100.02
x076_u002E_006 | Parametersatz 1->U<> | 076.006 | 0-100:0.01;blockiert=100.02 | s | tU>> PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 1 | 1 | 2 | SE | 100 | Voltage\V>> | Tdel | Real | 1 | 0 | 1 | x003_u002E_060;x076_u002E_001 |  |  | E;E | Parameter subset 1;Delta | 2 | Voltage\V>> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\V>> | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\V>> | Tdel | Real |  |  | 0 | 100.02
x076_u002E_027 | Parametersatz 1->U<> | 076.027 | 0-100:0.01;blockiert=100.02 | s | tU> 3p PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 1 | 1 | 2 | SE | 100 | Voltage\tV> 3-pole | Tdelay | Real | 1 | 0 | 1 | x003_u002E_060;x076_u002E_001 |  |  | E;E | Parameter subset 1;Delta | 2 | Voltage\tV> 3-pole | Tdelay | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\tV> 3-pole | Tdelay | Real | 0 | 9999999 | [7 empty] | Voltage\tV> 3-pole | Tdelay | Real |  |  | 0 | 100.02
x076_u002E_007 | Parametersatz 1->U<> | 076.007 | 0.2-1.5:0.01;blockiert=1.52 | Unom(/©3) | U< PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x076_u002E_001 | E;E | Parameter subset 1;Delta | 0.8 | 3 | SE | 1.5 | Voltage\V< | Uset | Real | 1 | 0 | 1 | x003_u002E_060;x076_u002E_001 |  |  | E;E | Parameter subset 1;Delta | 2 | Voltage\V< | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V< | outserv | Real | 0 | 0 | [7 empty] | Voltage\V< | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.52 | Voltage\V< | outserv | Real | 0 | 1
x076_u002E_008 | Parametersatz 1->U<> | 076.008 | 0.2-1.5:0.01;blockiert=1.52 | Unom(/©3) | U<< PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x076_u002E_001 | E;E | Parameter subset 1;Delta | 0.8 | 3 | SE | 1.5 | Voltage\V<< | Uset | Real | 1 | 0 | 1 | x003_u002E_060;x076_u002E_001 |  |  | E;E | Parameter subset 1;Delta | 2 | Voltage\V<< | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V<< | outserv | Real | 0 | 0 | [7 empty] | Voltage\V<< | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.52 | Voltage\V<< | outserv | Real | 0 | 1
x076_u002E_009 | Parametersatz 1->U<> | 076.009 | 0-100:0.01;blockiert=100.02 | s | tU< PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 1 | 1 | 2 | SE | 100 | Voltage\V< | Tdel | Real | 1 | 0 | 1 | x003_u002E_060;x076_u002E_001 |  |  | E;E | Parameter subset 1;Delta | 2 | Voltage\V< | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\V< | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\V< | Tdel | Real |  |  | 0 | 100.02
x076_u002E_010 | Parametersatz 1->U<> | 076.010 | 0-100:0.01;blockiert=100.02 | s | tU<< PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 1 | 1 | 2 | SE | 100 | Voltage\V<< | Tdel | Real | 1 | 0 | 1 | x003_u002E_060;x076_u002E_001 |  |  | E;E | Parameter subset 1;Delta | 2 | Voltage\V<< | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\V<< | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\V<< | Tdel | Real |  |  | 0 | 100.02
x076_u002E_028 | Parametersatz 1->U<> | 076.028 | 0-100:0.01;blockiert=100.02 | s | tU< 3p PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 1 | 1 | 2 | SE | 100 | Voltage\tV< 3-pole | Tdelay | Real | 1 | 0 | 1 | x003_u002E_060;x076_u002E_001 |  |  | E;E | Parameter subset 1;Delta | 2 | Voltage\tV< 3-pole | Tdelay | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\tV< 3-pole | Tdelay | Real | 0 | 9999999 | [7 empty] | Voltage\tV< 3-pole | Tdelay | Real |  |  | 0 | 100.02
x076_u002E_015 | Parametersatz 1->U<> | 076.015 | 0.2-1.5:0.01;blockiert=1.52 | Unom/©3 | Umit> PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 1 | 1.1 | 3 | SE | 1.5 | Voltage\Vpos> | Uset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Voltage\Vpos> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos> | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.52 | Voltage\Vpos> | outserv | Real | 0 | 1
x076_u002E_016 | Parametersatz 1->U<> | 076.016 | 0.2-1.5:0.01;blockiert=1.52 | Unom/©3 | Umit>> PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 1 | 1.1 | 3 | SE | 1.5 | Voltage\Vpos>> | Uset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Voltage\Vpos>> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos>> | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.52 | Voltage\Vpos>> | outserv | Real | 0 | 1
x076_u002E_017 | Parametersatz 1->U<> | 076.017 | 0-100:0.01;blockiert=100.02 | s | tUmit> PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 1 | 1 | 2 | SE | 100 | Voltage\Vpos> | Tdel | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Voltage\Vpos> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\Vpos> | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\Vpos> | Tdel | Real |  |  | 0 | 100.02
x076_u002E_018 | Parametersatz 1->U<> | 076.018 | 0-100:0.01;blockiert=100.02 | s | tUmit>> PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 1 | 1 | 2 | SE | 100 | Voltage\Vpos>> | Tdel | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Voltage\Vpos>> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\Vpos>> | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\Vpos>> | Tdel | Real |  |  | 0 | 100.02
x076_u002E_019 | Parametersatz 1->U<> | 076.019 | 0.2-1.5:0.01;blockiert=1.52 | Unom/©3 | Umit< PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 1 | 0.8 | 3 | SE | 1.5 | Voltage\Vpos< | Uset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Voltage\Vpos< | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos< | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos< | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.52 | Voltage\Vpos< | outserv | Real | 0 | 1
x076_u002E_020 | Parametersatz 1->U<> | 076.020 | 0.2-1.5:0.01;blockiert=1.52 | Unom/©3 | Umit<< PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 1 | 0.8 | 3 | SE | 1.5 | Voltage\Vpos<< | Uset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Voltage\Vpos<< | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos<< | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos<< | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.52 | Voltage\Vpos<< | outserv | Real | 0 | 1
x076_u002E_021 | Parametersatz 1->U<> | 076.021 | 0-100:0.01;blockiert=100.02 | s | tUmit< PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 1 | 1 | 2 | SE | 100 | Voltage\Vpos< | Tdel | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Voltage\Vpos< | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\Vpos< | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\Vpos< | Tdel | Real |  |  | 0 | 100.02
x076_u002E_022 | Parametersatz 1->U<> | 076.022 | 0-100:0.01;blockiert=100.02 | s | tUmit<< PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 1 | 1 | 2 | SE | 100 | Voltage\Vpos<< | Tdel | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Voltage\Vpos<< | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\Vpos<< | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\Vpos<< | Tdel | Real |  |  | 0 | 100.02
x076_u002E_023 | Parametersatz 1->U<> | 076.023 | 0.02-1.5:0.01;blockiert=1.52 | Unom/©3 | Ugegen> PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 1 | 1.52 | 3 | SE | 1.5 | Voltage\Vneg> | Uset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Voltage\Vneg> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vneg> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vneg> | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.52 | Voltage\Vneg> | outserv | Real | 0 | 1
x076_u002E_024 | Parametersatz 1->U<> | 076.024 | 0.02-1.5:0.01;blockiert=1.52 | Unom/©3 | Ugegen>> PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 1 | 1.52 | 3 | SE | 1.5 | Voltage\Vneg>> | Uset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Voltage\Vneg>> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vneg>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vneg>> | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.52 | Voltage\Vneg>> | outserv | Real | 0 | 1
x076_u002E_025 | Parametersatz 1->U<> | 076.025 | 0-100:0.01;blockiert=100.02 | s | tUgegen> PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 1 | 1 | 2 | SE | 100 | Voltage\Vneg> | Tdel | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Voltage\Vneg> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\Vneg> | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\Vneg> | Tdel | Real |  |  | 0 | 100.02
x076_u002E_026 | Parametersatz 1->U<> | 076.026 | 0-100:0.01;blockiert=100.02 | s | tUgegen>> PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 1 | 1 | 2 | SE | 100 | Voltage\Vneg>> | Tdel | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Voltage\Vneg>> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\Vneg>> | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\Vneg>> | Tdel | Real |  |  | 0 | 100.02
x076_u002E_011 | Parametersatz 1->U<> | 076.011 | 0.02-1:0.01;blockiert=1.02 | Unom(/©3) | UNE> PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x076_u002E_001 | E;E | Parameter subset 1;Delta | 1.02 | 3 | SE | 1 | Voltage\VNG> | Uset | Real | 1 | 0 | 1 | x003_u002E_060;x076_u002E_001 |  |  | E;E | Parameter subset 1;Delta | 2 | Voltage\VNG> | outserv | Real | E | 1 | 0 | 1.02
[16 empty] | SE | 1 | Voltage\VNG> | outserv | Real | 0 | 0 | [7 empty] | Voltage\VNG> | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.02 | Voltage\VNG> | outserv | Real | 0 | 1
x076_u002E_012 | Parametersatz 1->U<> | 076.012 | 0.02-1:0.01;blockiert=1.02 | Unom(/©3) | UNE>> PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x076_u002E_001 | E;E | Parameter subset 1;Delta | 1.02 | 3 | SE | 1 | Voltage\VNG>> | Uset | Real | 1 | 0 | 1 | x003_u002E_060;x076_u002E_001 |  |  | E;E | Parameter subset 1;Delta | 2 | Voltage\VNG>> | outserv | Real | E | 1 | 0 | 1.02
[16 empty] | SE | 1 | Voltage\VNG>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\VNG>> | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.02 | Voltage\VNG>> | outserv | Real | 0 | 1
x076_u002E_013 | Parametersatz 1->U<> | 076.013 | 0-100:0.01;blockiert=100.02 | s | tUNE> PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 1 | 1 | 2 | SE | 100 | Voltage\VNG> | Tdel | Real | 1 | 0 | 1 | x003_u002E_060;x076_u002E_001 |  |  | E;E | Parameter subset 1;Delta | 2 | Voltage\VNG> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\VNG> | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\VNG> | Tdel | Real |  |  | 0 | 100.02
x076_u002E_014 | Parametersatz 1->U<> | 076.014 | 0-100:0.01;blockiert=100.02 | s | tUNE>> PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 1 | 1 | 2 | SE | 100 | Voltage\VNG>> | Tdel | Real | 1 | 0 | 1 | x003_u002E_060;x076_u002E_001 |  |  | E;E | Parameter subset 1;Delta | 2 | Voltage\VNG>> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\VNG>> | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\VNG>> | Tdel | Real |  |  | 0 | 100.02
x001_u002E_162 | Parametersatz 1->U<> | 001.162 | ohne¦0;mit¦1 |  | Btr.art U< Überw PS1 | Enum | Parameter__Funktionsparameter | 1;0 | Real | 1 | x003_u002E_060 | E | Parameter subset 1 | 1 | 1 |  |  | Voltage\Imin | outserv | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 1 | Voltage\Imin | outserv | Real |  |  | 1 | 0
x001_u002E_155 | Parametersatz 1->U<> | 001.155 | 0.04-1:0.01 | Inom | I-Freigabe U< PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 1 | 0.1 | 1 |  |  | Voltage\Imin | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 1 | Voltage\Imin | Ipset | Real |  |  | 1 | 0
x018_u002E_196 | Parametersatz 1->f<> | 018.196 | nein¦0;ja¦1 |  | Freigabe PS1 | Enum | Parameter__Funktionsparameter | 1;0 | Real | 1 | x003_u002E_060;x023_u002E_031 | E;NE | Parameter subset 1;1 | 1 | 1 |  |  | Frequency | outserv | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 1 | Frequency | outserv | Real | E | 0 | 0 | 0
x018_u002E_120 | Parametersatz 1->f<> | 018.120 | f¦0;f mit df/dt¦1;f m. Delta f/Delta t¦2 |  | Betriebsart f1 PS1 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real | 1 | x003_u002E_060 | E | Parameter subset 1 | 0 | 1 | E | 0 | Frequency\df1/dt | outserv | Real | 0 | 1 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 3 | Frequency\f1 | outserv | Real | E | 1 | 0 | 0
[30 empty] | Frequency\df1/dt | outserv | Real | E | 1 | 0 | 0
[30 empty] | Frequency\df1/dt | outserv | Real |  |  | 0 | 1
x018_u002E_100 | Parametersatz 1->f<> | 018.100 | 40-70:0.01;blockiert=70.02 | Hz | f1 PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 1 | 49.8 | 3 | SE | 70 | Frequency\f1 | Fset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Frequency\f1 | outserv | Real | E | 1 | 0 | 70.02
[16 empty] | SE | 70 | Frequency\f1 | outserv | Real | 0 | 0 | [7 empty] | Frequency\f1 | Fset | Real |  |  | 1 | 0
[16 empty] | GE | 70.02 | Frequency\f1 | outserv | Real | 0 | 1
x018_u002E_104 | Parametersatz 1->f<> | 018.104 | 0-10:0.001;blockiert=10.002 | s | tf1 PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 1 | 0 | 4 | SE | 10 | Frequency\f1 | Tdel | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 4 | Frequency\f1 | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | GE | 10.002 | Frequency\f1 | Tdel | Real | 0 | 9999999 | [7 empty] | Frequency\f1 | Tdel | Real |  |  | 0 | 10.002
[16 empty] | SE | 10 | Frequency\df1/dt | Tdel | Real | 1 | 0 | [7 empty] | Frequency\df1/dt | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | GE | 10.002 | Frequency\df1/dt | Tdel | Real | 0 | 9999999 | [7 empty] | Frequency\df1/dt | Tdel | Real |  |  | 0 | 10.002
x018_u002E_108 | Parametersatz 1->f<> | 018.108 | 0.1-10:0.001;blockiert=10.002 | Hz/s | df1/dt PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x018_u002E_120 | E;E | Parameter subset 1;1 | 2 | 3 | SE | 10 | Frequency\df1/dt | dFset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Frequency\df1/dt | outserv | Real | E | 1 | 0 | 10.002
[16 empty] | SE | 10 | Frequency\df1/dt | outserv | Real | 0 | 0 | [7 empty] | Frequency\df1/dt | dFset | Real |  |  | 1 | 0
[16 empty] | GE | 10.002 | Frequency\df1/dt | outserv | Real | 0 | 1
x018_u002E_144 | Parametersatz 1->f<> | 018.144 | f¦0;f mit df/dt¦1;f m. Delta f/Delta t¦2 |  | Betriebsart f2 PS1 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real | 1 | x003_u002E_060 | E | Parameter subset 1 | 0 | 1 | E | 0 | Frequency\df2/dt | outserv | Real | 0 | 1 |  | x003_u002E_060 |  |  | E | Parameter subset 1 | 3 | Frequency\f2 | outserv | Real | E | 1 | 0 | 0
[30 empty] | Frequency\df2/dt | outserv | Real | E | 1 | 0 | 0
[30 empty] | Frequency\df2/dt | outserv | Real |  |  | 0 | 1
x018_u002E_124 | Parametersatz 1->f<> | 018.124 | 40-70:0.01;blockiert=70.02 | Hz | f2 PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 1 | 49.8 | 3 | SE | 70 | Frequency\f2 | Fset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Frequency\f2 | outserv | Real | E | 1 | 0 | 70.02
[16 empty] | SE | 70 | Frequency\f2 | outserv | Real | 0 | 0 | [7 empty] | Frequency\f2 | Fset | Real |  |  | 1 | 0
[16 empty] | GE | 70.02 | Frequency\f2 | outserv | Real | 0 | 1
x018_u002E_128 | Parametersatz 1->f<> | 018.128 | 0-10:0.001;blockiert=10.002 | s | tf2 PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 1 | 0 | 4 | SE | 10 | Frequency\f2 | Tdel | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 4 | Frequency\f2 | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | GE | 10.002 | Frequency\f2 | Tdel | Real | 0 | 9999999 | [7 empty] | Frequency\f2 | Tdel | Real |  |  | 0 | 10.002
[16 empty] | SE | 10 | Frequency\df2/dt | Tdel | Real | 1 | 0 | [7 empty] | Frequency\df2/dt | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | GE | 10.002 | Frequency\df2/dt | Tdel | Real | 0 | 9999999 | [7 empty] | Frequency\df2/dt | Tdel | Real |  |  | 0 | 10.002
x018_u002E_132 | Parametersatz 1->f<> | 018.132 | 0.1-10:0.001;blockiert=10.002 | Hz/s | df2/dt PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x018_u002E_144 | E;E | Parameter subset 1;1 | 2 | 3 | SE | 10 | Frequency\df2/dt | dFset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Frequency\df2/dt | outserv | Real | E | 1 | 0 | 10.002
[16 empty] | SE | 10 | Frequency\df2/dt | outserv | Real | 0 | 0 | [7 empty] | Frequency\df2/dt | dFset | Real |  |  | 1 | 0
[16 empty] | GE | 10.002 | Frequency\df2/dt | outserv | Real | 0 | 1
x018_u002E_168 | Parametersatz 1->f<> | 018.168 | f¦0;f mit df/dt¦1;f m. Delta f/Delta t¦2 |  | Betriebsart f3 PS1 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real | 1 | x003_u002E_060 | E | Parameter subset 1 | 0 | 1 | E | 0 | Frequency\df3/dt | outserv | Real | 0 | 1 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Frequency\f3 | outserv | Real | E | 1 | 0 | 0
[30 empty] | Frequency\df3/dt | outserv | Real | E | 1 | 0 | 0
[30 empty] | Frequency\df3/dt | outserv | Real |  |  | 0 | 1
x018_u002E_148 | Parametersatz 1->f<> | 018.148 | 40-70:0.01;blockiert=70.02 | Hz | f3 PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 1 | 49.8 | 3 | SE | 70 | Frequency\f3 | Fset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Frequency\f3 | outserv | Real | E | 1 | 0 | 70.02
[16 empty] | SE | 70 | Frequency\f3 | outserv | Real | 0 | 0 | [7 empty] | Frequency\f3 | Fset | Real |  |  | 1 | 0
[16 empty] | GE | 70.02 | Frequency\f3 | outserv | Real | 0 | 1
x018_u002E_152 | Parametersatz 1->f<> | 018.152 | 0-10:0.001;blockiert=10.002 | s | tf3 PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 1 | 0 | 4 | SE | 10 | Frequency\f3 | Tdel | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 4 | Frequency\f3 | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | GE | 10.002 | Frequency\f3 | Tdel | Real | 0 | 9999999 | [7 empty] | Frequency\f3 | Tdel | Real |  |  | 0 | 10.002
[16 empty] | SE | 10 | Frequency\df3/dt | Tdel | Real | 1 | 0 | [7 empty] | Frequency\df3/dt | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | GE | 10.002 | Frequency\df3/dt | Tdel | Real | 0 | 9999999 | [7 empty] | Frequency\df3/dt | Tdel | Real |  |  | 0 | 10.002
x018_u002E_156 | Parametersatz 1->f<> | 018.156 | 0.1-10:0.001;blockiert=10.002 | Hz/s | df3/dt PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x018_u002E_168 | E;E | Parameter subset 1;1 | 2 | 3 | SE | 10 | Frequency\df3/dt | dFset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Frequency\df3/dt | outserv | Real | E | 1 | 0 | 10.002
[16 empty] | SE | 10 | Frequency\df3/dt | outserv | Real | 0 | 0 | [7 empty] | Frequency\df3/dt | dFset | Real |  |  | 1 | 0
[16 empty] | GE | 10.002 | Frequency\df3/dt | outserv | Real | 0 | 1
x018_u002E_192 | Parametersatz 1->f<> | 018.192 | f¦0;f mit df/dt¦1;f m. Delta f/Delta t¦2 |  | Betriebsart f4 PS1 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real | 1 | x003_u002E_060 | E | Parameter subset 1 | 0 | 1 | E | 0 | Frequency\df4/dt | outserv | Real | 0 | 1 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Frequency\f4 | outserv | Real | E | 1 | 0 | 0
[30 empty] | Frequency\df4/dt | outserv | Real | E | 1 | 0 | 0
[30 empty] | Frequency\df4/dt | outserv | Real |  |  | 0 | 1
x018_u002E_172 | Parametersatz 1->f<> | 018.172 | 40-70:0.01;blockiert=70.02 | Hz | f4 PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 1 | 49.8 | 3 | SE | 70 | Frequency\f4 | Fset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Frequency\f4 | outserv | Real | E | 1 | 0 | 70.02
[16 empty] | SE | 70 | Frequency\f4 | outserv | Real | 0 | 0 | [7 empty] | Frequency\f4 | Fset | Real |  |  | 1 | 0
[16 empty] | GE | 70.02 | Frequency\f4 | outserv | Real | 0 | 1
x018_u002E_176 | Parametersatz 1->f<> | 018.176 | 0-10:0.001;blockiert=10.002 | s | tf4 PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 1 | 0 | 4 | SE | 10 | Frequency\f4 | Tdel | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 4 | Frequency\f4 | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | GE | 10.002 | Frequency\f4 | Tdel | Real | 0 | 9999999 | [7 empty] | Frequency\f4 | Tdel | Real |  |  | 0 | 10.002
[16 empty] | SE | 10 | Frequency\df4/dt | Tdel | Real | 1 | 0 | [7 empty] | Frequency\df4/dt | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | GE | 10.002 | Frequency\df4/dt | Tdel | Real | 0 | 9999999 | [7 empty] | Frequency\df4/dt | Tdel | Real |  |  | 0 | 10.002
x018_u002E_180 | Parametersatz 1->f<> | 018.180 | 0.1-10:0.001;blockiert=10.002 | Hz/s | df4/dt PS1 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x018_u002E_192 | E;E | Parameter subset 1;1 | 2 | 3 | SE | 10 | Frequency\df4/dt | dFset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 1 | 2 | Frequency\df4/dt | outserv | Real | E | 1 | 0 | 10.002
[16 empty] | SE | 10 | Frequency\df4/dt | outserv | Real | 0 | 0 | [7 empty] | Frequency\df4/dt | dFset | Real |  |  | 1 | 0
[16 empty] | GE | 10.002 | Frequency\df4/dt | outserv | Real | 0 | 1
x073_u002E_098 | Parametersatz 2->UMZ | 073.098 | nein¦0;ja¦1 |  | Freigabe PS2 | Enum | Parameter__Funktionsparameter | 1;0 | Real | 1 | x003_u002E_060;x022_u002E_075 | E;NE | Parameter subset 2;1 | 1 | 10 | E | 1 | Overcurrent\DTOC I> | outserv | Real | 0 | 1 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 10 | Overcurrent\DTOC I> | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\DTOC I>> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC I>> | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\DTOC I>>> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC I>>> | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\DTOC Ineg> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC Ineg> | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\DTOC Ineg>> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC Ineg>> | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\DTOC Ineg>>> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC Ineg>>> | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\DTOC Ineg>>>> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC Ineg>>>> | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\DTOC IN> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC IN> | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\DTOC IN>> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC IN>> | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\DTOC IN>>> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC IN>>> | outserv | Real | E | 0 | 0 | 0
x073_u002E_007 | Parametersatz 2->UMZ | 073.007 | 0.1-40:0.01;blockiert=40.02 | Inom | I> PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x073_u002E_098 | E;NE;NE | Parameter subset 2;1;1 | 1 | 3 | SE | 40 | Overcurrent\DTOC I> | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Overcurrent\DTOC I> | outserv | Real | E | 1 | 0 | 40.02
[16 empty] | SE | 40 | Overcurrent\DTOC I> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\DTOC I> | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 40.02 | Overcurrent\DTOC I> | outserv | Real | 0 | 1
x073_u002E_008 | Parametersatz 2->UMZ | 073.008 | 0.1-40:0.01;blockiert=40.02 | Inom | I>> PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x073_u002E_098 | E;NE;NE | Parameter subset 2;1;1 | 4 | 3 | SE | 40 | Overcurrent\DTOC I>> | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Overcurrent\DTOC I>> | outserv | Real | E | 1 | 0 | 40.02
[16 empty] | SE | 40 | Overcurrent\DTOC I>> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\DTOC I>> | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 40.02 | Overcurrent\DTOC I>> | outserv | Real | 0 | 1
x073_u002E_009 | Parametersatz 2->UMZ | 073.009 | 0.1-40:0.01;blockiert=40.02 | Inom | I>>> PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x073_u002E_098 | E;NE;NE | Parameter subset 2;1;1 | 40.02 | 4 | SE | 40 | Overcurrent\DTOC I>>> | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Overcurrent\DTOC I>>> | outserv | Real | E | 1 | 0 | 40.02
[16 empty] | SE | 40 | Overcurrent\DTOC I>>> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\DTOC I>>> | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 40.02 | Overcurrent\DTOC I>>> | outserv | Real | 0 | 1
[18 empty] | Overcurrent\DTOC I>>> | idir | Real | 0 | 0
x073_u002E_019 | Parametersatz 2->UMZ | 073.019 | 0-100:0.01;blockiert=100.02 | s | tI> PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x073_u002E_098 | E;NE;NE | Parameter subset 2;1;1 | 1 | 2 | SE | 100 | Overcurrent\DTOC I> | Tset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Overcurrent\DTOC I> | Tset | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Overcurrent\DTOC I> | Tset | Real | 0 | 9999999 | [7 empty] | Overcurrent\DTOC I> | Tset | Real |  |  | 0 | 100.02
x073_u002E_020 | Parametersatz 2->UMZ | 073.020 | 0-100:0.01;blockiert=100.02 | s | tI>> PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x073_u002E_098 | E;NE;NE | Parameter subset 2;1;1 | 0.5 | 2 | SE | 100 | Overcurrent\DTOC I>> | Tset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Overcurrent\DTOC I>> | Tset | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Overcurrent\DTOC I>> | Tset | Real | 0 | 9999999 | [7 empty] | Overcurrent\DTOC I>> | Tset | Real |  |  | 0 | 100.02
x073_u002E_021 | Parametersatz 2->UMZ | 073.021 | 0-100:0.01;blockiert=100.02 | s | tI>>> PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x073_u002E_098 | E;NE;NE | Parameter subset 2;1;1 | 0.5 | 2 | SE | 100 | Overcurrent\DTOC I>>> | Tset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Overcurrent\DTOC I>>> | Tset | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Overcurrent\DTOC I>>> | Tset | Real | 0 | 9999999 | [7 empty] | Overcurrent\DTOC I>>> | Tset | Real |  |  | 0 | 100.02
x073_u002E_011 | Parametersatz 2->UMZ | 073.011 | 0.1-25:0.01;blockiert=25.02 | Inom | Igegen> PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x073_u002E_098 | E;NE;NE | Parameter subset 2;1;1 | 1 | 3 | SE | 25 | Overcurrent\DTOC Ineg> | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Overcurrent\DTOC Ineg> | outserv | Real | E | 1 | 0 | 25.02
[16 empty] | SE | 25 | Overcurrent\DTOC Ineg> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\DTOC Ineg> | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 25.02 | Overcurrent\DTOC Ineg> | outserv | Real | 0 | 1
x073_u002E_012 | Parametersatz 2->UMZ | 073.012 | 0.1-25:0.01;blockiert=25.02 | Inom | Igegen>> PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x073_u002E_098 | E;NE;NE | Parameter subset 2;1;1 | 4 | 3 | SE | 25 | Overcurrent\DTOC Ineg>> | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Overcurrent\DTOC Ineg>> | outserv | Real | E | 1 | 0 | 25.02
[16 empty] | SE | 25 | Overcurrent\DTOC Ineg>> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\DTOC Ineg>> | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 25.02 | Overcurrent\DTOC Ineg>> | outserv | Real | 0 | 1
x073_u002E_013 | Parametersatz 2->UMZ | 073.013 | 0.1-25:0.01;blockiert=25.02 | Inom | Igegen>>> PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x073_u002E_098 | E;NE;NE | Parameter subset 2;1;1 | 25.02 | 3 | SE | 25 | Overcurrent\DTOC Ineg>>> | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Overcurrent\DTOC Ineg>>> | outserv | Real | E | 1 | 0 | 25.02
[16 empty] | SE | 25 | Overcurrent\DTOC Ineg>>> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\DTOC Ineg>>> | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 25.02 | Overcurrent\DTOC Ineg>>> | outserv | Real | 0 | 1
x073_u002E_023 | Parametersatz 2->UMZ | 073.023 | 0-100:0.01;blockiert=100.02 | s | tIgegen> PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x073_u002E_098 | E;NE;NE | Parameter subset 2;1;1 | 1 | 2 | SE | 100 | Overcurrent\DTOC Ineg> | Tset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Overcurrent\DTOC Ineg> | Tset | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Overcurrent\DTOC Ineg> | Tset | Real | 0 | 9999999 | [7 empty] | Overcurrent\DTOC Ineg> | Tset | Real |  |  | 0 | 100.02
x073_u002E_024 | Parametersatz 2->UMZ | 073.024 | 0-100:0.01;blockiert=100.02 | s | tIgegen>> PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x073_u002E_098 | E;NE;NE | Parameter subset 2;1;1 | 0.5 | 2 | SE | 100 | Overcurrent\DTOC Ineg>> | Tset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Overcurrent\DTOC Ineg>> | Tset | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Overcurrent\DTOC Ineg>> | Tset | Real | 0 | 9999999 | [7 empty] | Overcurrent\DTOC Ineg>> | Tset | Real |  |  | 0 | 100.02
x073_u002E_025 | Parametersatz 2->UMZ | 073.025 | 0-100:0.01;blockiert=100.02 | s | tIgegen>>> PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x073_u002E_098 | E;NE;NE | Parameter subset 2;1;1 | 100.02 | 2 | SE | 100 | Overcurrent\DTOC Ineg>>> | Tset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Overcurrent\DTOC Ineg>>> | Tset | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Overcurrent\DTOC Ineg>>> | Tset | Real | 0 | 9999999 | [7 empty] | Overcurrent\DTOC Ineg>>> | Tset | Real |  |  | 0 | 100.02
x073_u002E_015 | Parametersatz 2->UMZ | 073.015 | 0.002-8:0.001;blockiert=8.002 | Inom | IE> PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x073_u002E_098 | E;NE;NE | Parameter subset 2;1;1 | 0.25 | 3 | SE | 8 | Overcurrent\DTOC IN> | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Overcurrent\DTOC IN> | outserv | Real | E | 1 | 0 | 8.002
[16 empty] | SE | 8 | Overcurrent\DTOC IN> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\DTOC IN> | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 8.002 | Overcurrent\DTOC IN> | outserv | Real | 0 | 1
x073_u002E_016 | Parametersatz 2->UMZ | 073.016 | 0.002-8:0.001;blockiert=8.002 | Inom | IE>> PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x073_u002E_098 | E;NE;NE | Parameter subset 2;1;1 | 8.002 | 3 | SE | 8 | Overcurrent\DTOC IN>> | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Overcurrent\DTOC IN>> | outserv | Real | E | 1 | 0 | 8.002
[16 empty] | SE | 8 | Overcurrent\DTOC IN>> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\DTOC IN>> | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 8.002 | Overcurrent\DTOC IN>> | outserv | Real | 0 | 1
x073_u002E_017 | Parametersatz 2->UMZ | 073.017 | 0.002-8:0.001;blockiert=8.002 | Inom | IE>>> PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x073_u002E_098 | E;NE;NE | Parameter subset 2;1;1 | 8.002 | 4 | SE | 8 | Overcurrent\DTOC IN>>> | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Overcurrent\DTOC IN>>> | outserv | Real | E | 1 | 0 | 8.002
[16 empty] | SE | 8 | Overcurrent\DTOC IN>>> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\DTOC IN>>> | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 8.002 | Overcurrent\DTOC IN>>> | outserv | Real | 0 | 1
[18 empty] | Overcurrent\DTOC IN>>> | idir | Real | 0 | 0
x073_u002E_018 | Parametersatz 2->UMZ | 073.018 | 0.1-40:0.01;blockiert=40.02 | Inom | IE>>>> PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x073_u002E_098 | E;NE;NE | Parameter subset 2;1;1 | 40.02 | 3 | SE | 40 | Overcurrent\DTOC IN>>>> | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Overcurrent\DTOC IN>>>> | outserv | Real | E | 1 | 0 | 40.02
[16 empty] | SE | 40 | Overcurrent\DTOC IN>>>> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\DTOC IN>>>> | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 40.02 | Overcurrent\DTOC IN>>>> | outserv | Real | 0 | 1
x073_u002E_027 | Parametersatz 2->UMZ | 073.027 | 0-100:0.01;blockiert=100.02 | s | tIE> PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x073_u002E_098 | E;NE;NE | Parameter subset 2;1;1 | 1 | 2 | SE | 100 | Overcurrent\DTOC IN> | Tset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Overcurrent\DTOC IN> | Tset | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Overcurrent\DTOC IN> | Tset | Real | 0 | 9999999 | [7 empty] | Overcurrent\DTOC IN> | Tset | Real |  |  | 0 | 100.02
x073_u002E_028 | Parametersatz 2->UMZ | 073.028 | 0-100:0.01;blockiert=100.02 | s | tIE>> PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x073_u002E_098 | E;NE;NE | Parameter subset 2;1;1 | 0.5 | 2 | SE | 100 | Overcurrent\DTOC IN>> | Tset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Overcurrent\DTOC IN>> | Tset | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Overcurrent\DTOC IN>> | Tset | Real | 0 | 9999999 | [7 empty] | Overcurrent\DTOC IN>> | Tset | Real |  |  | 0 | 100.02
x073_u002E_029 | Parametersatz 2->UMZ | 073.029 | 0-100:0.01;blockiert=100.02 | s | tIE>>> PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x073_u002E_098 | E;NE;NE | Parameter subset 2;1;1 | 0.5 | 2 | SE | 100 | Overcurrent\DTOC IN>>> | Tset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Overcurrent\DTOC IN>>> | Tset | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Overcurrent\DTOC IN>>> | Tset | Real | 0 | 9999999 | [7 empty] | Overcurrent\DTOC IN>>> | Tset | Real |  |  | 0 | 100.02
x073_u002E_030 | Parametersatz 2->UMZ | 073.030 | 0-100:0.01;blockiert=100.02 | s | tIE>>>> PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x073_u002E_098 | E;NE;NE | Parameter subset 2;1;1 | 0.5 | 2 | SE | 100 | Overcurrent\DTOC IN>>>> | Tset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Overcurrent\DTOC IN>>>> | Tset | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Overcurrent\DTOC IN>>>> | Tset | Real | 0 | 9999999 | [7 empty] | Overcurrent\DTOC IN>>>> | Tset | Real |  |  | 0 | 100.02
x073_u002E_070 | Parametersatz 2->AMZ_1 | 073.070 | nein¦0;ja¦1 |  | Freigabe PS2 | Enum | Parameter__Funktionsparameter | 1;0 | Real | 1 | x003_u002E_060;x017_u002E_096 | E;NE | Parameter subset 2;1 | 1 | 6 | E | 1 | Overcurrent\IDMT1 P | outserv | Real | 0 | 1 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 3 | Overcurrent\IDMT1 P | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\IDMT1 neg | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\IDMT1 neg | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\IDMT1 N | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\IDMT1 N | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 0 | Overcurrent\IDMT1 P | ModFrame | Real | 0 | 1
[16 empty] | E | 0 | Overcurrent\IDMT1 neg | ModFrame | Real | 0 | 1
[16 empty] | E | 0 | Overcurrent\IDMT1 N | ModFrame | Real | 0 | 1
x073_u002E_050 | Parametersatz 2->AMZ_1 | 073.050 | 0.1-4:0.01;blockiert=4.02 | Inom | IB,L PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x017_u002E_096;x073_u002E_070 | E;NE;NE | Parameter subset 2;1;1 | 1 | 4 | SE | 4 | Overcurrent\IDMT1 P | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Overcurrent\IDMT1 P | outserv | Real | E | 1 | 0 | 4.02
[16 empty] | SE | 4 | Overcurrent\IDMT1 P | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\IDMT1 P | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 4.02 | Overcurrent\IDMT1 P | outserv | Real | 0 | 1
[18 empty] | Overcurrent\IDMT1 KI P | outserv | Real | 0 | 1
x073_u002E_056 | Parametersatz 2->AMZ_1 | 073.056 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Kennlinientyp L PS2 | Enum | Parameter__Funktionsparameter | Definite Time;IEC Standard Inverse;IEC Very Inverse;IEC Extremely Inverse;IEC Long Time Inverse;IEEE Moderately Inverse;IEEE Very Inverse;IEEE Extremely Inverse;ANSI Normally Inverse;ANSI Short Time Inverse;ANSI Long Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | 1 | x003_u002E_060 | E | Parameter subset 2 | Definite Time | 1 |  |  | Overcurrent\IDMT1 P | pcharac | String |  |  | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 1 | Overcurrent\IDMT1 P | pcharac | String
x073_u002E_053 | Parametersatz 2->AMZ_1 | 073.053 | 0.05-10:0.01 |  | Kennl.fakt. kt,L PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 2 | 1 | 2 |  |  | Overcurrent\IDMT1 P | Tpset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 1 | Overcurrent\IDMT1 P | Tpset | Real |  |  | 1 | 0
[18 empty] | Overcurrent\IDMT1 P | Tadder | Real | 0 | 0
x073_u002E_077 | Parametersatz 2->AMZ_1 | 073.077 | 0-10:0.001 | s | min. Auslösez. L PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 2 | 0 | 1 |  |  | Overcurrent\IDMT1 P | minresptime | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 1 | Overcurrent\IDMT1 P | minresptime | Real |  |  | 1 | 0
x073_u002E_059 | Parametersatz 2->AMZ_1 | 073.059 | unverzögert¦0;verzögert gem. Kennl¦1 |  | Rückfallen L PS2 | Enum | Parameter__Funktionsparameter | 0;1 | Real | 3 | x003_u002E_060;x073_u002E_056 | E;SW | Parameter subset 2;IEEE | 0 | 1 |  |  | Overcurrent\IDMT1 P | resetdis | Real | 1 | 0 | 1 | x003_u002E_060 |  |  |  | Parameter subset 2 | 1 | Overcurrent\IDMT1 P | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x073_u002E_056 | E;SW | Parameter subset 2;ANSI |  | 1 |  |  | Overcurrent\IDMT1 P | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | Parameter subset 2 |  | 1 |  |  | Overcurrent\IDMT1 P | resetdis | Real | 0 | 0
x073_u002E_051 | Parametersatz 2->AMZ_1 | 073.051 | 0.01-4:0.01;blockiert=4.02 | Inom | IB,gegen PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x017_u002E_096;x073_u002E_070 | E;NE;NE | Parameter subset 2;1;1 | 1 | 4 | SE | 4 | Overcurrent\IDMT1 neg | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Overcurrent\IDMT1 neg | outserv | Real | E | 1 | 0 | 4.02
[16 empty] | SE | 4 | Overcurrent\IDMT1 neg | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\IDMT1 neg | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 4.02 | Overcurrent\IDMT1 neg | outserv | Real | 0 | 1
[18 empty] | Overcurrent\IDMT1 KI neg | outserv | Real | 0 | 1
x073_u002E_057 | Parametersatz 2->AMZ_1 | 073.057 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Kennl.typ gegen PS2 | Enum | Parameter__Funktionsparameter | Definite Time;IEC Standard Inverse;IEC Very Inverse;IEC Extremely Inverse;IEC Long Time Inverse;IEEE Moderately Inverse;IEEE Very Inverse;IEEE Extremely Inverse;ANSI Normally Inverse;ANSI Short Time Inverse;ANSI Long Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | 1 | x003_u002E_060 | E | Parameter subset 2 | Definite Time | 1 |  |  | Overcurrent\IDMT1 neg | pcharac | String |  |  | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 1 | Overcurrent\IDMT1 neg | pcharac | String
x073_u002E_054 | Parametersatz 2->AMZ_1 | 073.054 | 0.05-10:0.01 |  | Kennl.f. kt,gegn PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 2 | 1 | 2 |  |  | Overcurrent\IDMT1 neg | Tpset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 1 | Overcurrent\IDMT1 neg | Tpset | Real |  |  | 1 | 0
[18 empty] | Overcurrent\IDMT1 neg | Tadder | Real | 0 | 0
x073_u002E_078 | Parametersatz 2->AMZ_1 | 073.078 | 0-10:0.001 | s | min.Auslösez.geg PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 2 | 0 | 1 |  |  | Overcurrent\IDMT1 neg | minresptime | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 1 | Overcurrent\IDMT1 neg | minresptime | Real |  |  | 1 | 0
x073_u002E_060 | Parametersatz 2->AMZ_1 | 073.060 | unverzögert¦0;verzögert gem. Kennl¦1 |  | Rückfallen gegen PS2 | Enum | Parameter__Funktionsparameter | 0;1 | Real | 3 | x003_u002E_060;x073_u002E_057 | E;SW | Parameter subset 2;IEEE | 0 | 1 |  |  | Overcurrent\IDMT1 neg | resetdis | Real | 1 | 0 | 1 | x003_u002E_060 |  |  |  | Parameter subset 2 | 1 | Overcurrent\IDMT1 neg | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x073_u002E_057 | E;SW | Parameter subset 2;ANSI |  | 1 |  |  | Overcurrent\IDMT1 neg | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | Parameter subset 2 |  | 1 |  |  | Overcurrent\IDMT1 neg | resetdis | Real | 0 | 0
x073_u002E_052 | Parametersatz 2->AMZ_1 | 073.052 | 0.01-4:0.01;blockiert=4.02 | Inom | IB,E PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x017_u002E_096;x073_u002E_070 | E;NE;NE | Parameter subset 2;1;1 | 1 | 4 | SE | 4 | Overcurrent\IDMT1 N | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Overcurrent\IDMT1 N | outserv | Real | E | 1 | 0 | 4.02
[16 empty] | SE | 4 | Overcurrent\IDMT1 N | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\IDMT1 N | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 4.02 | Overcurrent\IDMT1 N | outserv | Real | 0 | 1
[18 empty] | Overcurrent\IDMT1 KI N | outserv | Real | 0 | 1
x073_u002E_058 | Parametersatz 2->AMZ_1 | 073.058 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Kennlinientyp E PS2 | Enum | Parameter__Funktionsparameter | Definite Time;IEC Standard Inverse;IEC Very Inverse;IEC Extremely Inverse;IEC Long Time Inverse;IEEE Moderately Inverse;IEEE Very Inverse;IEEE Extremely Inverse;ANSI Normally Inverse;ANSI Short Time Inverse;ANSI Long Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | 1 | x003_u002E_060 | E | Parameter subset 2 | Definite Time | 1 |  |  | Overcurrent\IDMT1 N | pcharac | String |  |  | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 1 | Overcurrent\IDMT1 N | pcharac | String
x073_u002E_055 | Parametersatz 2->AMZ_1 | 073.055 | 0.05-10:0.01 |  | Kennl.f. kt,E PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 2 | 1 | 2 |  |  | Overcurrent\IDMT1 N | Tpset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 1 | Overcurrent\IDMT1 N | Tpset | Real |  |  | 1 | 0
[18 empty] | Overcurrent\IDMT1 N | Tadder | Real | 1 | 0
x073_u002E_079 | Parametersatz 2->AMZ_1 | 073.079 | 0-10:0.001 | s | min. Auslösez.E PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 2 | 0 | 1 |  |  | Overcurrent\IDMT1 N | minresptime | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 1 | Overcurrent\IDMT1 N | minresptime | Real |  |  | 1 | 0
x073_u002E_061 | Parametersatz 2->AMZ_1 | 073.061 | unverzögert¦0;verzögert gem. Kennl¦1 |  | Rückfallen E PS2 | Enum | Parameter__Funktionsparameter | 0;1 | Real | 3 | x003_u002E_060;x073_u002E_058 | E;SW | Parameter subset 2;IEEE | 0 | 1 |  |  | Overcurrent\IDMT1 N | resetdis | Real | 1 | 0 | 1 | x003_u002E_060 |  |  |  | Parameter subset 2 | 1 | Overcurrent\IDMT1 N | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x073_u002E_058 | E;SW | Parameter subset 2;ANSI |  | 1 |  |  | Overcurrent\IDMT1 N | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | Parameter subset 2 |  | 1 |  |  | Overcurrent\IDMT1 N | resetdis | Real | 0 | 0
x076_u002E_043 | Parametersatz 2->AMZ_2 | 076.043 | nein¦0;ja¦1 |  | Freigabe PS2 | Enum | Parameter__Funktionsparameter | 1;0 | Real | 1 | x003_u002E_060;x017_u002E_052 | E;NE | Parameter subset 2;1 | 1 | 6 | E | 1 | Overcurrent\IDMT2 P | outserv | Real | 0 | 1 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 3 | Overcurrent\IDMT2 P | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\IDMT2 neg | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\IDMT2 neg | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\IDMT2 N | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\IDMT2 N | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 0 | Overcurrent\IDMT2 P | ModFrame | Real | 0 | 1
[16 empty] | E | 0 | Overcurrent\IDMT2 neg | ModFrame | Real | 0 | 1
[16 empty] | E | 0 | Overcurrent\IDMT2 N | ModFrame | Real | 0 | 1
x076_u002E_237 | Parametersatz 2->AMZ_2 | 076.237 | 0.1-4:0.01;blockiert=4.02 | Inom | IB,L PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x017_u002E_052;x076_u002E_043 | E;NE;NE | Parameter subset 2;1;1 | 1 | 3 | SE | 4 | Overcurrent\IDMT2 P | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Overcurrent\IDMT2 P | outserv | Real | E | 1 | 0 | 4.02
[16 empty] | SE | 4 | Overcurrent\IDMT2 P | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\IDMT2 P | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 4.02 | Overcurrent\IDMT2 P | outserv | Real | 0 | 1
x071_u002E_005 | Parametersatz 2->AMZ_2 | 071.005 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Kennlinientyp L PS2 | Enum | Parameter__Funktionsparameter | Definite Time;IEC Standard Inverse;IEC Very Inverse;IEC Extremely Inverse;IEC Long Time Inverse;IEEE Moderately Inverse;IEEE Very Inverse;IEEE Extremely Inverse;ANSI Normally Inverse;ANSI Short Time Inverse;ANSI Long Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | 1 | x003_u002E_060 | E | Parameter subset 2 | Definite Time | 1 |  |  | Overcurrent\IDMT2 P | pcharac | String |  |  | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 1 | Overcurrent\IDMT2 P | pcharac | String
x078_u002E_251 | Parametersatz 2->AMZ_2 | 078.251 | 0.05-10:0.01 |  | Kennl.fakt. kt,L PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 2 | 1 | 1 |  |  | Overcurrent\IDMT2 P | Tpset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 1 | Overcurrent\IDMT2 P | Tpset | Real |  |  | 1 | 0
x071_u002E_045 | Parametersatz 2->AMZ_2 | 071.045 | 0-10:0.001 | s | min. Auslösez. L PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 2 | 0 | 1 |  |  | Overcurrent\IDMT2 P | minresptime | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 1 | Overcurrent\IDMT2 P | minresptime | Real |  |  | 1 | 0
x071_u002E_017 | Parametersatz 2->AMZ_2 | 071.017 | unverzögert¦0;verzögert gem. Kennl¦1 |  | Rückfallen L PS2 | Enum | Parameter__Funktionsparameter | 0;1 | Real | 3 | x003_u002E_060;x071_u002E_005 | E;SW | Parameter subset 2;IEEE | 0 | 1 |  |  | Overcurrent\IDMT2 P | resetdis | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 1 | Overcurrent\IDMT2 P | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x071_u002E_005 | E;SW | Parameter subset 2;ANSI |  | 1 |  |  | Overcurrent\IDMT2 P | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | Parameter subset 2 |  | 1 |  |  | Overcurrent\IDMT2 P | resetdis | Real | 0 | 0
x076_u002E_251 | Parametersatz 2->AMZ_2 | 076.251 | 0.01-4:0.01;blockiert=4.02 | Inom | IB,gegen PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x017_u002E_052;x076_u002E_043 | E;NE;NE | Parameter subset 2;1;1 | 1 | 3 | SE | 4 | Overcurrent\IDMT2 neg | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Overcurrent\IDMT2 neg | outserv | Real | E | 1 | 0 | 4.02
[16 empty] | SE | 4 | Overcurrent\IDMT2 neg | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\IDMT2 neg | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 4.02 | Overcurrent\IDMT2 neg | outserv | Real | 0 | 1
x071_u002E_009 | Parametersatz 2->AMZ_2 | 071.009 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Kennl.typ gegen PS2 | Enum | Parameter__Funktionsparameter | Definite Time;IEC Standard Inverse;IEC Very Inverse;IEC Extremely Inverse;IEC Long Time Inverse;IEEE Moderately Inverse;IEEE Very Inverse;IEEE Extremely Inverse;ANSI Normally Inverse;ANSI Short Time Inverse;ANSI Long Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | 1 | x003_u002E_060 | E | Parameter subset 2 | Definite Time | 1 |  |  | Overcurrent\IDMT2 neg | pcharac | String |  |  | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 1 | Overcurrent\IDMT2 neg | pcharac | String
x079_u002E_251 | Parametersatz 2->AMZ_2 | 079.251 | 0.05-10:0.01 |  | Kennl.f. kt,gegn PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 2 | 1 | 1 |  |  | Overcurrent\IDMT2 neg | Tpset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 1 | Overcurrent\IDMT2 neg | Tpset | Real |  |  | 1 | 0
x071_u002E_049 | Parametersatz 2->AMZ_2 | 071.049 | 0-10:0.001 | s | min.Auslösez.geg PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 2 | 0 | 1 |  |  | Overcurrent\IDMT2 neg | minresptime | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 1 | Overcurrent\IDMT2 neg | minresptime | Real |  |  | 1 | 0
x071_u002E_021 | Parametersatz 2->AMZ_2 | 071.021 | unverzögert¦0;verzögert gem. Kennl¦1 |  | Rückfallen gegen PS2 | Enum | Parameter__Funktionsparameter | 0;1 | Real | 3 | x003_u002E_060;x071_u002E_009 | E;SW | Parameter subset 2;IEEE | 0 | 1 |  |  | Overcurrent\IDMT2 neg | resetdis | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 1 | Overcurrent\IDMT2 neg | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x071_u002E_009 | E;SW | Parameter subset 2;ANSI |  | 1 |  |  | Overcurrent\IDMT2 neg | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | Parameter subset 2 |  | 1 |  |  | Overcurrent\IDMT2 neg | resetdis | Real | 0 | 0
x077_u002E_251 | Parametersatz 2->AMZ_2 | 077.251 | 0.01-4:0.01;blockiert=4.02 | Inom | IB,E PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x017_u002E_052;x076_u002E_043 | E;NE;NE | Parameter subset 2;1;1 | 1 | 3 | SE | 4 | Overcurrent\IDMT2 N | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Overcurrent\IDMT2 N | outserv | Real | E | 1 | 0 | 4.02
[16 empty] | SE | 4 | Overcurrent\IDMT2 N | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\IDMT2 N | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 4.02 | Overcurrent\IDMT2 N | outserv | Real | 0 | 1
x071_u002E_013 | Parametersatz 2->AMZ_2 | 071.013 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Kennlinientyp E PS2 | Enum | Parameter__Funktionsparameter | Definite Time;IEC Standard Inverse;IEC Very Inverse;IEC Extremely Inverse;IEC Long Time Inverse;IEEE Moderately Inverse;IEEE Very Inverse;IEEE Extremely Inverse;ANSI Normally Inverse;ANSI Short Time Inverse;ANSI Long Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | 1 | x003_u002E_060 | E | Parameter subset 2 | Definite Time | 1 |  |  | Overcurrent\IDMT2 N | pcharac | String |  |  | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 1 | Overcurrent\IDMT2 N | pcharac | String
x071_u002E_001 | Parametersatz 2->AMZ_2 | 071.001 | 0.05-10:0.01 |  | Kennl.f. kt,E PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 2 | 1 | 1 |  |  | Overcurrent\IDMT2 N | Tpset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 1 | Overcurrent\IDMT2 N | Tpset | Real |  |  | 1 | 0
x071_u002E_053 | Parametersatz 2->AMZ_2 | 071.053 | 0-10:0.001 | s | min. Auslösez.E PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 2 | 0 | 1 |  |  | Overcurrent\IDMT2 N | minresptime | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 1 | Overcurrent\IDMT2 N | minresptime | Real |  |  | 1 | 0
x071_u002E_025 | Parametersatz 2->AMZ_2 | 071.025 | unverzögert¦0;verzögert gem. Kennl¦1 |  | Rückfallen E PS2 | Enum | Parameter__Funktionsparameter | 0;1 | Real | 3 | x003_u002E_060;x071_u002E_013 | E;SW | Parameter subset 2;IEEE | 0 | 1 |  |  | Overcurrent\IDMT2 N | resetdis | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 1 | Overcurrent\IDMT2 N | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x071_u002E_013 | E;SW | Parameter subset 2;ANSI |  | 1 |  |  | Overcurrent\IDMT2 N | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | Parameter subset 2 |  | 1 |  |  | Overcurrent\IDMT2 N | resetdis | Real | 0 | 0
x077_u002E_235 | Parametersatz 2->KURI | 077.235 | nein¦0;ja¦1 |  | Freigabe PS2 | Enum | Parameter__Funktionsparameter | 1;0 | Real | 1 | x003_u002E_060;x017_u002E_070 | E;NE | Parameter subset 2;1 | 1 | 2 |  |  | Overcurrent\Directional P | outserv | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Overcurrent\Directional P | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\Directional N | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\Directional N | outserv | Real | E | 0 | 0 | 0
x077_u002E_237 | Parametersatz 2->KURI | 077.237 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung tI> PS2 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real | 1 | x003_u002E_060;x017_u002E_070;x077_u002E_235 | E;NE;NE | Parameter subset 2;1;1 | 1 | 1 |  |  | Overcurrent\DTOC I> | idir | Real | 1 | 0 | 1 | Overcurrent\Directional P;x003_u002E_060 | outserv | Real | E;E | 0;Parameter subset 2 | 1 | Overcurrent\DTOC I> | idir | Real |  |  | 1 | 0
x077_u002E_238 | Parametersatz 2->KURI | 077.238 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung tI>> PS2 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real | 1 | x003_u002E_060;x017_u002E_070;x077_u002E_235 | E;NE;NE | Parameter subset 2;1;1 | 1 | 1 |  |  | Overcurrent\DTOC I>> | idir | Real | 1 | 0 | 1 | Overcurrent\Directional P;x003_u002E_060 | outserv | Real | E;E | 0;Parameter subset 2 | 1 | Overcurrent\DTOC I>> | idir | Real |  |  | 1 | 0
x077_u002E_240 | Parametersatz 2->KURI | 077.240 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung tIE> PS2 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real | 1 | x003_u002E_060;x017_u002E_070;x077_u002E_235 | E;NE;NE | Parameter subset 2;1;1 | 1 | 1 |  |  | Overcurrent\DTOC IN> | idir | Real | 1 | 0 | 1 | Overcurrent\Directional N;x003_u002E_060 | outserv | Real | E;E | 0;Parameter subset 2 | 1 | Overcurrent\DTOC IN> | idir | Real |  |  | 1 | 0
x077_u002E_241 | Parametersatz 2->KURI | 077.241 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung tIE>> PS2 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real | 1 | x003_u002E_060;x017_u002E_070;x077_u002E_235 | E;NE;NE | Parameter subset 2;1;1 | 1 | 1 |  |  | Overcurrent\DTOC IN>> | idir | Real | 1 | 0 | 1 | Overcurrent\Directional N;x003_u002E_060 | outserv | Real | E;E | 0;Parameter subset 2 | 1 | Overcurrent\DTOC IN>> | idir | Real |  |  | 1 | 0
x077_u002E_239 | Parametersatz 2->KURI | 077.239 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung tIB,L> PS2 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real | 1 | x003_u002E_060;x017_u002E_070;x077_u002E_235 | E;NE;NE | Parameter subset 2;1;1 | 1 | 1 |  |  | Overcurrent\IDMT1 P | idir | Real | 1 | 0 | 1 | Overcurrent\Directional P;x003_u002E_060 | outserv | Real | E;E | 0;Parameter subset 2 | 1 | Overcurrent\IDMT1 P | idir | Real |  |  | 1 | 0
x077_u002E_242 | Parametersatz 2->KURI | 077.242 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung tIB,E> PS2 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real | 1 | x003_u002E_060;x017_u002E_070;x077_u002E_235 | E;NE;NE | Parameter subset 2;1;1 | 1 | 1 |  |  | Overcurrent\IDMT1 N | idir | Real | 1 | 0 | 1 | Overcurrent\Directional N;x003_u002E_060 | outserv | Real | E;E | 0;Parameter subset 2 | 1 | Overcurrent\IDMT1 N | idir | Real |  |  | 1 | 0
x077_u002E_243 | Parametersatz 2->KURI | 077.243 | -90-90:0.1 | ° | charakt.Winkel E PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 2 | -45 | 1 |  |  | Overcurrent\Directional N | mtau | Real | 1 | 0 | 1 | Overcurrent\Directional N;x003_u002E_060 | outserv | Real | E;E | 0;Parameter subset 2 | 1 | Overcurrent\Directional N | mtau | Real |  |  | 1 | 0
x077_u002E_244 | Parametersatz 2->KURI | 077.244 | 0.015-0.6:0.001 | Unom(/©3) | UNE> PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 2 | 0.1 | 1 |  |  | Overcurrent\Directional N | upolur | Real | 1 | 0 | 1 | Overcurrent\Directional N;x003_u002E_060 | outserv | Real | E;E | 0;Parameter subset 2 | 1 | Overcurrent\Directional N | upolur | Real |  |  | 1 | 0
x077_u002E_246 | Parametersatz 2->U<> | 077.246 | nein¦0;ja¦1 |  | Freigabe PS2 | Enum | Parameter__Funktionsparameter | 1;0 | Real | 1 | x003_u002E_060;x023_u002E_030 | E;NE | Parameter subset 2;1 | 1 | 1 |  |  | Voltage | outserv | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 1 | Voltage | outserv | Real | E | 0 | 0 | 0
x077_u002E_001 | Parametersatz 2->U<> | 077.001 | Dreieck¦0;Stern¦1 |  | Betriebsart PS2 | Enum | Parameter__Funktionsparameter | Delta;Star | String | 1 | x003_u002E_060 | E | Parameter subset 2 | Delta | 8 | E | Star | Voltage\V> | outserv | Real | 0 | 1
[16 empty] | E | Star | Voltage\V>> | outserv | Real | 0 | 1
[16 empty] | E | Star | Voltage\V< | outserv | Real | 0 | 1
[16 empty] | E | Star | Voltage\V<< | outserv | Real | 0 | 1
[16 empty] | E | Star | Voltage\VNG> | outserv | Real | 0 | 1
[16 empty] | E | Star | Voltage\VNG>> | outserv | Real | 0 | 1
x077_u002E_003 | Parametersatz 2->U<> | 077.003 | 0.2-1.5:0.01;blockiert=1.52 | Unom(/©3) | U> PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x077_u002E_001 | E;E | Parameter subset 2;Delta | 1.1 | 3 | SE | 1.5 | Voltage\V> | Uset | Real | 1 | 0 | 1 | x003_u002E_060;x077_u002E_001 |  |  | E;E | Parameter subset 2;Delta | 2 | Voltage\V> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V> | outserv | Real | 0 | 0 | [7 empty] | Voltage\V> | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.52 | Voltage\V> | outserv | Real | 0 | 1
x077_u002E_004 | Parametersatz 2->U<> | 077.004 | 0.2-1.5:0.01;blockiert=1.52 | Unom(/©3) | U>> PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x077_u002E_001 | E;E | Parameter subset 2;Delta | 1.1 | 3 | SE | 1.5 | Voltage\V>> | Uset | Real | 1 | 0 | 1 | x003_u002E_060;x077_u002E_001 |  |  | E;E | Parameter subset 2;Delta | 2 | Voltage\V>> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\V>> | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.52 | Voltage\V>> | outserv | Real | 0 | 1
x077_u002E_005 | Parametersatz 2->U<> | 077.005 | 0-100:0.01;blockiert=100.02 | s | tU> PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 2 | 1 | 2 | SE | 100 | Voltage\V> | Tdel | Real | 1 | 0 | 1 | x003_u002E_060;x077_u002E_001 |  |  | E;E | Parameter subset 2;Delta | 2 | Voltage\V> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\V> | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\V> | Tdel | Real |  |  | 0 | 100.02
x077_u002E_006 | Parametersatz 2->U<> | 077.006 | 0-100:0.01;blockiert=100.02 | s | tU>> PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 2 | 1 | 2 | SE | 100 | Voltage\V>> | Tdel | Real | 1 | 0 | 1 | x003_u002E_060;x077_u002E_001 |  |  | E;E | Parameter subset 2;Delta | 2 | Voltage\V>> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\V>> | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\V>> | Tdel | Real |  |  | 0 | 100.02
x077_u002E_027 | Parametersatz 2->U<> | 077.027 | 0-100:0.01;blockiert=100.02 | s | tU> 3p PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 2 | 1 | 2 | SE | 100 | Voltage\tV> 3-pole | Tdelay | Real | 1 | 0 | 1 | x003_u002E_060;x077_u002E_001 |  |  | E;E | Parameter subset 2;Delta | 2 | Voltage\tV> 3-pole | Tdelay | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\tV> 3-pole | Tdelay | Real | 0 | 9999999 | [7 empty] | Voltage\tV> 3-pole | Tdelay | Real |  |  | 0 | 100.02
x077_u002E_007 | Parametersatz 2->U<> | 077.007 | 0.2-1.5:0.01;blockiert=1.52 | Unom(/©3) | U< PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x077_u002E_001 | E;E | Parameter subset 2;Delta | 0.8 | 3 | SE | 1.5 | Voltage\V< | Uset | Real | 1 | 0 | 1 | x003_u002E_060;x077_u002E_001 |  |  | E;E | Parameter subset 2;Delta | 2 | Voltage\V< | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V< | outserv | Real | 0 | 0 | [7 empty] | Voltage\V< | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.52 | Voltage\V< | outserv | Real | 0 | 1
x077_u002E_008 | Parametersatz 2->U<> | 077.008 | 0.2-1.5:0.01;blockiert=1.52 | Unom(/©3) | U<< PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x077_u002E_001 | E;E | Parameter subset 2;Delta | 0.8 | 3 | SE | 1.5 | Voltage\V<< | Uset | Real | 1 | 0 | 1 | x003_u002E_060;x077_u002E_001 |  |  | E;E | Parameter subset 2;Delta | 2 | Voltage\V<< | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V<< | outserv | Real | 0 | 0 | [7 empty] | Voltage\V<< | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.52 | Voltage\V<< | outserv | Real | 0 | 1
x077_u002E_009 | Parametersatz 2->U<> | 077.009 | 0-100:0.01;blockiert=100.02 | s | tU< PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 2 | 1 | 2 | SE | 100 | Voltage\V< | Tdel | Real | 1 | 0 | 1 | x003_u002E_060;x077_u002E_001 |  |  | E;E | Parameter subset 2;Delta | 2 | Voltage\V< | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\V< | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\V< | Tdel | Real |  |  | 0 | 100.02
x077_u002E_010 | Parametersatz 2->U<> | 077.010 | 0-100:0.01;blockiert=100.02 | s | tU<< PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 2 | 1 | 2 | SE | 100 | Voltage\V<< | Tdel | Real | 1 | 0 | 1 | x003_u002E_060;x077_u002E_001 |  |  | E;E | Parameter subset 2;Delta | 2 | Voltage\V<< | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\V<< | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\V<< | Tdel | Real |  |  | 0 | 100.02
x077_u002E_028 | Parametersatz 2->U<> | 077.028 | 0-100:0.01;blockiert=100.02 | s | tU< 3p PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 2 | 1 | 2 | SE | 100 | Voltage\tV< 3-pole | Tdelay | Real | 1 | 0 | 1 | x003_u002E_060;x077_u002E_001 |  |  | E;E | Parameter subset 2;Delta | 2 | Voltage\tV< 3-pole | Tdelay | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\tV< 3-pole | Tdelay | Real | 0 | 9999999 | [7 empty] | Voltage\tV< 3-pole | Tdelay | Real |  |  | 0 | 100.02
x077_u002E_015 | Parametersatz 2->U<> | 077.015 | 0.2-1.5:0.01;blockiert=1.52 | Unom/©3 | Umit> PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 2 | 1.1 | 3 | SE | 1.5 | Voltage\Vpos> | Uset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Voltage\Vpos> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos> | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.52 | Voltage\Vpos> | outserv | Real | 0 | 1
x077_u002E_016 | Parametersatz 2->U<> | 077.016 | 0.2-1.5:0.01;blockiert=1.52 | Unom/©3 | Umit>> PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 2 | 1.1 | 3 | SE | 1.5 | Voltage\Vpos>> | Uset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Voltage\Vpos>> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos>> | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.52 | Voltage\Vpos>> | outserv | Real | 0 | 1
x077_u002E_017 | Parametersatz 2->U<> | 077.017 | 0-100:0.01;blockiert=100.02 | s | tUmit> PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 2 | 1 | 2 | SE | 100 | Voltage\Vpos> | Tdel | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Voltage\Vpos> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\Vpos> | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\Vpos> | Tdel | Real |  |  | 0 | 100.02
x077_u002E_018 | Parametersatz 2->U<> | 077.018 | 0-100:0.01;blockiert=100.02 | s | tUmit>> PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 2 | 1 | 2 | SE | 100 | Voltage\Vpos>> | Tdel | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Voltage\Vpos>> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\Vpos>> | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\Vpos>> | Tdel | Real |  |  | 0 | 100.02
x077_u002E_019 | Parametersatz 2->U<> | 077.019 | 0.2-1.5:0.01;blockiert=1.52 | Unom/©3 | Umit< PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 2 | 0.8 | 3 | SE | 1.5 | Voltage\Vpos< | Uset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Voltage\Vpos< | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos< | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos< | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.52 | Voltage\Vpos< | outserv | Real | 0 | 1
x077_u002E_020 | Parametersatz 2->U<> | 077.020 | 0.2-1.5:0.01;blockiert=1.52 | Unom/©3 | Umit<< PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 2 | 0.8 | 3 | SE | 1.5 | Voltage\Vpos<< | Uset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Voltage\Vpos<< | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos<< | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos<< | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.52 | Voltage\Vpos<< | outserv | Real | 0 | 1
x077_u002E_021 | Parametersatz 2->U<> | 077.021 | 0-100:0.01;blockiert=100.02 | s | tUmit< PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 2 | 1 | 2 | SE | 100 | Voltage\Vpos< | Tdel | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Voltage\Vpos< | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\Vpos< | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\Vpos< | Tdel | Real |  |  | 0 | 100.02
x077_u002E_022 | Parametersatz 2->U<> | 077.022 | 0-100:0.01;blockiert=100.02 | s | tUmit<< PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 2 | 1 | 2 | SE | 100 | Voltage\Vpos<< | Tdel | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Voltage\Vpos<< | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\Vpos<< | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\Vpos<< | Tdel | Real |  |  | 0 | 100.02
x077_u002E_023 | Parametersatz 2->U<> | 077.023 | 0.02-1.5:0.01;blockiert=1.52 | Unom/©3 | Ugegen> PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 2 | 1.52 | 3 | SE | 1.5 | Voltage\Vneg> | Uset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Voltage\Vneg> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vneg> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vneg> | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.52 | Voltage\Vneg> | outserv | Real | 0 | 1
x077_u002E_024 | Parametersatz 2->U<> | 077.024 | 0.02-1.5:0.01;blockiert=1.52 | Unom/©3 | Ugegen>> PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 2 | 1.52 | 3 | SE | 1.5 | Voltage\Vneg>> | Uset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Voltage\Vneg>> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vneg>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vneg>> | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.52 | Voltage\Vneg>> | outserv | Real | 0 | 1
x077_u002E_025 | Parametersatz 2->U<> | 077.025 | 0-100:0.01;blockiert=100.02 | s | tUgegen> PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 2 | 1 | 2 | SE | 100 | Voltage\Vneg> | Tdel | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Voltage\Vneg> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\Vneg> | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\Vneg> | Tdel | Real |  |  | 0 | 100.02
x077_u002E_026 | Parametersatz 2->U<> | 077.026 | 0-100:0.01;blockiert=100.02 | s | tUgegen>> PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 2 | 1 | 2 | SE | 100 | Voltage\Vneg>> | Tdel | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Voltage\Vneg>> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\Vneg>> | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\Vneg>> | Tdel | Real |  |  | 0 | 100.02
x077_u002E_011 | Parametersatz 2->U<> | 077.011 | 0.02-1:0.01;blockiert=1.02 | Unom(/©3) | UNE> PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x077_u002E_001 | E;E | Parameter subset 2;Delta | 1.02 | 3 | SE | 1 | Voltage\VNG> | Uset | Real | 1 | 0 | 1 | x003_u002E_060;x077_u002E_001 |  |  | E;E | Parameter subset 2;Delta | 2 | Voltage\VNG> | outserv | Real | E | 1 | 0 | 1.02
[16 empty] | SE | 1 | Voltage\VNG> | outserv | Real | 0 | 0 | [7 empty] | Voltage\VNG> | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.02 | Voltage\VNG> | outserv | Real | 0 | 1
x077_u002E_012 | Parametersatz 2->U<> | 077.012 | 0.02-1:0.01;blockiert=1.02 | Unom(/©3) | UNE>> PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x077_u002E_001 | E;E | Parameter subset 2;Delta | 1.02 | 3 | SE | 1 | Voltage\VNG>> | Uset | Real | 1 | 0 | 1 | x003_u002E_060;x077_u002E_001 |  |  | E;E | Parameter subset 2;Delta | 2 | Voltage\VNG>> | outserv | Real | E | 1 | 0 | 1.02
[16 empty] | SE | 1 | Voltage\VNG>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\VNG>> | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.02 | Voltage\VNG>> | outserv | Real | 0 | 1
x077_u002E_013 | Parametersatz 2->U<> | 077.013 | 0-100:0.01;blockiert=100.02 | s | tUNE> PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 2 | 1 | 2 | SE | 100 | Voltage\VNG> | Tdel | Real | 1 | 0 | 1 | x003_u002E_060;x077_u002E_001 |  |  | E;E | Parameter subset 2;Delta | 2 | Voltage\VNG> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\VNG> | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\VNG> | Tdel | Real |  |  | 0 | 100.02
x077_u002E_014 | Parametersatz 2->U<> | 077.014 | 0-100:0.01;blockiert=100.02 | s | tUNE>> PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 2 | 1 | 2 | SE | 100 | Voltage\VNG>> | Tdel | Real | 1 | 0 | 1 | x003_u002E_060;x077_u002E_001 |  |  | E;E | Parameter subset 2;Delta | 2 | Voltage\VNG>> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\VNG>> | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\VNG>> | Tdel | Real |  |  | 0 | 100.02
x001_u002E_163 | Parametersatz 2->U<> | 001.163 | ohne¦0;mit¦1 |  | Btr.art U< Überw PS2 | Enum | Parameter__Funktionsparameter | 1;0 | Real | 1 | x003_u002E_060 | E | Parameter subset 2 | 1 | 1 |  |  | Voltage\Imin | outserv | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 1 | Voltage\Imin | outserv | Real |  |  | 1 | 0
x001_u002E_159 | Parametersatz 2->U<> | 001.159 | 0.04-1:0.01 | Inom | I-Freigabe U< PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 2 | 0.1 | 1 |  |  | Voltage\Imin | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 1 | Voltage\Imin | Ipset | Real |  |  | 1 | 0
x018_u002E_197 | Parametersatz 2->f<> | 018.197 | nein¦0;ja¦1 |  | Freigabe PS2 | Enum | Parameter__Funktionsparameter | 1;0 | Real | 1 | x003_u002E_060;x023_u002E_031 | E;NE | Parameter subset 2;1 | 1 | 1 |  |  | Frequency | outserv | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 1 | Frequency | outserv | Real | E | 0 | 0 | 0
x018_u002E_121 | Parametersatz 2->f<> | 018.121 | f¦0;f mit df/dt¦1;f m. Delta f/Delta t¦2 |  | Betriebsart f1 PS2 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real | 1 | x003_u002E_060 | E | Parameter subset 2 | 0 | 1 | E | 0 | Frequency\df1/dt | outserv | Real | 0 | 1 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 3 | Frequency\f1 | outserv | Real | E | 1 | 0 | 0
[30 empty] | Frequency\df1/dt | outserv | Real | E | 1 | 0 | 0
[30 empty] | Frequency\df1/dt | outserv | Real |  |  | 0 | 1
x018_u002E_101 | Parametersatz 2->f<> | 018.101 | 40-70:0.01;blockiert=70.02 | Hz | f1 PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 2 | 49.8 | 3 | SE | 70 | Frequency\f1 | Fset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Frequency\f1 | outserv | Real | E | 1 | 0 | 70.02
[16 empty] | SE | 70 | Frequency\f1 | outserv | Real | 0 | 0 | [7 empty] | Frequency\f1 | Fset | Real |  |  | 1 | 0
[16 empty] | GE | 70.02 | Frequency\f1 | outserv | Real | 0 | 1
x018_u002E_105 | Parametersatz 2->f<> | 018.105 | 0-10:0.001;blockiert=10.002 | s | tf1 PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 2 | 0 | 4 | SE | 10 | Frequency\f1 | Tdel | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 4 | Frequency\f1 | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | GE | 10.002 | Frequency\f1 | Tdel | Real | 0 | 9999999 | [7 empty] | Frequency\f1 | Tdel | Real |  |  | 0 | 10.002
[16 empty] | SE | 10 | Frequency\df1/dt | Tdel | Real | 1 | 0 | [7 empty] | Frequency\df1/dt | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | GE | 10.002 | Frequency\df1/dt | Tdel | Real | 0 | 9999999 | [7 empty] | Frequency\df1/dt | Tdel | Real |  |  | 0 | 10.002
x018_u002E_109 | Parametersatz 2->f<> | 018.109 | 0.1-10:0.001;blockiert=10.002 | Hz/s | df1/dt PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x018_u002E_121 | E;E | Parameter subset 2;1 | 2 | 3 | SE | 10 | Frequency\df1/dt | dFset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Frequency\df1/dt | outserv | Real | E | 1 | 0 | 10.002
[16 empty] | SE | 10 | Frequency\df1/dt | outserv | Real | 0 | 0 | [7 empty] | Frequency\df1/dt | dFset | Real |  |  | 1 | 0
[16 empty] | GE | 10.002 | Frequency\df1/dt | outserv | Real | 0 | 1
x018_u002E_145 | Parametersatz 2->f<> | 018.145 | f¦0;f mit df/dt¦1;f m. Delta f/Delta t¦2 |  | Betriebsart f2 PS2 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real | 1 | x003_u002E_060 | E | Parameter subset 2 | 0 | 1 | E | 0 | Frequency\df2/dt | outserv | Real | 0 | 1 |  | x003_u002E_060 |  |  | E | Parameter subset 2 | 3 | Frequency\f2 | outserv | Real | E | 1 | 0 | 0
[30 empty] | Frequency\df2/dt | outserv | Real | E | 1 | 0 | 0
[30 empty] | Frequency\df2/dt | outserv | Real |  |  | 0 | 1
x018_u002E_125 | Parametersatz 2->f<> | 018.125 | 40-70:0.01;blockiert=70.02 | Hz | f2 PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 2 | 49.8 | 3 | SE | 70 | Frequency\f2 | Fset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Frequency\f2 | outserv | Real | E | 1 | 0 | 70.02
[16 empty] | SE | 70 | Frequency\f2 | outserv | Real | 0 | 0 | [7 empty] | Frequency\f2 | Fset | Real |  |  | 1 | 0
[16 empty] | GE | 70.02 | Frequency\f2 | outserv | Real | 0 | 1
x018_u002E_129 | Parametersatz 2->f<> | 018.129 | 0-10:0.001;blockiert=10.002 | s | tf2 PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 2 | 0 | 4 | SE | 10 | Frequency\f2 | Tdel | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 4 | Frequency\f2 | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | GE | 10.002 | Frequency\f2 | Tdel | Real | 0 | 9999999 | [7 empty] | Frequency\f2 | Tdel | Real |  |  | 0 | 10.002
[16 empty] | SE | 10 | Frequency\df2/dt | Tdel | Real | 1 | 0 | [7 empty] | Frequency\df2/dt | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | GE | 10.002 | Frequency\df2/dt | Tdel | Real | 0 | 9999999 | [7 empty] | Frequency\df2/dt | Tdel | Real |  |  | 0 | 10.002
x018_u002E_133 | Parametersatz 2->f<> | 018.133 | 0.1-10:0.001;blockiert=10.002 | Hz/s | df2/dt PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x018_u002E_145 | E;E | Parameter subset 2;1 | 2 | 3 | SE | 10 | Frequency\df2/dt | dFset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Frequency\df2/dt | outserv | Real | E | 1 | 0 | 10.002
[16 empty] | SE | 10 | Frequency\df2/dt | outserv | Real | 0 | 0 | [7 empty] | Frequency\df2/dt | dFset | Real |  |  | 1 | 0
[16 empty] | GE | 10.002 | Frequency\df2/dt | outserv | Real | 0 | 1
x018_u002E_169 | Parametersatz 2->f<> | 018.169 | f¦0;f mit df/dt¦1;f m. Delta f/Delta t¦2 |  | Betriebsart f3 PS2 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real | 1 | x003_u002E_060 | E | Parameter subset 2 | 0 | 1 | E | 0 | Frequency\df3/dt | outserv | Real | 0 | 1 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Frequency\f3 | outserv | Real | E | 1 | 0 | 0
[30 empty] | Frequency\df3/dt | outserv | Real | E | 1 | 0 | 0
[30 empty] | Frequency\df3/dt | outserv | Real |  |  | 0 | 1
x018_u002E_149 | Parametersatz 2->f<> | 018.149 | 40-70:0.01;blockiert=70.02 | Hz | f3 PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 2 | 49.8 | 3 | SE | 70 | Frequency\f3 | Fset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Frequency\f3 | outserv | Real | E | 1 | 0 | 70.02
[16 empty] | SE | 70 | Frequency\f3 | outserv | Real | 0 | 0 | [7 empty] | Frequency\f3 | Fset | Real |  |  | 1 | 0
[16 empty] | GE | 70.02 | Frequency\f3 | outserv | Real | 0 | 1
x018_u002E_153 | Parametersatz 2->f<> | 018.153 | 0-10:0.001;blockiert=10.002 | s | tf3 PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 2 | 0 | 4 | SE | 10 | Frequency\f3 | Tdel | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 4 | Frequency\f3 | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | GE | 10.002 | Frequency\f3 | Tdel | Real | 0 | 9999999 | [7 empty] | Frequency\f3 | Tdel | Real |  |  | 0 | 10.002
[16 empty] | SE | 10 | Frequency\df3/dt | Tdel | Real | 1 | 0 | [7 empty] | Frequency\df3/dt | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | GE | 10.002 | Frequency\df3/dt | Tdel | Real | 0 | 9999999 | [7 empty] | Frequency\df3/dt | Tdel | Real |  |  | 0 | 10.002
x018_u002E_157 | Parametersatz 2->f<> | 018.157 | 0.1-10:0.001;blockiert=10.002 | Hz/s | df3/dt PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x018_u002E_169 | E;E | Parameter subset 2;1 | 2 | 3 | SE | 10 | Frequency\df3/dt | dFset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Frequency\df3/dt | outserv | Real | E | 1 | 0 | 10.002
[16 empty] | SE | 10 | Frequency\df3/dt | outserv | Real | 0 | 0 | [7 empty] | Frequency\df3/dt | dFset | Real |  |  | 1 | 0
[16 empty] | GE | 10.002 | Frequency\df3/dt | outserv | Real | 0 | 1
x018_u002E_193 | Parametersatz 2->f<> | 018.193 | f¦0;f mit df/dt¦1;f m. Delta f/Delta t¦2 |  | Betriebsart f4 PS2 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real | 1 | x003_u002E_060 | E | Parameter subset 2 | 0 | 1 | E | 0 | Frequency\df4/dt | outserv | Real | 0 | 1 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Frequency\f4 | outserv | Real | E | 1 | 0 | 0
[30 empty] | Frequency\df4/dt | outserv | Real | E | 1 | 0 | 0
[30 empty] | Frequency\df4/dt | outserv | Real |  |  | 0 | 1
x018_u002E_173 | Parametersatz 2->f<> | 018.173 | 40-70:0.01;blockiert=70.02 | Hz | f4 PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 2 | 49.8 | 3 | SE | 70 | Frequency\f4 | Fset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Frequency\f4 | outserv | Real | E | 1 | 0 | 70.02
[16 empty] | SE | 70 | Frequency\f4 | outserv | Real | 0 | 0 | [7 empty] | Frequency\f4 | Fset | Real |  |  | 1 | 0
[16 empty] | GE | 70.02 | Frequency\f4 | outserv | Real | 0 | 1
x018_u002E_177 | Parametersatz 2->f<> | 018.177 | 0-10:0.001;blockiert=10.002 | s | tf4 PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 2 | 0 | 4 | SE | 10 | Frequency\f4 | Tdel | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 4 | Frequency\f4 | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | GE | 10.002 | Frequency\f4 | Tdel | Real | 0 | 9999999 | [7 empty] | Frequency\f4 | Tdel | Real |  |  | 0 | 10.002
[16 empty] | SE | 10 | Frequency\df4/dt | Tdel | Real | 1 | 0 | [7 empty] | Frequency\df4/dt | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | GE | 10.002 | Frequency\df4/dt | Tdel | Real | 0 | 9999999 | [7 empty] | Frequency\df4/dt | Tdel | Real |  |  | 0 | 10.002
x018_u002E_181 | Parametersatz 2->f<> | 018.181 | 0.1-10:0.001;blockiert=10.002 | Hz/s | df4/dt PS2 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x018_u002E_193 | E;E | Parameter subset 2;1 | 2 | 3 | SE | 10 | Frequency\df4/dt | dFset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 2 | 2 | Frequency\df4/dt | outserv | Real | E | 1 | 0 | 10.002
[16 empty] | SE | 10 | Frequency\df4/dt | outserv | Real | 0 | 0 | [7 empty] | Frequency\df4/dt | dFset | Real |  |  | 1 | 0
[16 empty] | GE | 10.002 | Frequency\df4/dt | outserv | Real | 0 | 1
x074_u002E_098 | Parametersatz 3->UMZ | 074.098 | nein¦0;ja¦1 |  | Freigabe PS3 | Enum | Parameter__Funktionsparameter | 1;0 | Real | 1 | x003_u002E_060;x022_u002E_075 | E;NE | Parameter subset 3;1 | 1 | 10 | E | 1 | Overcurrent\DTOC I> | outserv | Real | 0 | 1 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 10 | Overcurrent\DTOC I> | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\DTOC I>> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC I>> | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\DTOC I>>> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC I>>> | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\DTOC Ineg> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC Ineg> | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\DTOC Ineg>> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC Ineg>> | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\DTOC Ineg>>> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC Ineg>>> | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\DTOC Ineg>>>> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC Ineg>>>> | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\DTOC IN> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC IN> | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\DTOC IN>> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC IN>> | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\DTOC IN>>> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC IN>>> | outserv | Real | E | 0 | 0 | 0
x074_u002E_007 | Parametersatz 3->UMZ | 074.007 | 0.1-40:0.01;blockiert=40.02 | Inom | I> PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x074_u002E_098 | E;NE;NE | Parameter subset 3;1;1 | 1 | 3 | SE | 40 | Overcurrent\DTOC I> | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Overcurrent\DTOC I> | outserv | Real | E | 1 | 0 | 40.02
[16 empty] | SE | 40 | Overcurrent\DTOC I> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\DTOC I> | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 40.02 | Overcurrent\DTOC I> | outserv | Real | 0 | 1
x074_u002E_008 | Parametersatz 3->UMZ | 074.008 | 0.1-40:0.01;blockiert=40.02 | Inom | I>> PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x074_u002E_098 | E;NE;NE | Parameter subset 3;1;1 | 4 | 3 | SE | 40 | Overcurrent\DTOC I>> | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Overcurrent\DTOC I>> | outserv | Real | E | 1 | 0 | 40.02
[16 empty] | SE | 40 | Overcurrent\DTOC I>> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\DTOC I>> | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 40.02 | Overcurrent\DTOC I>> | outserv | Real | 0 | 1
x074_u002E_009 | Parametersatz 3->UMZ | 074.009 | 0.1-40:0.01;blockiert=40.02 | Inom | I>>> PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x074_u002E_098 | E;NE;NE | Parameter subset 3;1;1 | 40.02 | 4 | SE | 40 | Overcurrent\DTOC I>>> | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Overcurrent\DTOC I>>> | outserv | Real | E | 1 | 0 | 40.02
[16 empty] | SE | 40 | Overcurrent\DTOC I>>> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\DTOC I>>> | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 40.02 | Overcurrent\DTOC I>>> | outserv | Real | 0 | 1
[18 empty] | Overcurrent\DTOC I>>> | idir | Real | 0 | 0
x074_u002E_019 | Parametersatz 3->UMZ | 074.019 | 0-100:0.01;blockiert=100.02 | s | tI> PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x074_u002E_098 | E;NE;NE | Parameter subset 3;1;1 | 1 | 2 | SE | 100 | Overcurrent\DTOC I> | Tset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Overcurrent\DTOC I> | Tset | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Overcurrent\DTOC I> | Tset | Real | 0 | 9999999 | [7 empty] | Overcurrent\DTOC I> | Tset | Real |  |  | 0 | 100.02
x074_u002E_020 | Parametersatz 3->UMZ | 074.020 | 0-100:0.01;blockiert=100.02 | s | tI>> PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x074_u002E_098 | E;NE;NE | Parameter subset 3;1;1 | 0.5 | 2 | SE | 100 | Overcurrent\DTOC I>> | Tset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Overcurrent\DTOC I>> | Tset | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Overcurrent\DTOC I>> | Tset | Real | 0 | 9999999 | [7 empty] | Overcurrent\DTOC I>> | Tset | Real |  |  | 0 | 100.02
x074_u002E_021 | Parametersatz 3->UMZ | 074.021 | 0-100:0.01;blockiert=100.02 | s | tI>>> PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x074_u002E_098 | E;NE;NE | Parameter subset 3;1;1 | 0.5 | 2 | SE | 100 | Overcurrent\DTOC I>>> | Tset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Overcurrent\DTOC I>>> | Tset | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Overcurrent\DTOC I>>> | Tset | Real | 0 | 9999999 | [7 empty] | Overcurrent\DTOC I>>> | Tset | Real |  |  | 0 | 100.02
x074_u002E_011 | Parametersatz 3->UMZ | 074.011 | 0.1-25:0.01;blockiert=25.02 | Inom | Igegen> PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x074_u002E_098 | E;NE;NE | Parameter subset 3;1;1 | 1 | 3 | SE | 25 | Overcurrent\DTOC Ineg> | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Overcurrent\DTOC Ineg> | outserv | Real | E | 1 | 0 | 25.02
[16 empty] | SE | 25 | Overcurrent\DTOC Ineg> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\DTOC Ineg> | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 25.02 | Overcurrent\DTOC Ineg> | outserv | Real | 0 | 1
x074_u002E_012 | Parametersatz 3->UMZ | 074.012 | 0.1-25:0.01;blockiert=25.02 | Inom | Igegen>> PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x074_u002E_098 | E;NE;NE | Parameter subset 3;1;1 | 4 | 3 | SE | 25 | Overcurrent\DTOC Ineg>> | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Overcurrent\DTOC Ineg>> | outserv | Real | E | 1 | 0 | 25.02
[16 empty] | SE | 25 | Overcurrent\DTOC Ineg>> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\DTOC Ineg>> | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 25.02 | Overcurrent\DTOC Ineg>> | outserv | Real | 0 | 1
x074_u002E_013 | Parametersatz 3->UMZ | 074.013 | 0.1-25:0.01;blockiert=25.02 | Inom | Igegen>>> PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x074_u002E_098 | E;NE;NE | Parameter subset 3;1;1 | 25.02 | 3 | SE | 25 | Overcurrent\DTOC Ineg>>> | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Overcurrent\DTOC Ineg>>> | outserv | Real | E | 1 | 0 | 25.02
[16 empty] | SE | 25 | Overcurrent\DTOC Ineg>>> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\DTOC Ineg>>> | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 25.02 | Overcurrent\DTOC Ineg>>> | outserv | Real | 0 | 1
x074_u002E_023 | Parametersatz 3->UMZ | 074.023 | 0-100:0.01;blockiert=100.02 | s | tIgegen> PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x074_u002E_098 | E;NE;NE | Parameter subset 3;1;1 | 1 | 2 | SE | 100 | Overcurrent\DTOC Ineg> | Tset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Overcurrent\DTOC Ineg> | Tset | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Overcurrent\DTOC Ineg> | Tset | Real | 0 | 9999999 | [7 empty] | Overcurrent\DTOC Ineg> | Tset | Real |  |  | 0 | 100.02
x074_u002E_024 | Parametersatz 3->UMZ | 074.024 | 0-100:0.01;blockiert=100.02 | s | tIgegen>> PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x074_u002E_098 | E;NE;NE | Parameter subset 3;1;1 | 0.5 | 2 | SE | 100 | Overcurrent\DTOC Ineg>> | Tset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Overcurrent\DTOC Ineg>> | Tset | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Overcurrent\DTOC Ineg>> | Tset | Real | 0 | 9999999 | [7 empty] | Overcurrent\DTOC Ineg>> | Tset | Real |  |  | 0 | 100.02
x074_u002E_025 | Parametersatz 3->UMZ | 074.025 | 0-100:0.01;blockiert=100.02 | s | tIgegen>>> PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x074_u002E_098 | E;NE;NE | Parameter subset 3;1;1 | 100.02 | 2 | SE | 100 | Overcurrent\DTOC Ineg>>> | Tset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Overcurrent\DTOC Ineg>>> | Tset | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Overcurrent\DTOC Ineg>>> | Tset | Real | 0 | 9999999 | [7 empty] | Overcurrent\DTOC Ineg>>> | Tset | Real |  |  | 0 | 100.02
x074_u002E_015 | Parametersatz 3->UMZ | 074.015 | 0.002-8:0.001;blockiert=8.002 | Inom | IE> PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x074_u002E_098 | E;NE;NE | Parameter subset 3;1;1 | 0.25 | 3 | SE | 8 | Overcurrent\DTOC IN> | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Overcurrent\DTOC IN> | outserv | Real | E | 1 | 0 | 8.002
[16 empty] | SE | 8 | Overcurrent\DTOC IN> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\DTOC IN> | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 8.002 | Overcurrent\DTOC IN> | outserv | Real | 0 | 1
x074_u002E_016 | Parametersatz 3->UMZ | 074.016 | 0.002-8:0.001;blockiert=8.002 | Inom | IE>> PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x074_u002E_098 | E;NE;NE | Parameter subset 3;1;1 | 8.002 | 3 | SE | 8 | Overcurrent\DTOC IN>> | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Overcurrent\DTOC IN>> | outserv | Real | E | 1 | 0 | 8.002
[16 empty] | SE | 8 | Overcurrent\DTOC IN>> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\DTOC IN>> | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 8.002 | Overcurrent\DTOC IN>> | outserv | Real | 0 | 1
x074_u002E_017 | Parametersatz 3->UMZ | 074.017 | 0.002-8:0.001;blockiert=8.002 | Inom | IE>>> PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x074_u002E_098 | E;NE;NE | Parameter subset 3;1;1 | 8.002 | 4 | SE | 8 | Overcurrent\DTOC IN>>> | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Overcurrent\DTOC IN>>> | outserv | Real | E | 1 | 0 | 8.002
[16 empty] | SE | 8 | Overcurrent\DTOC IN>>> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\DTOC IN>>> | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 8.002 | Overcurrent\DTOC IN>>> | outserv | Real | 0 | 1
[18 empty] | Overcurrent\DTOC IN>>> | idir | Real | 0 | 0
x074_u002E_018 | Parametersatz 3->UMZ | 074.018 | 0.1-40:0.01;blockiert=40.02 | Inom | IE>>>> PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x074_u002E_098 | E;NE;NE | Parameter subset 3;1;1 | 40.02 | 3 | SE | 40 | Overcurrent\DTOC IN>>>> | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Overcurrent\DTOC IN>>>> | outserv | Real | E | 1 | 0 | 40.02
[16 empty] | SE | 40 | Overcurrent\DTOC IN>>>> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\DTOC IN>>>> | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 40.02 | Overcurrent\DTOC IN>>>> | outserv | Real | 0 | 1
x074_u002E_027 | Parametersatz 3->UMZ | 074.027 | 0-100:0.01;blockiert=100.02 | s | tIE> PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x074_u002E_098 | E;NE;NE | Parameter subset 3;1;1 | 1 | 2 | SE | 100 | Overcurrent\DTOC IN> | Tset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Overcurrent\DTOC IN> | Tset | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Overcurrent\DTOC IN> | Tset | Real | 0 | 9999999 | [7 empty] | Overcurrent\DTOC IN> | Tset | Real |  |  | 0 | 100.02
x074_u002E_028 | Parametersatz 3->UMZ | 074.028 | 0-100:0.01;blockiert=100.02 | s | tIE>> PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x074_u002E_098 | E;NE;NE | Parameter subset 3;1;1 | 0.5 | 2 | SE | 100 | Overcurrent\DTOC IN>> | Tset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Overcurrent\DTOC IN>> | Tset | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Overcurrent\DTOC IN>> | Tset | Real | 0 | 9999999 | [7 empty] | Overcurrent\DTOC IN>> | Tset | Real |  |  | 0 | 100.02
x074_u002E_029 | Parametersatz 3->UMZ | 074.029 | 0-100:0.01;blockiert=100.02 | s | tIE>>> PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x074_u002E_098 | E;NE;NE | Parameter subset 3;1;1 | 0.5 | 2 | SE | 100 | Overcurrent\DTOC IN>>> | Tset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Overcurrent\DTOC IN>>> | Tset | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Overcurrent\DTOC IN>>> | Tset | Real | 0 | 9999999 | [7 empty] | Overcurrent\DTOC IN>>> | Tset | Real |  |  | 0 | 100.02
x074_u002E_030 | Parametersatz 3->UMZ | 074.030 | 0-100:0.01;blockiert=100.02 | s | tIE>>>> PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x074_u002E_098 | E;NE;NE | Parameter subset 3;1;1 | 0.5 | 2 | SE | 100 | Overcurrent\DTOC IN>>>> | Tset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Overcurrent\DTOC IN>>>> | Tset | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Overcurrent\DTOC IN>>>> | Tset | Real | 0 | 9999999 | [7 empty] | Overcurrent\DTOC IN>>>> | Tset | Real |  |  | 0 | 100.02
x074_u002E_070 | Parametersatz 3->AMZ_1 | 074.070 | nein¦0;ja¦1 |  | Freigabe PS3 | Enum | Parameter__Funktionsparameter | 1;0 | Real | 1 | x003_u002E_060;x017_u002E_096 | E;NE | Parameter subset 3;1 | 1 | 6 | E | 1 | Overcurrent\IDMT1 P | outserv | Real | 0 | 1 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 3 | Overcurrent\IDMT1 P | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\IDMT1 neg | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\IDMT1 neg | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\IDMT1 N | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\IDMT1 N | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 0 | Overcurrent\IDMT1 P | ModFrame | Real | 0 | 1
[16 empty] | E | 0 | Overcurrent\IDMT1 neg | ModFrame | Real | 0 | 1
[16 empty] | E | 0 | Overcurrent\IDMT1 N | ModFrame | Real | 0 | 1
x074_u002E_050 | Parametersatz 3->AMZ_1 | 074.050 | 0.1-4:0.01;blockiert=4.02 | Inom | IB,L PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x017_u002E_096;x074_u002E_070 | E;NE;NE | Parameter subset 3;1;1 | 4 | 3 | SE | 4 | Overcurrent\IDMT1 P | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Overcurrent\IDMT1 P | outserv | Real | E | 1 | 0 | 4.02
[16 empty] | SE | 4 | Overcurrent\IDMT1 P | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\IDMT1 P | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 4.02 | Overcurrent\IDMT1 P | outserv | Real | 0 | 1
[18 empty] | Overcurrent\IDMT1 KI P | outserv | Real | 0 | 1
x074_u002E_056 | Parametersatz 3->AMZ_1 | 074.056 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Kennlinientyp L PS3 | Enum | Parameter__Funktionsparameter | Definite Time;IEC Standard Inverse;IEC Very Inverse;IEC Extremely Inverse;IEC Long Time Inverse;IEEE Moderately Inverse;IEEE Very Inverse;IEEE Extremely Inverse;ANSI Normally Inverse;ANSI Short Time Inverse;ANSI Long Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | 1 | x003_u002E_060 | E | Parameter subset 3 | Definite Time | 1 |  |  | Overcurrent\IDMT1 P | pcharac | String |  |  | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 1 | Overcurrent\IDMT1 P | pcharac | String
x074_u002E_053 | Parametersatz 3->AMZ_1 | 074.053 | 0.05-10:0.01 |  | Kennl.fakt. kt,L PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 3 | 1 | 2 |  |  | Overcurrent\IDMT1 P | Tpset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 1 | Overcurrent\IDMT1 P | Tpset | Real |  |  | 1 | 0
[18 empty] | Overcurrent\IDMT1 P | Tadder | Real | 0 | 0
x074_u002E_077 | Parametersatz 3->AMZ_1 | 074.077 | 0-10:0.001 | s | min. Auslösez. L PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 3 | 0 | 1 |  |  | Overcurrent\IDMT1 P | minresptime | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 1 | Overcurrent\IDMT1 P | minresptime | Real |  |  | 1 | 0
x074_u002E_059 | Parametersatz 3->AMZ_1 | 074.059 | unverzögert¦0;verzögert gem. Kennl¦1 |  | Rückfallen L PS3 | Enum | Parameter__Funktionsparameter | 0;1 | Real | 3 | x003_u002E_060;x074_u002E_056 | E;SW | Parameter subset 3;IEEE | 0 | 1 |  |  | Overcurrent\IDMT1 P | resetdis | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 1 | Overcurrent\IDMT1 P | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x074_u002E_056 | E;SW | Parameter subset 3;ANSI |  | 1 |  |  | Overcurrent\IDMT1 P | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060;x074_u002E_056 | E | Parameter subset 3 |  | 1 |  |  | Overcurrent\IDMT1 P | resetdis | Real | 0 | 0
x074_u002E_051 | Parametersatz 3->AMZ_1 | 074.051 | 0.01-4:0.01;blockiert=4.02 | Inom | IB,gegen PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x017_u002E_096;x074_u002E_070 | E;NE;NE | Parameter subset 3;1;1 | 1 | 4 | SE | 4 | Overcurrent\IDMT1 neg | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Overcurrent\IDMT1 neg | outserv | Real | E | 1 | 0 | 4.02
[16 empty] | SE | 4 | Overcurrent\IDMT1 neg | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\IDMT1 neg | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 4.02 | Overcurrent\IDMT1 neg | outserv | Real | 0 | 1
[18 empty] | Overcurrent\IDMT1 KI neg | outserv | Real | 0 | 1
x074_u002E_057 | Parametersatz 3->AMZ_1 | 074.057 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Kennl.typ gegen PS3 | Enum | Parameter__Funktionsparameter | Definite Time;IEC Standard Inverse;IEC Very Inverse;IEC Extremely Inverse;IEC Long Time Inverse;IEEE Moderately Inverse;IEEE Very Inverse;IEEE Extremely Inverse;ANSI Normally Inverse;ANSI Short Time Inverse;ANSI Long Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | 1 | x003_u002E_060 | E | Parameter subset 3 | Definite Time | 1 |  |  | Overcurrent\IDMT1 neg | pcharac | String |  |  | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 1 | Overcurrent\IDMT1 neg | pcharac | String
x074_u002E_054 | Parametersatz 3->AMZ_1 | 074.054 | 0.05-10:0.01 |  | Kennl.f. kt,gegn PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 3 | 1 | 2 |  |  | Overcurrent\IDMT1 neg | Tpset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 1 | Overcurrent\IDMT1 neg | Tpset | Real |  |  | 1 | 0
[18 empty] | Overcurrent\IDMT1 neg | Tadder | Real | 0 | 0
x074_u002E_078 | Parametersatz 3->AMZ_1 | 074.078 | 0-10:0.001 | s | min.Auslösez.geg PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 3 | 0 | 1 |  |  | Overcurrent\IDMT1 neg | minresptime | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 1 | Overcurrent\IDMT1 neg | minresptime | Real |  |  | 1 | 0
x074_u002E_060 | Parametersatz 3->AMZ_1 | 074.060 | unverzögert¦0;verzögert gem. Kennl¦1 |  | Rückfallen gegen PS3 | Enum | Parameter__Funktionsparameter | 0;1 | Real | 3 | x003_u002E_060;x074_u002E_057 | E;SW | Parameter subset 3;IEEE | 0 | 1 |  |  | Overcurrent\IDMT1 neg | resetdis | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 1 | Overcurrent\IDMT1 neg | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x074_u002E_057 | E;SW | Parameter subset 3;ANSI |  | 1 |  |  | Overcurrent\IDMT1 neg | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060;x074_u002E_056 | E | Parameter subset 3 |  | 1 |  |  | Overcurrent\IDMT1 neg | resetdis | Real | 0 | 0
x074_u002E_052 | Parametersatz 3->AMZ_1 | 074.052 | 0.01-4:0.01;blockiert=4.02 | Inom | IB,E PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x017_u002E_096;x074_u002E_070 | E;NE;NE | Parameter subset 3;1;1 | 1 | 4 | SE | 4 | Overcurrent\IDMT1 N | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Overcurrent\IDMT1 N | outserv | Real | E | 1 | 0 | 4.02
[16 empty] | SE | 4 | Overcurrent\IDMT1 N | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\IDMT1 N | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 4.02 | Overcurrent\IDMT1 N | outserv | Real | 0 | 1
[18 empty] | Overcurrent\IDMT1 KI N | outserv | Real | 0 | 1
x074_u002E_058 | Parametersatz 3->AMZ_1 | 074.058 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Kennlinientyp E PS3 | Enum | Parameter__Funktionsparameter | Definite Time;IEC Standard Inverse;IEC Very Inverse;IEC Extremely Inverse;IEC Long Time Inverse;IEEE Moderately Inverse;IEEE Very Inverse;IEEE Extremely Inverse;ANSI Normally Inverse;ANSI Short Time Inverse;ANSI Long Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | 1 | x003_u002E_060 | E | Parameter subset 3 | Definite Time | 1 |  |  | Overcurrent\IDMT1 N | pcharac | String |  |  | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 1 | Overcurrent\IDMT1 N | pcharac | String
x074_u002E_055 | Parametersatz 3->AMZ_1 | 074.055 | 0.05-10:0.01 |  | Kennl.f. kt,E PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 3 | 1 | 2 |  |  | Overcurrent\IDMT1 N | Tpset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 1 | Overcurrent\IDMT1 N | Tpset | Real |  |  | 1 | 0
[18 empty] | Overcurrent\IDMT1 N | Tadder | Real | 0 | 0
x074_u002E_079 | Parametersatz 3->AMZ_1 | 074.079 | 0-10:0.001 | s | min. Auslösez.E PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 3 | 0 | 1 |  |  | Overcurrent\IDMT1 N | minresptime | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 1 | Overcurrent\IDMT1 N | minresptime | Real |  |  | 1 | 0
x074_u002E_061 | Parametersatz 3->AMZ_1 | 074.061 | unverzögert¦0;verzögert gem. Kennl¦1 |  | Rückfallen E PS3 | Enum | Parameter__Funktionsparameter | 0;1 | Real | 3 | x003_u002E_060;x074_u002E_058 | E;SW | Parameter subset 3;IEEE | 0 | 1 |  |  | Overcurrent\IDMT1 N | resetdis | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 1 | Overcurrent\IDMT1 N | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x074_u002E_058 | E;SW | Parameter subset 3;ANSI |  | 1 |  |  | Overcurrent\IDMT1 N | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060;x074_u002E_056 | E | Parameter subset 3 |  | 1 |  |  | Overcurrent\IDMT1 N | resetdis | Real | 0 | 0
x076_u002E_044 | Parametersatz 3->AMZ_2 | 076.044 | nein¦0;ja¦1 |  | Freigabe PS3 | Enum | Parameter__Funktionsparameter | 1;0 | Real | 1 | x003_u002E_060;x017_u002E_052 | E;NE | Parameter subset 3;1 | 1 | 6 | E | 1 | Overcurrent\IDMT2 P | outserv | Real | 0 | 1 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 3 | Overcurrent\IDMT2 P | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\IDMT2 neg | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\IDMT2 neg | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\IDMT2 N | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\IDMT2 N | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 0 | Overcurrent\IDMT2 P | ModFrame | Real | 0 | 1
[16 empty] | E | 0 | Overcurrent\IDMT2 neg | ModFrame | Real | 0 | 1
[16 empty] | E | 0 | Overcurrent\IDMT2 N | ModFrame | Real | 0 | 1
x076_u002E_238 | Parametersatz 3->AMZ_2 | 076.238 | 0.1-4:0.01;blockiert=4.02 | Inom | IB,L PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x017_u002E_052;x076_u002E_044 | E;NE;NE | Parameter subset 3;1;1 | 1 | 3 | SE | 4 | Overcurrent\IDMT2 P | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Overcurrent\IDMT2 P | outserv | Real | E | 1 | 0 | 4.02
[16 empty] | SE | 4 | Overcurrent\IDMT2 P | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\IDMT2 P | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 4.02 | Overcurrent\IDMT2 P | outserv | Real | 0 | 1
x071_u002E_006 | Parametersatz 3->AMZ_2 | 071.006 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Kennlinientyp L PS3 | Enum | Parameter__Funktionsparameter | Definite Time;IEC Standard Inverse;IEC Very Inverse;IEC Extremely Inverse;IEC Long Time Inverse;IEEE Moderately Inverse;IEEE Very Inverse;IEEE Extremely Inverse;ANSI Normally Inverse;ANSI Short Time Inverse;ANSI Long Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | 1 | x003_u002E_060 | E | Parameter subset 3 | Definite Time | 1 |  |  | Overcurrent\IDMT2 P | pcharac | String |  |  | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 1 | Overcurrent\IDMT2 P | pcharac | String
x078_u002E_252 | Parametersatz 3->AMZ_2 | 078.252 | 0.05-10:0.01 |  | Kennl.fakt. kt,L PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 3 | 1 | 1 |  |  | Overcurrent\IDMT2 P | Tpset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 1 | Overcurrent\IDMT2 P | Tpset | Real |  |  | 1 | 0
x071_u002E_046 | Parametersatz 3->AMZ_2 | 071.046 | 0-10:0.001 | s | min. Auslösez. L PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 3 | 0 | 1 |  |  | Overcurrent\IDMT2 P | minresptime | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 1 | Overcurrent\IDMT2 P | minresptime | Real |  |  | 1 | 0
x071_u002E_018 | Parametersatz 3->AMZ_2 | 071.018 | unverzögert¦0;verzögert gem. Kennl¦1 |  | Rückfallen L PS3 | Enum | Parameter__Funktionsparameter | 0;1 | Real | 3 | x003_u002E_060;x071_u002E_006 | E;SW | Parameter subset 3;IEEE | 0 | 1 |  |  | Overcurrent\IDMT2 P | resetdis | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 1 | Overcurrent\IDMT2 P | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x071_u002E_006 | E;SW | Parameter subset 3;ANSI |  | 1 |  |  | Overcurrent\IDMT2 P | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | Parameter subset 3 |  | 1 |  |  | Overcurrent\IDMT2 P | resetdis | Real | 0 | 0
x076_u002E_252 | Parametersatz 3->AMZ_2 | 076.252 | 0.01-4:0.01;blockiert=4.02 | Inom | IB,gegen PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x017_u002E_052;x076_u002E_044 | E;NE;NE | Parameter subset 3;1;1 | 1 | 3 | SE | 4 | Overcurrent\IDMT2 neg | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Overcurrent\IDMT2 neg | outserv | Real | E | 1 | 0 | 4.02
[16 empty] | SE | 4 | Overcurrent\IDMT2 neg | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\IDMT2 neg | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 4.02 | Overcurrent\IDMT2 neg | outserv | Real | 0 | 1
x071_u002E_010 | Parametersatz 3->AMZ_2 | 071.010 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Kennl.typ gegen PS3 | Enum | Parameter__Funktionsparameter | Definite Time;IEC Standard Inverse;IEC Very Inverse;IEC Extremely Inverse;IEC Long Time Inverse;IEEE Moderately Inverse;IEEE Very Inverse;IEEE Extremely Inverse;ANSI Normally Inverse;ANSI Short Time Inverse;ANSI Long Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | 1 | x003_u002E_060 | E | Parameter subset 3 | Definite Time | 1 |  |  | Overcurrent\IDMT2 neg | pcharac | String |  |  | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 1 | Overcurrent\IDMT2 neg | pcharac | String
x079_u002E_252 | Parametersatz 3->AMZ_2 | 079.252 | 0.05-10:0.01 |  | Kennl.f. kt,gegn PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 3 | 1 | 1 |  |  | Overcurrent\IDMT2 neg | Tpset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 1 | Overcurrent\IDMT2 neg | Tpset | Real |  |  | 1 | 0
x071_u002E_050 | Parametersatz 3->AMZ_2 | 071.050 | 0-10:0.001 | s | min.Auslösez.geg PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 3 | 0 | 1 |  |  | Overcurrent\IDMT2 neg | minresptime | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 1 | Overcurrent\IDMT2 neg | minresptime | Real |  |  | 1 | 0
x071_u002E_022 | Parametersatz 3->AMZ_2 | 071.022 | unverzögert¦0;verzögert gem. Kennl¦1 |  | Rückfallen gegen PS3 | Enum | Parameter__Funktionsparameter | 0;1 | Real | 3 | x003_u002E_060;x071_u002E_010 | E;SW | Parameter subset 3;IEEE | 0 | 1 |  |  | Overcurrent\IDMT2 neg | resetdis | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 1 | Overcurrent\IDMT2 neg | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x071_u002E_010 | E;SW | Parameter subset 3;ANSI |  | 1 |  |  | Overcurrent\IDMT2 neg | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | Parameter subset 3 |  | 1 |  |  | Overcurrent\IDMT2 neg | resetdis | Real | 0 | 0
x077_u002E_252 | Parametersatz 3->AMZ_2 | 077.252 | 0.01-4:0.01;blockiert=4.02 | Inom | IB,E PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x017_u002E_052;x076_u002E_044 | E;NE;NE | Parameter subset 3;1;1 | 1 | 3 | SE | 4 | Overcurrent\IDMT2 N | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Overcurrent\IDMT2 N | outserv | Real | E | 1 | 0 | 4.02
[16 empty] | SE | 4 | Overcurrent\IDMT2 N | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\IDMT2 N | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 4.02 | Overcurrent\IDMT2 N | outserv | Real | 0 | 1
x071_u002E_014 | Parametersatz 3->AMZ_2 | 071.014 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Kennlinientyp E PS3 | Enum | Parameter__Funktionsparameter | Definite Time;IEC Standard Inverse;IEC Very Inverse;IEC Extremely Inverse;IEC Long Time Inverse;IEEE Moderately Inverse;IEEE Very Inverse;IEEE Extremely Inverse;ANSI Normally Inverse;ANSI Short Time Inverse;ANSI Long Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | 1 | x003_u002E_060 | E | Parameter subset 3 | Definite Time | 1 |  |  | Overcurrent\IDMT2 N | pcharac | String |  |  | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 1 | Overcurrent\IDMT2 N | pcharac | String
x071_u002E_002 | Parametersatz 3->AMZ_2 | 071.002 | 0.05-10:0.01 |  | Kennl.f. kt,E PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 3 | 1 | 1 |  |  | Overcurrent\IDMT2 N | Tpset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 1 | Overcurrent\IDMT2 N | Tpset | Real |  |  | 1 | 0
x071_u002E_054 | Parametersatz 3->AMZ_2 | 071.054 | 0-10:0.001 | s | min. Auslösez.E PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 3 | 0 | 1 |  |  | Overcurrent\IDMT2 N | minresptime | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 1 | Overcurrent\IDMT2 N | minresptime | Real |  |  | 1 | 0
x071_u002E_026 | Parametersatz 3->AMZ_2 | 071.026 | unverzögert¦0;verzögert gem. Kennl¦1 |  | Rückfallen E PS3 | Enum | Parameter__Funktionsparameter | 0;1 | Real | 3 | x003_u002E_060;x071_u002E_014 | E;SW | Parameter subset 3;IEEE | 0 | 1 |  |  | Overcurrent\IDMT2 N | resetdis | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 1 | Overcurrent\IDMT2 N | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x071_u002E_014 | E;SW | Parameter subset 3;ANSI |  | 1 |  |  | Overcurrent\IDMT2 N | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | Parameter subset 3 |  | 1 |  |  | Overcurrent\IDMT2 N | resetdis | Real | 0 | 0
x078_u002E_235 | Parametersatz 3->KURI | 078.235 | nein¦0;ja¦1 |  | Freigabe PS3 | Enum | Parameter__Funktionsparameter | 1;0 | Real | 1 | x003_u002E_060;x017_u002E_070 | E;NE | Parameter subset 3;1 | 1 | 2 |  |  | Overcurrent\Directional P | outserv | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Overcurrent\Directional P | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\Directional N | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\Directional N | outserv | Real | E | 0 | 0 | 0
x078_u002E_237 | Parametersatz 3->KURI | 078.237 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung tI> PS3 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real | 1 | x003_u002E_060;x017_u002E_070;x078_u002E_235 | E;NE;NE | Parameter subset 3;1;1 | 1 | 1 |  |  | Overcurrent\DTOC I> | idir | Real | 1 | 0 | 1 | Overcurrent\Directional P;x003_u002E_060 | outserv | Real | E;E | 0;Parameter subset 3 | 1 | Overcurrent\DTOC I> | idir | Real |  |  | 1 | 0
x078_u002E_238 | Parametersatz 3->KURI | 078.238 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung tI>> PS3 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real | 1 | x003_u002E_060;x017_u002E_070;x078_u002E_235 | E;NE;NE | Parameter subset 3;1;1 | 1 | 1 |  |  | Overcurrent\DTOC I>> | idir | Real | 1 | 0 | 1 | Overcurrent\Directional P;x003_u002E_060 | outserv | Real | E;E | 0;Parameter subset 3 | 1 | Overcurrent\DTOC I>> | idir | Real |  |  | 1 | 0
x078_u002E_240 | Parametersatz 3->KURI | 078.240 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung tIE> PS3 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real | 1 | x003_u002E_060;x017_u002E_070;x078_u002E_235 | E;NE;NE | Parameter subset 3;1;1 | 1 | 1 |  |  | Overcurrent\DTOC IN> | idir | Real | 1 | 0 | 1 | Overcurrent\Directional N;x003_u002E_060 | outserv | Real | E;E | 0;Parameter subset 3 | 1 | Overcurrent\DTOC IN> | idir | Real |  |  | 1 | 0
x078_u002E_241 | Parametersatz 3->KURI | 078.241 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung tIE>> PS3 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real | 1 | x003_u002E_060;x017_u002E_070;x078_u002E_235 | E;NE;NE | Parameter subset 3;1;1 | 1 | 1 |  |  | Overcurrent\DTOC IN>> | idir | Real | 1 | 0 | 1 | Overcurrent\Directional N;x003_u002E_060 | outserv | Real | E;E | 0;Parameter subset 3 | 1 | Overcurrent\DTOC IN>> | idir | Real |  |  | 1 | 0
x078_u002E_239 | Parametersatz 3->KURI | 078.239 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung tIB,L> PS3 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real | 1 | x003_u002E_060;x017_u002E_070;x078_u002E_235 | E;NE;NE | Parameter subset 3;1;1 | 1 | 1 |  |  | Overcurrent\IDMT1 P | idir | Real | 1 | 0 | 1 | Overcurrent\Directional P;x003_u002E_060 | outserv | Real | E;E | 0;Parameter subset 3 | 1 | Overcurrent\IDMT1 P | idir | Real |  |  | 1 | 0
x078_u002E_242 | Parametersatz 3->KURI | 078.242 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung tIB,E> PS3 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real | 1 | x003_u002E_060;x017_u002E_070;x078_u002E_235 | E;NE;NE | Parameter subset 3;1;1 | 1 | 1 |  |  | Overcurrent\IDMT1 N | idir | Real | 1 | 0 | 1 | Overcurrent\Directional N;x003_u002E_060 | outserv | Real | E;E | 0;Parameter subset 3 | 1 | Overcurrent\IDMT1 N | idir | Real |  |  | 1 | 0
x078_u002E_243 | Parametersatz 3->KURI | 078.243 | -90-90:0.1 | ° | charakt.Winkel E PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 3 | -45 | 1 |  |  | Overcurrent\Directional N | mtau | Real | 1 | 0 | 1 | Overcurrent\Directional N;x003_u002E_060 | outserv | Real | E;E | 0;Parameter subset 3 | 1 | Overcurrent\Directional N | mtau | Real |  |  | 1 | 0
x078_u002E_244 | Parametersatz 3->KURI | 078.244 | 0.015-0.6:0.001 | Unom(/©3) | UNE> PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 3 | 0.1 | 1 |  |  | Overcurrent\Directional N | upolur | Real | 1 | 0 | 1 | Overcurrent\Directional N;x003_u002E_060 | outserv | Real | E;E | 0;Parameter subset 3 | 1 | Overcurrent\Directional N | upolur | Real |  |  | 1 | 0
x078_u002E_246 | Parametersatz 3->U<> | 078.246 | nein¦0;ja¦1 |  | Freigabe PS3 | Enum | Parameter__Funktionsparameter | 1;0 | Real | 1 | x003_u002E_060;x023_u002E_030 | E;NE | Parameter subset 3;1 | 1 | 1 |  |  | Voltage | outserv | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 1 | Voltage | outserv | Real | E | 0 | 0 | 0
x078_u002E_001 | Parametersatz 3->U<> | 078.001 | Dreieck¦0;Stern¦1 |  | Betriebsart PS3 | Enum | Parameter__Funktionsparameter | Delta;Star | String | 1 | x003_u002E_060 | E | Parameter subset 3 | Delta | 8 | E | Star | Voltage\V> | outserv | Real | 0 | 1
[16 empty] | E | Star | Voltage\V>> | outserv | Real | 0 | 1
[16 empty] | E | Star | Voltage\V< | outserv | Real | 0 | 1
[16 empty] | E | Star | Voltage\V<< | outserv | Real | 0 | 1
[16 empty] | E | Star | Voltage\VNG> | outserv | Real | 0 | 1
[16 empty] | E | Star | Voltage\VNG>> | outserv | Real | 0 | 1
x078_u002E_003 | Parametersatz 3->U<> | 078.003 | 0.2-1.5:0.01;blockiert=1.52 | Unom(/©3) | U> PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x078_u002E_001 | E;E | Parameter subset 3;Delta | 1.1 | 3 | SE | 1.5 | Voltage\V> | Uset | Real | 1 | 0 | 1 | x003_u002E_060;x078_u002E_001 |  |  | E;E | Parameter subset 3;Delta | 2 | Voltage\V> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V> | outserv | Real | 0 | 0 | [7 empty] | Voltage\V> | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.52 | Voltage\V> | outserv | Real | 0 | 1
x078_u002E_004 | Parametersatz 3->U<> | 078.004 | 0.2-1.5:0.01;blockiert=1.52 | Unom(/©3) | U>> PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x078_u002E_001 | E;E | Parameter subset 3;Delta | 1.1 | 3 | SE | 1.5 | Voltage\V>> | Uset | Real | 1 | 0 | 1 | x003_u002E_060;x078_u002E_001 |  |  | E;E | Parameter subset 3;Delta | 2 | Voltage\V>> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\V>> | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.52 | Voltage\V>> | outserv | Real | 0 | 1
x078_u002E_005 | Parametersatz 3->U<> | 078.005 | 0-100:0.01;blockiert=100.02 | s | tU> PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 3 | 1 | 2 | SE | 100 | Voltage\V> | Tdel | Real | 1 | 0 | 1 | x003_u002E_060;x078_u002E_001 |  |  | E;E | Parameter subset 3;Delta | 2 | Voltage\V> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\V> | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\V> | Tdel | Real |  |  | 0 | 100.02
x078_u002E_006 | Parametersatz 3->U<> | 078.006 | 0-100:0.01;blockiert=100.02 | s | tU>> PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 3 | 1 | 2 | SE | 100 | Voltage\V>> | Tdel | Real | 1 | 0 | 1 | x003_u002E_060;x078_u002E_001 |  |  | E;E | Parameter subset 3;Delta | 2 | Voltage\V>> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\V>> | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\V>> | Tdel | Real |  |  | 0 | 100.02
x078_u002E_027 | Parametersatz 3->U<> | 078.027 | 0-100:0.01;blockiert=100.02 | s | tU> 3p PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 3 | 1 | 2 | SE | 100 | Voltage\tV> 3-pole | Tdelay | Real | 1 | 0 | 1 | x003_u002E_060;x078_u002E_001 |  |  | E;E | Parameter subset 3;Delta | 2 | Voltage\tV> 3-pole | Tdelay | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\tV> 3-pole | Tdelay | Real | 0 | 9999999 | [7 empty] | Voltage\tV> 3-pole | Tdelay | Real |  |  | 0 | 100.02
x078_u002E_007 | Parametersatz 3->U<> | 078.007 | 0.2-1.5:0.01;blockiert=1.52 | Unom(/©3) | U< PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x078_u002E_001 | E;E | Parameter subset 3;Delta | 0.8 | 3 | SE | 1.5 | Voltage\V< | Uset | Real | 1 | 0 | 1 | x003_u002E_060;x078_u002E_001 |  |  | E;E | Parameter subset 3;Delta | 2 | Voltage\V< | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V< | outserv | Real | 0 | 0 | [7 empty] | Voltage\V< | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.52 | Voltage\V< | outserv | Real | 0 | 1
x078_u002E_008 | Parametersatz 3->U<> | 078.008 | 0.2-1.5:0.01;blockiert=1.52 | Unom(/©3) | U<< PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x078_u002E_001 | E;E | Parameter subset 3;Delta | 0.8 | 3 | SE | 1.5 | Voltage\V<< | Uset | Real | 1 | 0 | 1 | x003_u002E_060;x078_u002E_001 |  |  | E;E | Parameter subset 3;Delta | 2 | Voltage\V<< | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V<< | outserv | Real | 0 | 0 | [7 empty] | Voltage\V<< | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.52 | Voltage\V<< | outserv | Real | 0 | 1
x078_u002E_009 | Parametersatz 3->U<> | 078.009 | 0-100:0.01;blockiert=100.02 | s | tU< PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 3 | 1 | 2 | SE | 100 | Voltage\V< | Tdel | Real | 1 | 0 | 1 | x003_u002E_060;x078_u002E_001 |  |  | E;E | Parameter subset 3;Delta | 2 | Voltage\V< | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\V< | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\V< | Tdel | Real |  |  | 0 | 100.02
x078_u002E_010 | Parametersatz 3->U<> | 078.010 | 0-100:0.01;blockiert=100.02 | s | tU<< PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 3 | 1 | 2 | SE | 100 | Voltage\V<< | Tdel | Real | 1 | 0 | 1 | x003_u002E_060;x078_u002E_001 |  |  | E;E | Parameter subset 3;Delta | 2 | Voltage\V<< | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\V<< | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\V<< | Tdel | Real |  |  | 0 | 100.02
x078_u002E_028 | Parametersatz 3->U<> | 078.028 | 0-100:0.01;blockiert=100.02 | s | tU< 3p PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 3 | 1 | 2 | SE | 100 | Voltage\tV< 3-pole | Tdelay | Real | 1 | 0 | 1 | x003_u002E_060;x078_u002E_001 |  |  | E;E | Parameter subset 3;Delta | 2 | Voltage\tV< 3-pole | Tdelay | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\tV< 3-pole | Tdelay | Real | 0 | 9999999 | [7 empty] | Voltage\tV< 3-pole | Tdelay | Real |  |  | 0 | 100.02
x078_u002E_015 | Parametersatz 3->U<> | 078.015 | 0.2-1.5:0.01;blockiert=1.52 | Unom/©3 | Umit> PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 3 | 1.1 | 3 | SE | 1.5 | Voltage\Vpos> | Uset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Voltage\Vpos> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos> | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.52 | Voltage\Vpos> | outserv | Real | 0 | 1
x078_u002E_016 | Parametersatz 3->U<> | 078.016 | 0.2-1.5:0.01;blockiert=1.52 | Unom/©3 | Umit>> PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 3 | 1.1 | 3 | SE | 1.5 | Voltage\Vpos>> | Uset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Voltage\Vpos>> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos>> | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.52 | Voltage\Vpos>> | outserv | Real | 0 | 1
x078_u002E_017 | Parametersatz 3->U<> | 078.017 | 0-100:0.01;blockiert=100.02 | s | tUmit> PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 3 | 1 | 2 | SE | 100 | Voltage\Vpos> | Tdel | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Voltage\Vpos> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\Vpos> | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\Vpos> | Tdel | Real |  |  | 0 | 100.02
x078_u002E_018 | Parametersatz 3->U<> | 078.018 | 0-100:0.01;blockiert=100.02 | s | tUmit>> PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 3 | 1 | 2 | SE | 100 | Voltage\Vpos>> | Tdel | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Voltage\Vpos>> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\Vpos>> | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\Vpos>> | Tdel | Real |  |  | 0 | 100.02
x078_u002E_019 | Parametersatz 3->U<> | 078.019 | 0.2-1.5:0.01;blockiert=1.52 | Unom/©3 | Umit< PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 3 | 0.8 | 3 | SE | 1.5 | Voltage\Vpos< | Uset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Voltage\Vpos< | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos< | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos< | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.52 | Voltage\Vpos< | outserv | Real | 0 | 1
x078_u002E_020 | Parametersatz 3->U<> | 078.020 | 0.2-1.5:0.01;blockiert=1.52 | Unom/©3 | Umit<< PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 3 | 0.8 | 3 | SE | 1.5 | Voltage\Vpos<< | Uset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Voltage\Vpos<< | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos<< | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos<< | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.52 | Voltage\Vpos<< | outserv | Real | 0 | 1
x078_u002E_021 | Parametersatz 3->U<> | 078.021 | 0-100:0.01;blockiert=100.02 | s | tUmit< PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 3 | 1 | 2 | SE | 100 | Voltage\Vpos< | Tdel | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Voltage\Vpos< | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\Vpos< | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\Vpos< | Tdel | Real |  |  | 0 | 100.02
x078_u002E_022 | Parametersatz 3->U<> | 078.022 | 0-100:0.01;blockiert=100.02 | s | tUmit<< PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 3 | 1 | 2 | SE | 100 | Voltage\Vpos<< | Tdel | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Voltage\Vpos<< | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\Vpos<< | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\Vpos<< | Tdel | Real |  |  | 0 | 100.02
x078_u002E_023 | Parametersatz 3->U<> | 078.023 | 0.02-1.5:0.01;blockiert=1.52 | Unom/©3 | Ugegen> PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 3 | 1.52 | 3 | SE | 1.5 | Voltage\Vneg> | Uset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Voltage\Vneg> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vneg> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vneg> | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.52 | Voltage\Vneg> | outserv | Real | 0 | 1
x078_u002E_024 | Parametersatz 3->U<> | 078.024 | 0.02-1.5:0.01;blockiert=1.52 | Unom/©3 | Ugegen>> PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 3 | 1.52 | 3 | SE | 1.5 | Voltage\Vneg>> | Uset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Voltage\Vneg>> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vneg>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vneg>> | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.52 | Voltage\Vneg>> | outserv | Real | 0 | 1
x078_u002E_025 | Parametersatz 3->U<> | 078.025 | 0-100:0.01;blockiert=100.02 | s | tUgegen> PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 3 | 1 | 2 | SE | 100 | Voltage\Vneg> | Tdel | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Voltage\Vneg> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\Vneg> | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\Vneg> | Tdel | Real |  |  | 0 | 100.02
x078_u002E_026 | Parametersatz 3->U<> | 078.026 | 0-100:0.01;blockiert=100.02 | s | tUgegen>> PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 3 | 1 | 2 | SE | 100 | Voltage\Vneg>> | Tdel | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Voltage\Vneg>> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\Vneg>> | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\Vneg>> | Tdel | Real |  |  | 0 | 100.02
x078_u002E_011 | Parametersatz 3->U<> | 078.011 | 0.02-1:0.01;blockiert=1.02 | Unom(/©3) | UNE> PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x078_u002E_001 | E;E | Parameter subset 3;Delta | 1.02 | 3 | SE | 1 | Voltage\VNG> | Uset | Real | 1 | 0 | 1 | x003_u002E_060;x078_u002E_001 |  |  | E;E | Parameter subset 3;Delta | 2 | Voltage\VNG> | outserv | Real | E | 1 | 0 | 1.02
[16 empty] | SE | 1 | Voltage\VNG> | outserv | Real | 0 | 0 | [7 empty] | Voltage\VNG> | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.02 | Voltage\VNG> | outserv | Real | 0 | 1
x078_u002E_012 | Parametersatz 3->U<> | 078.012 | 0.02-1:0.01;blockiert=1.02 | Unom(/©3) | UNE>> PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x078_u002E_001 | E;E | Parameter subset 3;Delta | 1.02 | 3 | SE | 1 | Voltage\VNG>> | Uset | Real | 1 | 0 | 1 | x003_u002E_060;x078_u002E_001 |  |  | E;E | Parameter subset 3;Delta | 2 | Voltage\VNG>> | outserv | Real | E | 1 | 0 | 1.02
[16 empty] | SE | 1 | Voltage\VNG>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\VNG>> | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.02 | Voltage\VNG>> | outserv | Real | 0 | 1
x078_u002E_013 | Parametersatz 3->U<> | 078.013 | 0-100:0.01;blockiert=100.02 | s | tUNE> PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 3 | 1 | 2 | SE | 100 | Voltage\VNG> | Tdel | Real | 1 | 0 | 1 | x003_u002E_060;x078_u002E_001 |  |  | E;E | Parameter subset 3;Delta | 2 | Voltage\VNG> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\VNG> | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\VNG> | Tdel | Real |  |  | 0 | 100.02
x078_u002E_014 | Parametersatz 3->U<> | 078.014 | 0-100:0.01;blockiert=100.02 | s | tUNE>> PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 3 | 1 | 2 | SE | 100 | Voltage\VNG>> | Tdel | Real | 1 | 0 | 1 | x003_u002E_060;x078_u002E_001 |  |  | E;E | Parameter subset 3;Delta | 2 | Voltage\VNG>> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\VNG>> | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\VNG>> | Tdel | Real |  |  | 0 | 100.02
x001_u002E_164 | Parametersatz 3->U<> | 001.164 | ohne¦0;mit¦1 |  | Btr.art U< Überw PS3 | Enum | Parameter__Funktionsparameter | 1;0 | Real | 1 | x003_u002E_060 | E | Parameter subset 3 | 1 | 1 |  |  | Voltage\Imin | outserv | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 1 | Voltage\Imin | outserv | Real |  |  | 1 | 0
x001_u002E_160 | Parametersatz 3->U<> | 001.160 | 0.04-1:0.01 | Inom | I-Freigabe U< PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 3 | 0.1 | 1 |  |  | Voltage\Imin | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 1 | Voltage\Imin | Ipset | Real |  |  | 1 | 0
x018_u002E_198 | Parametersatz 3->f<> | 018.198 | nein¦0;ja¦1 |  | Freigabe PS3 | Enum | Parameter__Funktionsparameter | 1;0 | Real | 1 | x003_u002E_060;x023_u002E_031 | E;NE | Parameter subset 3;1 | 1 | 1 |  |  | Frequency | outserv | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 1 | Frequency | outserv | Real | E | 0 | 0 | 0
x018_u002E_122 | Parametersatz 3->f<> | 018.122 | f¦0;f mit df/dt¦1;f m. Delta f/Delta t¦2 |  | Betriebsart f1 PS3 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real | 1 | x003_u002E_060 | E | Parameter subset 3 | 0 | 1 | E | 0 | Frequency\df1/dt | outserv | Real | 0 | 1 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 3 | Frequency\f1 | outserv | Real | E | 1 | 0 | 0
[30 empty] | Frequency\df1/dt | outserv | Real | E | 1 | 0 | 0
[30 empty] | Frequency\df1/dt | outserv | Real |  |  | 0 | 1
x018_u002E_102 | Parametersatz 3->f<> | 018.102 | 40-70:0.01;blockiert=70.02 | Hz | f1 PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 3 | 49.8 | 3 | SE | 70 | Frequency\f1 | Fset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Frequency\f1 | outserv | Real | E | 1 | 0 | 70.02
[16 empty] | SE | 70 | Frequency\f1 | outserv | Real | 0 | 0 | [7 empty] | Frequency\f1 | Fset | Real |  |  | 1 | 0
[16 empty] | GE | 70.02 | Frequency\f1 | outserv | Real | 0 | 1
x018_u002E_106 | Parametersatz 3->f<> | 018.106 | 0-10:0.001;blockiert=10.002 | s | tf1 PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 3 | 0 | 4 | SE | 10 | Frequency\f1 | Tdel | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 4 | Frequency\f1 | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | GE | 10.002 | Frequency\f1 | Tdel | Real | 0 | 9999999 | [7 empty] | Frequency\f1 | Tdel | Real |  |  | 0 | 10.002
[16 empty] | SE | 10 | Frequency\df1/dt | Tdel | Real | 1 | 0 | [7 empty] | Frequency\df1/dt | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | GE | 10.002 | Frequency\df1/dt | Tdel | Real | 0 | 9999999 | [7 empty] | Frequency\df1/dt | Tdel | Real |  |  | 0 | 10.002
x018_u002E_110 | Parametersatz 3->f<> | 018.110 | 0.1-10:0.001;blockiert=10.002 | Hz/s | df1/dt PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x018_u002E_122 | E;E | Parameter subset 3;1 | 2 | 3 | SE | 10 | Frequency\df1/dt | dFset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Frequency\df1/dt | outserv | Real | E | 1 | 0 | 10.002
[16 empty] | SE | 10 | Frequency\df1/dt | outserv | Real | 0 | 0 | [7 empty] | Frequency\df1/dt | dFset | Real |  |  | 1 | 0
[16 empty] | GE | 10.002 | Frequency\df1/dt | outserv | Real | 0 | 1
x018_u002E_146 | Parametersatz 3->f<> | 018.146 | f¦0;f mit df/dt¦1;f m. Delta f/Delta t¦2 |  | Betriebsart f2 PS3 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real | 1 | x003_u002E_060 | E | Parameter subset 3 | 0 | 1 | E | 0 | Frequency\df2/dt | outserv | Real | 0 | 1 |  | x003_u002E_060 |  |  | E | Parameter subset 3 | 3 | Frequency\f2 | outserv | Real | E | 1 | 0 | 0
[30 empty] | Frequency\df2/dt | outserv | Real | E | 1 | 0 | 0
[30 empty] | Frequency\df2/dt | outserv | Real |  |  | 0 | 1
x018_u002E_126 | Parametersatz 3->f<> | 018.126 | 40-70:0.01;blockiert=70.02 | Hz | f2 PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 3 | 49.8 | 3 | SE | 70 | Frequency\f2 | Fset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Frequency\f2 | outserv | Real | E | 1 | 0 | 70.02
[16 empty] | SE | 70 | Frequency\f2 | outserv | Real | 0 | 0 | [7 empty] | Frequency\f2 | Fset | Real |  |  | 1 | 0
[16 empty] | GE | 70.02 | Frequency\f2 | outserv | Real | 0 | 1
x018_u002E_130 | Parametersatz 3->f<> | 018.130 | 0-10:0.001;blockiert=10.002 | s | tf2 PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 3 | 0 | 4 | SE | 10 | Frequency\f2 | Tdel | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 4 | Frequency\f2 | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | GE | 10.002 | Frequency\f2 | Tdel | Real | 0 | 9999999 | [7 empty] | Frequency\f2 | Tdel | Real |  |  | 0 | 10.002
[16 empty] | SE | 10 | Frequency\df2/dt | Tdel | Real | 1 | 0 | [7 empty] | Frequency\df2/dt | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | GE | 10.002 | Frequency\df2/dt | Tdel | Real | 0 | 9999999 | [7 empty] | Frequency\df2/dt | Tdel | Real |  |  | 0 | 10.002
x018_u002E_134 | Parametersatz 3->f<> | 018.134 | 0.1-10:0.001;blockiert=10.002 | Hz/s | df2/dt PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x018_u002E_146 | E;E | Parameter subset 3;1 | 2 | 3 | SE | 10 | Frequency\df2/dt | dFset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Frequency\df2/dt | outserv | Real | E | 1 | 0 | 10.002
[16 empty] | SE | 10 | Frequency\df2/dt | outserv | Real | 0 | 0 | [7 empty] | Frequency\df2/dt | dFset | Real |  |  | 1 | 0
[16 empty] | GE | 10.002 | Frequency\df2/dt | outserv | Real | 0 | 1
x018_u002E_170 | Parametersatz 3->f<> | 018.170 | f¦0;f mit df/dt¦1;f m. Delta f/Delta t¦2 |  | Betriebsart f3 PS3 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real | 1 | x003_u002E_060 | E | Parameter subset 3 | 0 | 1 | E | 0 | Frequency\df3/dt | outserv | Real | 0 | 1 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Frequency\f3 | outserv | Real | E | 1 | 0 | 0
[30 empty] | Frequency\df3/dt | outserv | Real | E | 1 | 0 | 0
[30 empty] | Frequency\df3/dt | outserv | Real |  |  | 0 | 1
x018_u002E_150 | Parametersatz 3->f<> | 018.150 | 40-70:0.01;blockiert=70.02 | Hz | f3 PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 3 | 49.8 | 3 | SE | 70 | Frequency\f3 | Fset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Frequency\f3 | outserv | Real | E | 1 | 0 | 70.02
[16 empty] | SE | 70 | Frequency\f3 | outserv | Real | 0 | 0 | [7 empty] | Frequency\f3 | Fset | Real |  |  | 1 | 0
[16 empty] | GE | 70.02 | Frequency\f3 | outserv | Real | 0 | 1
x018_u002E_154 | Parametersatz 3->f<> | 018.154 | 0-10:0.001;blockiert=10.002 | s | tf3 PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 3 | 0 | 4 | SE | 10 | Frequency\f3 | Tdel | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 4 | Frequency\f3 | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | GE | 10.002 | Frequency\f3 | Tdel | Real | 0 | 9999999 | [7 empty] | Frequency\f3 | Tdel | Real |  |  | 0 | 10.002
[16 empty] | SE | 10 | Frequency\df3/dt | Tdel | Real | 1 | 0 | [7 empty] | Frequency\df3/dt | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | GE | 10.002 | Frequency\df3/dt | Tdel | Real | 0 | 9999999 | [7 empty] | Frequency\df3/dt | Tdel | Real |  |  | 0 | 10.002
x018_u002E_158 | Parametersatz 3->f<> | 018.158 | 0.1-10:0.001;blockiert=10.002 | Hz/s | df3/dt PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x018_u002E_170 | E;E | Parameter subset 3;1 | 2 | 3 | SE | 10 | Frequency\df3/dt | dFset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Frequency\df3/dt | outserv | Real | E | 1 | 0 | 10.002
[16 empty] | SE | 10 | Frequency\df3/dt | outserv | Real | 0 | 0 | [7 empty] | Frequency\df3/dt | dFset | Real |  |  | 1 | 0
[16 empty] | GE | 10.002 | Frequency\df3/dt | outserv | Real | 0 | 1
x018_u002E_194 | Parametersatz 3->f<> | 018.194 | f¦0;f mit df/dt¦1;f m. Delta f/Delta t¦2 |  | Betriebsart f4 PS3 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real | 1 | x003_u002E_060 | E | Parameter subset 3 | 0 | 1 | E | 0 | Frequency\df4/dt | outserv | Real | 0 | 1 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Frequency\f4 | outserv | Real | E | 1 | 0 | 0
[30 empty] | Frequency\df4/dt | outserv | Real | E | 1 | 0 | 0
[30 empty] | Frequency\df4/dt | outserv | Real |  |  | 0 | 1
x018_u002E_174 | Parametersatz 3->f<> | 018.174 | 40-70:0.01;blockiert=70.02 | Hz | f4 PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 3 | 49.8 | 3 | SE | 70 | Frequency\f4 | Fset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Frequency\f4 | outserv | Real | E | 1 | 0 | 70.02
[16 empty] | SE | 70 | Frequency\f4 | outserv | Real | 0 | 0 | [7 empty] | Frequency\f4 | Fset | Real |  |  | 1 | 0
[16 empty] | GE | 70.02 | Frequency\f4 | outserv | Real | 0 | 1
x018_u002E_178 | Parametersatz 3->f<> | 018.178 | 0-10:0.001;blockiert=10.002 | s | tf4 PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 3 | 0 | 4 | SE | 10 | Frequency\f4 | Tdel | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 4 | Frequency\f4 | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | GE | 10.002 | Frequency\f4 | Tdel | Real | 0 | 9999999 | [7 empty] | Frequency\f4 | Tdel | Real |  |  | 0 | 10.002
[16 empty] | SE | 10 | Frequency\df4/dt | Tdel | Real | 1 | 0 | [7 empty] | Frequency\df4/dt | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | GE | 10.002 | Frequency\df4/dt | Tdel | Real | 0 | 9999999 | [7 empty] | Frequency\df4/dt | Tdel | Real |  |  | 0 | 10.002
x018_u002E_182 | Parametersatz 3->f<> | 018.182 | 0.1-10:0.001;blockiert=10.002 | Hz/s | df4/dt PS3 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x018_u002E_194 | E;E | Parameter subset 3;1 | 2 | 3 | SE | 10 | Frequency\df4/dt | dFset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 3 | 2 | Frequency\df4/dt | outserv | Real | E | 1 | 0 | 10.002
[16 empty] | SE | 10 | Frequency\df4/dt | outserv | Real | 0 | 0 | [7 empty] | Frequency\df4/dt | dFset | Real |  |  | 1 | 0
[16 empty] | GE | 10.002 | Frequency\df4/dt | outserv | Real | 0 | 1
x075_u002E_098 | Parametersatz 4->UMZ | 075.098 | nein¦0;ja¦1 |  | Freigabe PS4 | Enum | Parameter__Funktionsparameter | 1;0 | Real | 1 | x003_u002E_060;x022_u002E_075 | E;NE | Parameter subset 4;1 | 1 | 10 | E | 1 | Overcurrent\DTOC I> | outserv | Real | 0 | 1 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 10 | Overcurrent\DTOC I> | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\DTOC I>> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC I>> | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\DTOC I>>> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC I>>> | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\DTOC Ineg> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC Ineg> | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\DTOC Ineg>> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC Ineg>> | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\DTOC Ineg>>> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC Ineg>>> | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\DTOC Ineg>>>> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC Ineg>>>> | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\DTOC IN> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC IN> | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\DTOC IN>> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC IN>> | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\DTOC IN>>> | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\DTOC IN>>> | outserv | Real | E | 0 | 0 | 0
x075_u002E_007 | Parametersatz 4->UMZ | 075.007 | 0.1-40:0.01;blockiert=40.02 | Inom | I> PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x075_u002E_098 | E;NE;NE | Parameter subset 4;1;1 | 1 | 3 | SE | 40 | Overcurrent\DTOC I> | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Overcurrent\DTOC I> | outserv | Real | E | 1 | 0 | 40.02
[16 empty] | SE | 40 | Overcurrent\DTOC I> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\DTOC I> | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 40.02 | Overcurrent\DTOC I> | outserv | Real | 0 | 1
x075_u002E_008 | Parametersatz 4->UMZ | 075.008 | 0.1-40:0.01;blockiert=40.02 | Inom | I>> PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x075_u002E_098 | E;NE;NE | Parameter subset 4;1;1 | 4 | 3 | SE | 40 | Overcurrent\DTOC I>> | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Overcurrent\DTOC I>> | outserv | Real | E | 1 | 0 | 40.02
[16 empty] | SE | 40 | Overcurrent\DTOC I>> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\DTOC I>> | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 40.02 | Overcurrent\DTOC I>> | outserv | Real | 0 | 1
x075_u002E_009 | Parametersatz 4->UMZ | 075.009 | 0.1-40:0.01;blockiert=40.02 | Inom | I>>> PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x075_u002E_098 | E;NE;NE | Parameter subset 4;1;1 | 40.02 | 4 | SE | 40 | Overcurrent\DTOC I>>> | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Overcurrent\DTOC I>>> | outserv | Real | E | 1 | 0 | 40.02
[16 empty] | SE | 40 | Overcurrent\DTOC I>>> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\DTOC I>>> | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 40.02 | Overcurrent\DTOC I>>> | outserv | Real | 0 | 1
[18 empty] | Overcurrent\DTOC I>>> | idir | Real | 0 | 0
x075_u002E_019 | Parametersatz 4->UMZ | 075.019 | 0-100:0.01;blockiert=100.02 | s | tI> PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x075_u002E_098 | E;NE;NE | Parameter subset 4;1;1 | 1 | 2 | SE | 100 | Overcurrent\DTOC I> | Tset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Overcurrent\DTOC I> | Tset | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Overcurrent\DTOC I> | Tset | Real | 0 | 9999999 | [7 empty] | Overcurrent\DTOC I> | Tset | Real |  |  | 0 | 100.02
x075_u002E_020 | Parametersatz 4->UMZ | 075.020 | 0-100:0.01;blockiert=100.02 | s | tI>> PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x075_u002E_098 | E;NE;NE | Parameter subset 4;1;1 | 0.5 | 2 | SE | 100 | Overcurrent\DTOC I>> | Tset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Overcurrent\DTOC I>> | Tset | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Overcurrent\DTOC I>> | Tset | Real | 0 | 9999999 | [7 empty] | Overcurrent\DTOC I>> | Tset | Real |  |  | 0 | 100.02
x075_u002E_021 | Parametersatz 4->UMZ | 075.021 | 0-100:0.01;blockiert=100.02 | s | tI>>> PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x075_u002E_098 | E;NE;NE | Parameter subset 4;1;1 | 0.5 | 2 | SE | 100 | Overcurrent\DTOC I>>> | Tset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Overcurrent\DTOC I>>> | Tset | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Overcurrent\DTOC I>>> | Tset | Real | 0 | 9999999 | [7 empty] | Overcurrent\DTOC I>>> | Tset | Real |  |  | 0 | 100.02
x075_u002E_011 | Parametersatz 4->UMZ | 075.011 | 0.1-25:0.01;blockiert=25.02 | Inom | Igegen> PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x075_u002E_098 | E;NE;NE | Parameter subset 4;1;1 | 1 | 3 | SE | 25 | Overcurrent\DTOC Ineg> | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Overcurrent\DTOC Ineg> | outserv | Real | E | 1 | 0 | 25.02
[16 empty] | SE | 25 | Overcurrent\DTOC Ineg> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\DTOC Ineg> | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 25.02 | Overcurrent\DTOC Ineg> | outserv | Real | 0 | 1
x075_u002E_012 | Parametersatz 4->UMZ | 075.012 | 0.1-25:0.01;blockiert=25.02 | Inom | Igegen>> PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x075_u002E_098 | E;NE;NE | Parameter subset 4;1;1 | 4 | 3 | SE | 25 | Overcurrent\DTOC Ineg>> | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Overcurrent\DTOC Ineg>> | outserv | Real | E | 1 | 0 | 25.02
[16 empty] | SE | 25 | Overcurrent\DTOC Ineg>> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\DTOC Ineg>> | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 25.02 | Overcurrent\DTOC Ineg>> | outserv | Real | 0 | 1
x075_u002E_013 | Parametersatz 4->UMZ | 075.013 | 0.1-25:0.01;blockiert=25.02 | Inom | Igegen>>> PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x075_u002E_098 | E;NE;NE | Parameter subset 4;1;1 | 25.02 | 3 | SE | 25 | Overcurrent\DTOC Ineg>>> | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Overcurrent\DTOC Ineg>>> | outserv | Real | E | 1 | 0 | 25.02
[16 empty] | SE | 25 | Overcurrent\DTOC Ineg>>> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\DTOC Ineg>>> | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 25.02 | Overcurrent\DTOC Ineg>>> | outserv | Real | 0 | 1
x075_u002E_023 | Parametersatz 4->UMZ | 075.023 | 0-100:0.01;blockiert=100.02 | s | tIgegen> PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x075_u002E_098 | E;NE;NE | Parameter subset 4;1;1 | 1 | 2 | SE | 100 | Overcurrent\DTOC Ineg> | Tset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Overcurrent\DTOC Ineg> | Tset | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Overcurrent\DTOC Ineg> | Tset | Real | 0 | 9999999 | [7 empty] | Overcurrent\DTOC Ineg> | Tset | Real |  |  | 0 | 100.02
x075_u002E_024 | Parametersatz 4->UMZ | 075.024 | 0-100:0.01;blockiert=100.02 | s | tIgegen>> PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x075_u002E_098 | E;NE;NE | Parameter subset 4;1;1 | 0.5 | 2 | SE | 100 | Overcurrent\DTOC Ineg>> | Tset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Overcurrent\DTOC Ineg>> | Tset | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Overcurrent\DTOC Ineg>> | Tset | Real | 0 | 9999999 | [7 empty] | Overcurrent\DTOC Ineg>> | Tset | Real |  |  | 0 | 100.02
x075_u002E_025 | Parametersatz 4->UMZ | 075.025 | 0-100:0.01;blockiert=100.02 | s | tIgegen>>> PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x075_u002E_098 | E;NE;NE | Parameter subset 4;1;1 | 100.02 | 2 | SE | 100 | Overcurrent\DTOC Ineg>>> | Tset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Overcurrent\DTOC Ineg>>> | Tset | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Overcurrent\DTOC Ineg>>> | Tset | Real | 0 | 9999999 | [7 empty] | Overcurrent\DTOC Ineg>>> | Tset | Real |  |  | 0 | 100.02
x075_u002E_015 | Parametersatz 4->UMZ | 075.015 | 0.002-8:0.001;blockiert=8.002 | Inom | IE> PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x075_u002E_098 | E;NE;NE | Parameter subset 4;1;1 | 0.25 | 3 | SE | 8 | Overcurrent\DTOC IN> | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Overcurrent\DTOC IN> | outserv | Real | E | 1 | 0 | 8.002
[16 empty] | SE | 8 | Overcurrent\DTOC IN> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\DTOC IN> | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 8.002 | Overcurrent\DTOC IN> | outserv | Real | 0 | 1
x075_u002E_016 | Parametersatz 4->UMZ | 075.016 | 0.002-8:0.001;blockiert=8.002 | Inom | IE>> PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x075_u002E_098 | E;NE;NE | Parameter subset 4;1;1 | 8.002 | 3 | SE | 8 | Overcurrent\DTOC IN>> | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Overcurrent\DTOC IN>> | outserv | Real | E | 1 | 0 | 8.002
[16 empty] | SE | 8 | Overcurrent\DTOC IN>> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\DTOC IN>> | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 8.002 | Overcurrent\DTOC IN>> | outserv | Real | 0 | 1
x075_u002E_017 | Parametersatz 4->UMZ | 075.017 | 0.002-8:0.001;blockiert=8.002 | Inom | IE>>> PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x075_u002E_098 | E;NE;NE | Parameter subset 4;1;1 | 8.002 | 4 | SE | 8 | Overcurrent\DTOC IN>>> | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Overcurrent\DTOC IN>>> | outserv | Real | E | 1 | 0 | 8.002
[16 empty] | SE | 8 | Overcurrent\DTOC IN>>> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\DTOC IN>>> | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 8.002 | Overcurrent\DTOC IN>>> | outserv | Real | 0 | 1
[18 empty] | Overcurrent\DTOC IN>>> | idir | Real | 0 | 0
x075_u002E_018 | Parametersatz 4->UMZ | 075.018 | 0.1-40:0.01;blockiert=40.02 | Inom | IE>>>> PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x075_u002E_098 | E;NE;NE | Parameter subset 4;1;1 | 40.02 | 3 | SE | 40 | Overcurrent\DTOC IN>>>> | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Overcurrent\DTOC IN>>>> | outserv | Real | E | 1 | 0 | 40.02
[16 empty] | SE | 40 | Overcurrent\DTOC IN>>>> | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\DTOC IN>>>> | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 40.02 | Overcurrent\DTOC IN>>>> | outserv | Real | 0 | 1
x075_u002E_027 | Parametersatz 4->UMZ | 075.027 | 0-100:0.01;blockiert=100.02 | s | tIE> PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x075_u002E_098 | E;NE;NE | Parameter subset 4;1;1 | 1 | 2 | SE | 100 | Overcurrent\DTOC IN> | Tset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Overcurrent\DTOC IN> | Tset | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Overcurrent\DTOC IN> | Tset | Real | 0 | 9999999 | [7 empty] | Overcurrent\DTOC IN> | Tset | Real |  |  | 0 | 100.02
x075_u002E_028 | Parametersatz 4->UMZ | 075.028 | 0-100:0.01;blockiert=100.02 | s | tIE>> PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x075_u002E_098 | E;NE;NE | Parameter subset 4;1;1 | 0.5 | 2 | SE | 100 | Overcurrent\DTOC IN>> | Tset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Overcurrent\DTOC IN>> | Tset | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Overcurrent\DTOC IN>> | Tset | Real | 0 | 9999999 | [7 empty] | Overcurrent\DTOC IN>> | Tset | Real |  |  | 0 | 100.02
x075_u002E_029 | Parametersatz 4->UMZ | 075.029 | 0-100:0.01;blockiert=100.02 | s | tIE>>> PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x075_u002E_098 | E;NE;NE | Parameter subset 4;1;1 | 0.5 | 2 | SE | 100 | Overcurrent\DTOC IN>>> | Tset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Overcurrent\DTOC IN>>> | Tset | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Overcurrent\DTOC IN>>> | Tset | Real | 0 | 9999999 | [7 empty] | Overcurrent\DTOC IN>>> | Tset | Real |  |  | 0 | 100.02
x075_u002E_030 | Parametersatz 4->UMZ | 075.030 | 0-100:0.01;blockiert=100.02 | s | tIE>>>> PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x022_u002E_075;x075_u002E_098 | E;NE;NE | Parameter subset 4;1;1 | 0.5 | 2 | SE | 100 | Overcurrent\DTOC IN>>>> | Tset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Overcurrent\DTOC IN>>>> | Tset | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Overcurrent\DTOC IN>>>> | Tset | Real | 0 | 9999999 | [7 empty] | Overcurrent\DTOC IN>>>> | Tset | Real |  |  | 0 | 100.02
x075_u002E_070 | Parametersatz 4->AMZ_1 | 075.070 | nein¦0;ja¦1 |  | Freigabe PS4 | Enum | Parameter__Funktionsparameter | 1;0 | Real | 1 | x003_u002E_060;x017_u002E_096 | E;NE | Parameter subset 4;1 | 1 | 6 | E | 1 | Overcurrent\IDMT1 P | outserv | Real | 0 | 1 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 3 | Overcurrent\IDMT1 P | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\IDMT1 neg | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\IDMT1 neg | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\IDMT1 N | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\IDMT1 N | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 0 | Overcurrent\IDMT1 P | ModFrame | Real | 0 | 1
[16 empty] | E | 0 | Overcurrent\IDMT1 neg | ModFrame | Real | 0 | 1
[16 empty] | E | 0 | Overcurrent\IDMT1 N | ModFrame | Real | 0 | 1
x075_u002E_050 | Parametersatz 4->AMZ_1 | 075.050 | 0.1-4:0.01;blockiert=4.02 | Inom | IB,L PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x017_u002E_096;x075_u002E_070 | E;NE;NE | Parameter subset 4;1;1 | 1 | 4 | SE | 4 | Overcurrent\IDMT1 P | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Overcurrent\IDMT1 P | outserv | Real | E | 1 | 0 | 4.02
[16 empty] | SE | 4 | Overcurrent\IDMT1 P | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\IDMT1 P | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 4.02 | Overcurrent\IDMT1 P | outserv | Real | 0 | 1
[18 empty] | Overcurrent\IDMT1 KI P | outserv | Real | 0 | 1
x075_u002E_056 | Parametersatz 4->AMZ_1 | 075.056 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Kennlinientyp L PS4 | Enum | Parameter__Funktionsparameter | Definite Time;IEC Standard Inverse;IEC Very Inverse;IEC Extremely Inverse;IEC Long Time Inverse;IEEE Moderately Inverse;IEEE Very Inverse;IEEE Extremely Inverse;ANSI Normally Inverse;ANSI Short Time Inverse;ANSI Long Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | 1 | x003_u002E_060 | E | Parameter subset 4 | Definite Time | 1 |  |  | Overcurrent\IDMT1 P | pcharac | String |  |  | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 1 | Overcurrent\IDMT1 P | pcharac | String
x075_u002E_053 | Parametersatz 4->AMZ_1 | 075.053 | 0.05-10:0.01 |  | Kennl.fakt. kt,L PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 4 | 1 | 2 |  |  | Overcurrent\IDMT1 P | Tpset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 1 | Overcurrent\IDMT1 P | Tpset | Real |  |  | 1 | 0
[18 empty] | Overcurrent\IDMT1 P | Tadder | Real | 0 | 0
x075_u002E_077 | Parametersatz 4->AMZ_1 | 075.077 | 0-10:0.001 | s | min. Auslösez. L PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 4 | 0 | 1 |  |  | Overcurrent\IDMT1 P | minresptime | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 1 | Overcurrent\IDMT1 P | minresptime | Real |  |  | 1 | 0
x075_u002E_059 | Parametersatz 4->AMZ_1 | 075.059 | unverzögert¦0;verzögert gem. Kennl¦1 |  | Rückfallen L PS4 | Enum | Parameter__Funktionsparameter | 0;1 | Real | 3 | x003_u002E_060;x075_u002E_056 | E;SW | Parameter subset 4;IEEE | 0 | 1 |  |  | Overcurrent\IDMT1 P | resetdis | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 1 | Overcurrent\IDMT1 P | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x075_u002E_056 | E;SW | Parameter subset 4;ANSI |  | 1 |  |  | Overcurrent\IDMT1 P | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | Parameter subset 4 |  | 1 |  |  | Overcurrent\IDMT1 P | resetdis | Real | 0 | 0
x075_u002E_051 | Parametersatz 4->AMZ_1 | 075.051 | 0.01-4:0.01;blockiert=4.02 | Inom | IB,gegen PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x017_u002E_096;x075_u002E_070 | E;NE;NE | Parameter subset 4;1;1 | 1 | 4 | SE | 4 | Overcurrent\IDMT1 neg | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Overcurrent\IDMT1 neg | outserv | Real | E | 1 | 0 | 4.02
[16 empty] | SE | 4 | Overcurrent\IDMT1 neg | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\IDMT1 neg | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 4.02 | Overcurrent\IDMT1 neg | outserv | Real | 0 | 1
[18 empty] | Overcurrent\IDMT1 KI neg | outserv | Real | 0 | 1
x075_u002E_057 | Parametersatz 4->AMZ_1 | 075.057 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Kennl.typ gegen PS4 | Enum | Parameter__Funktionsparameter | Definite Time;IEC Standard Inverse;IEC Very Inverse;IEC Extremely Inverse;IEC Long Time Inverse;IEEE Moderately Inverse;IEEE Very Inverse;IEEE Extremely Inverse;ANSI Normally Inverse;ANSI Short Time Inverse;ANSI Long Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | 1 | x003_u002E_060 | E | Parameter subset 4 | Definite Time | 1 |  |  | Overcurrent\IDMT1 neg | pcharac | String |  |  | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 1 | Overcurrent\IDMT1 neg | pcharac | String
x075_u002E_054 | Parametersatz 4->AMZ_1 | 075.054 | 0.05-10:0.01 |  | Kennl.f. kt,gegn PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 4 | 1 | 2 |  |  | Overcurrent\IDMT1 neg | Tpset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 1 | Overcurrent\IDMT1 neg | Tpset | Real |  |  | 1 | 0
[18 empty] | Overcurrent\IDMT1 neg | Tadder | Real | 0 | 0
x075_u002E_078 | Parametersatz 4->AMZ_1 | 075.078 | 0-10:0.001 | s | min.Auslösez.geg PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 4 | 0 | 1 |  |  | Overcurrent\IDMT1 neg | minresptime | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 1 | Overcurrent\IDMT1 neg | minresptime | Real |  |  | 1 | 0
x075_u002E_060 | Parametersatz 4->AMZ_1 | 075.060 | unverzögert¦0;verzögert gem. Kennl¦1 |  | Rückfallen gegen PS4 | Enum | Parameter__Funktionsparameter | 0;1 | Real | 3 | x003_u002E_060;x075_u002E_057 | E;SW | Parameter subset 4;IEEE | 0 | 1 |  |  | Overcurrent\IDMT1 neg | resetdis | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 1 | Overcurrent\IDMT1 neg | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x075_u002E_057 | E;SW | Parameter subset 4;ANSI |  | 1 |  |  | Overcurrent\IDMT1 neg | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | Parameter subset 4 |  | 1 |  |  | Overcurrent\IDMT1 neg | resetdis | Real | 0 | 0
x075_u002E_052 | Parametersatz 4->AMZ_1 | 075.052 | 0.01-4:0.01;blockiert=4.02 | Inom | IB,E PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x017_u002E_096;x075_u002E_070 | E;NE;NE | Parameter subset 4;1;1 | 1 | 4 | SE | 4 | Overcurrent\IDMT1 N | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Overcurrent\IDMT1 N | outserv | Real | E | 1 | 0 | 4.02
[16 empty] | SE | 4 | Overcurrent\IDMT1 N | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\IDMT1 N | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 4.02 | Overcurrent\IDMT1 N | outserv | Real | 0 | 1
[18 empty] | Overcurrent\IDMT1 KI N | outserv | Real | 0 | 1
x075_u002E_058 | Parametersatz 4->AMZ_1 | 075.058 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Kennlinientyp E PS4 | Enum | Parameter__Funktionsparameter | Definite Time;IEC Standard Inverse;IEC Very Inverse;IEC Extremely Inverse;IEC Long Time Inverse;IEEE Moderately Inverse;IEEE Very Inverse;IEEE Extremely Inverse;ANSI Normally Inverse;ANSI Short Time Inverse;ANSI Long Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | 1 | x003_u002E_060 | E | Parameter subset 4 | Definite Time | 1 |  |  | Overcurrent\IDMT1 N | pcharac | String |  |  | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 1 | Overcurrent\IDMT1 N | pcharac | String
x075_u002E_055 | Parametersatz 4->AMZ_1 | 075.055 | 0.05-10:0.01 |  | Kennl.f. kt,E PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 4 | 1 | 2 |  |  | Overcurrent\IDMT1 N | Tpset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 1 | Overcurrent\IDMT1 N | Tpset | Real |  |  | 1 | 0
[18 empty] | Overcurrent\IDMT1 N | Tadder | Real | 0 | 0
x075_u002E_079 | Parametersatz 4->AMZ_1 | 075.079 | 0-10:0.001 | s | min. Auslösez.E PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 4 | 0 | 1 |  |  | Overcurrent\IDMT1 N | minresptime | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 1 | Overcurrent\IDMT1 N | minresptime | Real |  |  | 1 | 0
x075_u002E_061 | Parametersatz 4->AMZ_1 | 075.061 | unverzögert¦0;verzögert gem. Kennl¦1 |  | Rückfallen E PS4 | Enum | Parameter__Funktionsparameter | 0;1 | Real | 3 | x003_u002E_060;x075_u002E_058 | E;SW | Parameter subset 4;IEEE | 0 | 1 |  |  | Overcurrent\IDMT1 N | resetdis | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 1 | Overcurrent\IDMT1 N | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x075_u002E_058 | E;SW | Parameter subset 4;ANSI |  | 1 |  |  | Overcurrent\IDMT1 N | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | Parameter subset 4 |  | 1 |  |  | Overcurrent\IDMT1 N | resetdis | Real | 0 | 0
x076_u002E_045 | Parametersatz 4->AMZ_2 | 076.045 | nein¦0;ja¦1 |  | Freigabe PS4 | Enum | Parameter__Funktionsparameter | 1;0 | Real | 1 | x003_u002E_060;x017_u002E_052 | E;NE | Parameter subset 4;1 | 1 | 6 | E | 1 | Overcurrent\IDMT2 P | outserv | Real | 0 | 1 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 3 | Overcurrent\IDMT2 P | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\IDMT2 neg | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\IDMT2 neg | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Overcurrent\IDMT2 N | outserv | Real | 0 | 1 | [7 empty] | Overcurrent\IDMT2 N | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 0 | Overcurrent\IDMT2 P | ModFrame | Real | 0 | 1
[16 empty] | E | 0 | Overcurrent\IDMT2 neg | ModFrame | Real | 0 | 1
[16 empty] | E | 0 | Overcurrent\IDMT2 N | ModFrame | Real | 0 | 1
x076_u002E_239 | Parametersatz 4->AMZ_2 | 076.239 | 0.1-4:0.01;blockiert=4.02 | Inom | IB,L PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x017_u002E_052;x076_u002E_045 | E;NE;NE | Parameter subset 4;1;1 | 1 | 3 | SE | 4 | Overcurrent\IDMT2 P | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Overcurrent\IDMT2 P | outserv | Real | E | 1 | 0 | 4.02
[16 empty] | SE | 4 | Overcurrent\IDMT2 P | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\IDMT2 P | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 4.02 | Overcurrent\IDMT2 P | outserv | Real | 0 | 1
x071_u002E_007 | Parametersatz 4->AMZ_2 | 071.007 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Kennlinientyp L PS4 | Enum | Parameter__Funktionsparameter | Definite Time;IEC Standard Inverse;IEC Very Inverse;IEC Extremely Inverse;IEC Long Time Inverse;IEEE Moderately Inverse;IEEE Very Inverse;IEEE Extremely Inverse;ANSI Normally Inverse;ANSI Short Time Inverse;ANSI Long Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | 1 | x003_u002E_060 | E | Parameter subset 4 | Definite Time | 1 |  |  | Overcurrent\IDMT2 P | pcharac | String |  |  | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 1 | Overcurrent\IDMT2 P | pcharac | String
x078_u002E_253 | Parametersatz 4->AMZ_2 | 078.253 | 0.05-10:0.01 |  | Kennl.fakt. kt,L PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 4 | 1 | 1 |  |  | Overcurrent\IDMT2 P | Tpset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 1 | Overcurrent\IDMT2 P | Tpset | Real |  |  | 1 | 0
x071_u002E_047 | Parametersatz 4->AMZ_2 | 071.047 | 0-10:0.001 | s | min. Auslösez. L PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 4 | 0 | 1 |  |  | Overcurrent\IDMT2 P | minresptime | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 1 | Overcurrent\IDMT2 P | minresptime | Real |  |  | 1 | 0
x071_u002E_019 | Parametersatz 4->AMZ_2 | 071.019 | unverzögert¦0;verzögert gem. Kennl¦1 |  | Rückfallen L PS4 | Enum | Parameter__Funktionsparameter | 0;1 | Real | 3 | x003_u002E_060;x071_u002E_007 | E;SW | Parameter subset 4;IEEE | 0 | 1 |  |  | Overcurrent\IDMT2 P | resetdis | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 1 | Overcurrent\IDMT2 P | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x071_u002E_007 | E;SW | Parameter subset 4;ANSI |  | 1 |  |  | Overcurrent\IDMT2 P | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | Parameter subset 4 |  | 1 |  |  | Overcurrent\IDMT2 P | resetdis | Real | 0 | 0
x076_u002E_253 | Parametersatz 4->AMZ_2 | 076.253 | 0.01-4:0.01;blockiert=4.02 | Inom | IB,gegen PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x017_u002E_052;x076_u002E_045 | E;NE;NE | Parameter subset 4;1;1 | 1 | 3 | SE | 4 | Overcurrent\IDMT2 neg | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Overcurrent\IDMT2 neg | outserv | Real | E | 1 | 0 | 4.02
[16 empty] | SE | 4 | Overcurrent\IDMT2 neg | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\IDMT2 neg | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 4.02 | Overcurrent\IDMT2 neg | outserv | Real | 0 | 1
x071_u002E_011 | Parametersatz 4->AMZ_2 | 071.011 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Kennl.typ gegen PS4 | Enum | Parameter__Funktionsparameter | Definite Time;IEC Standard Inverse;IEC Very Inverse;IEC Extremely Inverse;IEC Long Time Inverse;IEEE Moderately Inverse;IEEE Very Inverse;IEEE Extremely Inverse;ANSI Normally Inverse;ANSI Short Time Inverse;ANSI Long Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | 1 | x003_u002E_060 | E | Parameter subset 4 | Definite Time | 1 |  |  | Overcurrent\IDMT2 neg | pcharac | String |  |  | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 1 | Overcurrent\IDMT2 neg | pcharac | String
x079_u002E_253 | Parametersatz 4->AMZ_2 | 079.253 | 0.05-10:0.01 |  | Kennl.f. kt,gegn PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 4 | 1 | 1 |  |  | Overcurrent\IDMT2 neg | Tpset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 1 | Overcurrent\IDMT2 neg | Tpset | Real |  |  | 1 | 0
x071_u002E_051 | Parametersatz 4->AMZ_2 | 071.051 | 0-10:0.001 | s | min.Auslösez.geg PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 4 | 0 | 1 |  |  | Overcurrent\IDMT2 neg | minresptime | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 1 | Overcurrent\IDMT2 neg | minresptime | Real |  |  | 1 | 0
x071_u002E_023 | Parametersatz 4->AMZ_2 | 071.023 | unverzögert¦0;verzögert gem. Kennl¦1 |  | Rückfallen gegen PS4 | Enum | Parameter__Funktionsparameter | 0;1 | Real | 3 | x003_u002E_060;x071_u002E_011 | E;SW | Parameter subset 4;IEEE | 0 | 1 |  |  | Overcurrent\IDMT2 neg | resetdis | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 1 | Overcurrent\IDMT2 neg | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x071_u002E_011 | E;SW | Parameter subset 4;ANSI |  | 1 |  |  | Overcurrent\IDMT2 neg | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | Parameter subset 4 |  | 1 |  |  | Overcurrent\IDMT2 neg | resetdis | Real | 0 | 0
x077_u002E_253 | Parametersatz 4->AMZ_2 | 077.253 | 0.01-4:0.01;blockiert=4.02 | Inom | IB,E PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x017_u002E_052;x076_u002E_045 | E;NE;NE | Parameter subset 4;1;1 | 1 | 3 | SE | 4 | Overcurrent\IDMT2 N | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Overcurrent\IDMT2 N | outserv | Real | E | 1 | 0 | 4.02
[16 empty] | SE | 4 | Overcurrent\IDMT2 N | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\IDMT2 N | Ipset | Real |  |  | 1 | 0
[16 empty] | GE | 4.02 | Overcurrent\IDMT2 N | outserv | Real | 0 | 1
x071_u002E_015 | Parametersatz 4->AMZ_2 | 071.015 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Kennlinientyp E PS4 | Enum | Parameter__Funktionsparameter | Definite Time;IEC Standard Inverse;IEC Very Inverse;IEC Extremely Inverse;IEC Long Time Inverse;IEEE Moderately Inverse;IEEE Very Inverse;IEEE Extremely Inverse;ANSI Normally Inverse;ANSI Short Time Inverse;ANSI Long Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | 1 | x003_u002E_060 | E | Parameter subset 4 | Definite Time | 1 |  |  | Overcurrent\IDMT2 N | pcharac | String |  |  | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 1 | Overcurrent\IDMT2 N | pcharac | String
x071_u002E_003 | Parametersatz 4->AMZ_2 | 071.003 | 0.05-10:0.01 |  | Kennl.f. kt,E PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 4 | 1 | 1 |  |  | Overcurrent\IDMT2 N | Tpset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 1 | Overcurrent\IDMT2 N | Tpset | Real |  |  | 1 | 0
x071_u002E_055 | Parametersatz 4->AMZ_2 | 071.055 | 0-10:0.001 | s | min. Auslösez.E PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 4 | 0 | 1 |  |  | Overcurrent\IDMT2 N | minresptime | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 1 | Overcurrent\IDMT2 N | minresptime | Real |  |  | 1 | 0
x071_u002E_027 | Parametersatz 4->AMZ_2 | 071.027 | unverzögert¦0;verzögert gem. Kennl¦1 |  | Rückfallen E PS4 | Enum | Parameter__Funktionsparameter | 0;1 | Real | 3 | x003_u002E_060;x071_u002E_015 | E;SW | Parameter subset 4;IEEE | 0 | 1 |  |  | Overcurrent\IDMT2 N | resetdis | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 1 | Overcurrent\IDMT2 N | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x071_u002E_015 | E;SW | Parameter subset 4;ANSI |  | 1 |  |  | Overcurrent\IDMT2 N | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | Parameter subset 4 |  | 1 |  |  | Overcurrent\IDMT2 N | resetdis | Real | 0 | 0
x079_u002E_235 | Parametersatz 4->KURI | 079.235 | nein¦0;ja¦1 |  | Freigabe PS4 | Enum | Parameter__Funktionsparameter | 1;0 | Real | 1 | x003_u002E_060;x017_u002E_070 | E;NE | Parameter subset 4;1 | 1 | 2 |  |  | Overcurrent\Directional P | outserv | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Overcurrent\Directional P | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\Directional N | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\Directional N | outserv | Real | E | 0 | 0 | 0
x079_u002E_237 | Parametersatz 4->KURI | 079.237 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung tI> PS4 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real | 1 | x003_u002E_060;x017_u002E_070;x079_u002E_235 | E;NE;NE | Parameter subset 4;1;1 | 1 | 1 |  |  | Overcurrent\DTOC I> | idir | Real | 1 | 0 | 1 | Overcurrent\Directional P;x003_u002E_060 | outserv | Real | E;E | 0;Parameter subset 4 | 1 | Overcurrent\DTOC I> | idir | Real |  |  | 1 | 0
x079_u002E_238 | Parametersatz 4->KURI | 079.238 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung tI>> PS4 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real | 1 | x003_u002E_060;x017_u002E_070;x079_u002E_235 | E;NE;NE | Parameter subset 4;1;1 | 1 | 1 |  |  | Overcurrent\DTOC I>> | idir | Real | 1 | 0 | 1 | Overcurrent\Directional P;x003_u002E_060 | outserv | Real | E;E | 0;Parameter subset 4 | 1 | Overcurrent\DTOC I>> | idir | Real |  |  | 1 | 0
x079_u002E_240 | Parametersatz 4->KURI | 079.240 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung tIE> PS4 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real | 1 | x003_u002E_060;x017_u002E_070;x079_u002E_235 | E;NE;NE | Parameter subset 4;1;1 | 1 | 1 |  |  | Overcurrent\DTOC IN> | idir | Real | 1 | 0 | 1 | Overcurrent\Directional N;x003_u002E_060 | outserv | Real | E;E | 0;Parameter subset 4 | 1 | Overcurrent\DTOC IN> | idir | Real |  |  | 1 | 0
x079_u002E_241 | Parametersatz 4->KURI | 079.241 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung tIE>> PS4 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real | 1 | x003_u002E_060;x017_u002E_070;x079_u002E_235 | E;NE;NE | Parameter subset 4;1;1 | 1 | 1 |  |  | Overcurrent\DTOC IN>> | idir | Real | 1 | 0 | 1 | Overcurrent\Directional N;x003_u002E_060 | outserv | Real | E;E | 0;Parameter subset 4 | 1 | Overcurrent\DTOC IN>> | idir | Real |  |  | 1 | 0
x079_u002E_239 | Parametersatz 4->KURI | 079.239 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung tIB,L> PS4 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real | 1 | x003_u002E_060;x017_u002E_070;x079_u002E_235 | E;NE;NE | Parameter subset 4;1;1 | 1 | 1 |  |  | Overcurrent\IDMT1 P | idir | Real | 1 | 0 | 1 | Overcurrent\Directional P;x003_u002E_060 | outserv | Real | E;E | 0;Parameter subset 4 | 1 | Overcurrent\IDMT1 P | idir | Real |  |  | 1 | 0
x079_u002E_242 | Parametersatz 4->KURI | 079.242 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung tIB,E> PS4 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real | 1 | x003_u002E_060;x017_u002E_070;x079_u002E_235 | E;NE;NE | Parameter subset 4;1;1 | 1 | 1 |  |  | Overcurrent\IDMT1 N | idir | Real | 1 | 0 | 1 | Overcurrent\Directional N;x003_u002E_060 | outserv | Real | E;E | 0;Parameter subset 4 | 1 | Overcurrent\IDMT1 N | idir | Real |  |  | 1 | 0
x079_u002E_243 | Parametersatz 4->KURI | 079.243 | -90-90:0.1 | ° | charakt.Winkel E PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 4 | -45 | 1 |  |  | Overcurrent\Directional N | mtau | Real | 1 | 0 | 1 | Overcurrent\Directional N;x003_u002E_060 | outserv | Real | E;E | 0;Parameter subset 4 | 1 | Overcurrent\Directional N | mtau | Real |  |  | 1 | 0
x079_u002E_244 | Parametersatz 4->KURI | 079.244 | 0.015-0.6:0.001 | Unom(/©3) | UNE> PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 4 | 0.1 | 1 |  |  | Overcurrent\Directional N | upolur | Real | 1 | 0 | 1 | Overcurrent\Directional N;x003_u002E_060 | outserv | Real | E;E | 0;Parameter subset 4 | 1 | Overcurrent\Directional N | upolur | Real |  |  | 1 | 0
x079_u002E_246 | Parametersatz 4->U<> | 079.246 | nein¦0;ja¦1 |  | Freigabe PS4 | Enum | Parameter__Funktionsparameter | 1;0 | Real | 1 | x003_u002E_060;x023_u002E_030 | E;NE | Parameter subset 4;1 | 1 | 1 |  |  | Voltage | outserv | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 1 | Voltage | outserv | Real | E | 0 | 0 | 0
x079_u002E_001 | Parametersatz 4->U<> | 079.001 | Dreieck¦0;Stern¦1 |  | Betriebsart PS4 | Enum | Parameter__Funktionsparameter | Delta;Star | String | 1 | x003_u002E_060 | E | Parameter subset 4 | Delta | 8 | E | Star | Voltage\V> | outserv | Real | 0 | 1
[16 empty] | E | Star | Voltage\V>> | outserv | Real | 0 | 1
[16 empty] | E | Star | Voltage\V< | outserv | Real | 0 | 1
[16 empty] | E | Star | Voltage\V<< | outserv | Real | 0 | 1
[16 empty] | E | Star | Voltage\VNG> | outserv | Real | 0 | 1
[16 empty] | E | Star | Voltage\VNG>> | outserv | Real | 0 | 1
x079_u002E_003 | Parametersatz 4->U<> | 079.003 | 0.2-1.5:0.01;blockiert=1.52 | Unom(/©3) | U> PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x079_u002E_001 | E;E | Parameter subset 4;Delta | 1.1 | 3 | SE | 1.5 | Voltage\V> | Uset | Real | 1 | 0 | 1 | x003_u002E_060;x079_u002E_001 |  |  | E;E | Parameter subset 4;Delta | 2 | Voltage\V> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V> | outserv | Real | 0 | 0 | [7 empty] | Voltage\V> | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.52 | Voltage\V> | outserv | Real | 0 | 1
x079_u002E_004 | Parametersatz 4->U<> | 079.004 | 0.2-1.5:0.01;blockiert=1.52 | Unom(/©3) | U>> PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x079_u002E_001 | E;E | Parameter subset 4;Delta | 1.1 | 3 | SE | 1.5 | Voltage\V>> | Uset | Real | 1 | 0 | 1 | x003_u002E_060;x079_u002E_001 |  |  | E;E | Parameter subset 4;Delta | 2 | Voltage\V>> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\V>> | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.52 | Voltage\V>> | outserv | Real | 0 | 1
x079_u002E_005 | Parametersatz 4->U<> | 079.005 | 0-100:0.01;blockiert=100.02 | s | tU> PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 4 | 1 | 2 | SE | 100 | Voltage\V> | Tdel | Real | 1 | 0 | 1 | x003_u002E_060;x079_u002E_001 |  |  | E;E | Parameter subset 4;Delta | 2 | Voltage\V> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\V> | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\V> | Tdel | Real |  |  | 0 | 100.02
x079_u002E_006 | Parametersatz 4->U<> | 079.006 | 0-100:0.01;blockiert=100.02 | s | tU>> PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 4 | 1 | 2 | SE | 100 | Voltage\V>> | Tdel | Real | 1 | 0 | 1 | x003_u002E_060;x079_u002E_001 |  |  | E;E | Parameter subset 4;Delta | 2 | Voltage\V>> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\V>> | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\V>> | Tdel | Real |  |  | 0 | 100.02
x079_u002E_027 | Parametersatz 4->U<> | 079.027 | 0-100:0.01;blockiert=100.02 | s | tU> 3p PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 4 | 1 | 2 | SE | 100 | Voltage\tV> 3-pole | Tdelay | Real | 1 | 0 | 1 | x003_u002E_060;x079_u002E_001 |  |  | E;E | Parameter subset 4;Delta | 2 | Voltage\tV> 3-pole | Tdelay | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\tV> 3-pole | Tdelay | Real | 0 | 9999999 | [7 empty] | Voltage\tV> 3-pole | Tdelay | Real |  |  | 0 | 100.02
x079_u002E_007 | Parametersatz 4->U<> | 079.007 | 0.2-1.5:0.01;blockiert=1.52 | Unom(/©3) | U< PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x079_u002E_001 | E;E | Parameter subset 4;Delta | 0.8 | 3 | SE | 1.5 | Voltage\V< | Uset | Real | 1 | 0 | 1 | x003_u002E_060;x079_u002E_001 |  |  | E;E | Parameter subset 4;Delta | 2 | Voltage\V< | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V< | outserv | Real | 0 | 0 | [7 empty] | Voltage\V< | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.52 | Voltage\V< | outserv | Real | 0 | 1
x079_u002E_008 | Parametersatz 4->U<> | 079.008 | 0.2-1.5:0.01;blockiert=1.52 | Unom(/©3) | U<< PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x079_u002E_001 | E;E | Parameter subset 4;Delta | 0.8 | 3 | SE | 1.5 | Voltage\V<< | Uset | Real | 1 | 0 | 1 | x003_u002E_060;x079_u002E_001 |  |  | E;E | Parameter subset 4;Delta | 2 | Voltage\V<< | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V<< | outserv | Real | 0 | 0 | [7 empty] | Voltage\V<< | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.52 | Voltage\V<< | outserv | Real | 0 | 1
x079_u002E_009 | Parametersatz 4->U<> | 079.009 | 0-100:0.01;blockiert=100.02 | s | tU< PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 4 | 1 | 2 | SE | 100 | Voltage\V< | Tdel | Real | 1 | 0 | 1 | x003_u002E_060;x079_u002E_001 |  |  | E;E | Parameter subset 4;Delta | 2 | Voltage\V< | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\V< | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\V< | Tdel | Real |  |  | 0 | 100.02
x079_u002E_010 | Parametersatz 4->U<> | 079.010 | 0-100:0.01;blockiert=100.02 | s | tU<< PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 4 | 1 | 2 | SE | 100 | Voltage\V<< | Tdel | Real | 1 | 0 | 1 | x003_u002E_060;x079_u002E_001 |  |  | E;E | Parameter subset 4;Delta | 2 | Voltage\V<< | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\V<< | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\V<< | Tdel | Real |  |  | 0 | 100.02
x079_u002E_028 | Parametersatz 4->U<> | 079.028 | 0-100:0.01;blockiert=100.02 | s | tU< 3p PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 4 | 1 | 2 | SE | 100 | Voltage\tV< 3-pole | Tdelay | Real | 1 | 0 | 1 | x003_u002E_060;x079_u002E_001 |  |  | E;E | Parameter subset 4;Delta | 2 | Voltage\tV< 3-pole | Tdelay | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\tV< 3-pole | Tdelay | Real | 0 | 9999999 | [7 empty] | Voltage\tV< 3-pole | Tdelay | Real |  |  | 0 | 100.02
x079_u002E_015 | Parametersatz 4->U<> | 079.015 | 0.2-1.5:0.01;blockiert=1.52 | Unom/©3 | Umit> PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 4 | 1.1 | 3 | SE | 1.5 | Voltage\Vpos> | Uset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Voltage\Vpos> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos> | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.52 | Voltage\Vpos> | outserv | Real | 0 | 1
x079_u002E_016 | Parametersatz 4->U<> | 079.016 | 0.2-1.5:0.01;blockiert=1.52 | Unom/©3 | Umit>> PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 4 | 1.1 | 3 | SE | 1.5 | Voltage\Vpos>> | Uset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Voltage\Vpos>> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos>> | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.52 | Voltage\Vpos>> | outserv | Real | 0 | 1
x079_u002E_017 | Parametersatz 4->U<> | 079.017 | 0-100:0.01;blockiert=100.02 | s | tUmit> PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 4 | 1 | 2 | SE | 100 | Voltage\Vpos> | Tdel | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Voltage\Vpos> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\Vpos> | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\Vpos> | Tdel | Real |  |  | 0 | 100.02
x079_u002E_018 | Parametersatz 4->U<> | 079.018 | 0-100:0.01;blockiert=100.02 | s | tUmit>> PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 4 | 1 | 2 | SE | 100 | Voltage\Vpos>> | Tdel | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Voltage\Vpos>> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\Vpos>> | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\Vpos>> | Tdel | Real |  |  | 0 | 100.02
x079_u002E_019 | Parametersatz 4->U<> | 079.019 | 0.2-1.5:0.01;blockiert=1.52 | Unom/©3 | Umit< PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 4 | 0.8 | 3 | SE | 1.5 | Voltage\Vpos< | Uset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Voltage\Vpos< | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos< | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos< | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.52 | Voltage\Vpos< | outserv | Real | 0 | 1
x079_u002E_020 | Parametersatz 4->U<> | 079.020 | 0.2-1.5:0.01;blockiert=1.52 | Unom/©3 | Umit<< PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 4 | 0.8 | 3 | SE | 1.5 | Voltage\Vpos<< | Uset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Voltage\Vpos<< | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos<< | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos<< | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.52 | Voltage\Vpos<< | outserv | Real | 0 | 1
x079_u002E_021 | Parametersatz 4->U<> | 079.021 | 0-100:0.01;blockiert=100.02 | s | tUmit< PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 4 | 1 | 2 | SE | 100 | Voltage\Vpos< | Tdel | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Voltage\Vpos< | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\Vpos< | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\Vpos< | Tdel | Real |  |  | 0 | 100.02
x079_u002E_022 | Parametersatz 4->U<> | 079.022 | 0-100:0.01;blockiert=100.02 | s | tUmit<< PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 4 | 1 | 2 | SE | 100 | Voltage\Vpos<< | Tdel | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Voltage\Vpos<< | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\Vpos<< | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\Vpos<< | Tdel | Real |  |  | 0 | 100.02
x079_u002E_023 | Parametersatz 4->U<> | 079.023 | 0.02-1.5:0.01;blockiert=1.52 | Unom/©3 | Ugegen> PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 4 | 1.52 | 3 | SE | 1.5 | Voltage\Vneg> | Uset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Voltage\Vneg> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vneg> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vneg> | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.52 | Voltage\Vneg> | outserv | Real | 0 | 1
x079_u002E_024 | Parametersatz 4->U<> | 079.024 | 0.02-1.5:0.01;blockiert=1.52 | Unom/©3 | Ugegen>> PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 4 | 1.52 | 3 | SE | 1.5 | Voltage\Vneg>> | Uset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Voltage\Vneg>> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vneg>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vneg>> | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.52 | Voltage\Vneg>> | outserv | Real | 0 | 1
x079_u002E_025 | Parametersatz 4->U<> | 079.025 | 0-100:0.01;blockiert=100.02 | s | tUgegen> PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 4 | 1 | 2 | SE | 100 | Voltage\Vneg> | Tdel | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Voltage\Vneg> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\Vneg> | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\Vneg> | Tdel | Real |  |  | 0 | 100.02
x079_u002E_026 | Parametersatz 4->U<> | 079.026 | 0-100:0.01;blockiert=100.02 | s | tUgegen>> PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 4 | 1 | 2 | SE | 100 | Voltage\Vneg>> | Tdel | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Voltage\Vneg>> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\Vneg>> | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\Vneg>> | Tdel | Real |  |  | 0 | 100.02
x079_u002E_011 | Parametersatz 4->U<> | 079.011 | 0.02-1:0.01;blockiert=1.02 | Unom(/©3) | UNE> PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x079_u002E_001 | E;E | Parameter subset 4;Delta | 1.02 | 3 | SE | 1 | Voltage\VNG> | Uset | Real | 1 | 0 | 1 | x003_u002E_060;x079_u002E_001 |  |  | E;E | Parameter subset 4;Delta | 2 | Voltage\VNG> | outserv | Real | E | 1 | 0 | 1.02
[16 empty] | SE | 1 | Voltage\VNG> | outserv | Real | 0 | 0 | [7 empty] | Voltage\VNG> | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.02 | Voltage\VNG> | outserv | Real | 0 | 1
x079_u002E_012 | Parametersatz 4->U<> | 079.012 | 0.02-1:0.01;blockiert=1.02 | Unom(/©3) | UNE>> PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x079_u002E_001 | E;E | Parameter subset 4;Delta | 1.02 | 3 | SE | 1 | Voltage\VNG>> | Uset | Real | 1 | 0 | 1 | x003_u002E_060;x079_u002E_001 |  |  | E;E | Parameter subset 4;Delta | 2 | Voltage\VNG>> | outserv | Real | E | 1 | 0 | 1.02
[16 empty] | SE | 1 | Voltage\VNG>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\VNG>> | Uset | Real |  |  | 1 | 0
[16 empty] | GE | 1.02 | Voltage\VNG>> | outserv | Real | 0 | 1
x079_u002E_013 | Parametersatz 4->U<> | 079.013 | 0-100:0.01;blockiert=100.02 | s | tUNE> PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 4 | 1 | 2 | SE | 100 | Voltage\VNG> | Tdel | Real | 1 | 0 | 1 | x003_u002E_060;x079_u002E_001 |  |  | E;E | Parameter subset 4;Delta | 2 | Voltage\VNG> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\VNG> | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\VNG> | Tdel | Real |  |  | 0 | 100.02
x079_u002E_014 | Parametersatz 4->U<> | 079.014 | 0-100:0.01;blockiert=100.02 | s | tUNE>> PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 4 | 1 | 2 | SE | 100 | Voltage\VNG>> | Tdel | Real | 1 | 0 | 1 | x003_u002E_060;x079_u002E_001 |  |  | E;E | Parameter subset 4;Delta | 2 | Voltage\VNG>> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | GE | 100.02 | Voltage\VNG>> | Tdel | Real | 0 | 9999999 | [7 empty] | Voltage\VNG>> | Tdel | Real |  |  | 0 | 100.02
x001_u002E_165 | Parametersatz 4->U<> | 001.165 | ohne¦0;mit¦1 |  | Btr.art U< Überw PS4 | Enum | Parameter__Funktionsparameter | 1;0 | Real | 1 | x003_u002E_060 | E | Parameter subset 4 | 1 | 1 |  |  | Voltage\Imin | outserv | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 1 | Voltage\Imin | outserv | Real |  |  | 1 | 0
x001_u002E_161 | Parametersatz 4->U<> | 001.161 | 0.04-1:0.01 | Inom | I-Freigabe U< PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 4 | 0.1 | 1 |  |  | Voltage\Imin | Ipset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 1 | Voltage\Imin | Ipset | Real |  |  | 1 | 0
x018_u002E_199 | Parametersatz 4->f<> | 018.199 | nein¦0;ja¦1 |  | Freigabe PS4 | Enum | Parameter__Funktionsparameter | 1;0 | Real | 1 | x003_u002E_060;x023_u002E_031 | E;NE | Parameter subset 4;1 | 1 | 1 |  |  | Frequency | outserv | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 1 | Frequency | outserv | Real | E | 0 | 0 | 0
x018_u002E_123 | Parametersatz 4->f<> | 018.123 | f¦0;f mit df/dt¦1;f m. Delta f/Delta t¦2 |  | Betriebsart f1 PS4 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real | 1 | x003_u002E_060 | E | Parameter subset 4 | 0 | 1 | E | 0 | Frequency\df1/dt | outserv | Real | 0 | 1 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 3 | Frequency\f1 | outserv | Real | E | 1 | 0 | 0
[30 empty] | Frequency\df1/dt | outserv | Real | E | 1 | 0 | 0
[30 empty] | Frequency\df1/dt | outserv | Real |  |  | 0 | 1
x018_u002E_103 | Parametersatz 4->f<> | 018.103 | 40-70:0.01;blockiert=70.02 | Hz | f1 PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 4 | 49.8 | 3 | SE | 70 | Frequency\f1 | Fset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Frequency\f1 | outserv | Real | E | 1 | 0 | 70.02
[16 empty] | SE | 70 | Frequency\f1 | outserv | Real | 0 | 0 | [7 empty] | Frequency\f1 | Fset | Real |  |  | 1 | 0
[16 empty] | GE | 70.02 | Frequency\f1 | outserv | Real | 0 | 1
x018_u002E_107 | Parametersatz 4->f<> | 018.107 | 0-10:0.001;blockiert=10.002 | s | tf1 PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 4 | 0 | 4 | SE | 10 | Frequency\f1 | Tdel | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 4 | Frequency\f1 | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | GE | 10.002 | Frequency\f1 | Tdel | Real | 0 | 9999999 | [7 empty] | Frequency\f1 | Tdel | Real |  |  | 0 | 10.002
[16 empty] | SE | 10 | Frequency\df1/dt | Tdel | Real | 1 | 0 | [7 empty] | Frequency\df1/dt | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | GE | 10.002 | Frequency\df1/dt | Tdel | Real | 0 | 9999999 | [7 empty] | Frequency\df1/dt | Tdel | Real |  |  | 0 | 10.002
x018_u002E_111 | Parametersatz 4->f<> | 018.111 | 0.1-10:0.001;blockiert=10.002 | Hz/s | df1/dt PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x018_u002E_123 | E;E | Parameter subset 4;1 | 2 | 3 | SE | 10 | Frequency\df1/dt | dFset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Frequency\df1/dt | outserv | Real | E | 1 | 0 | 10.002
[16 empty] | SE | 10 | Frequency\df1/dt | outserv | Real | 0 | 0 | [7 empty] | Frequency\df1/dt | dFset | Real |  |  | 1 | 0
[16 empty] | GE | 10.002 | Frequency\df1/dt | outserv | Real | 0 | 1
x018_u002E_147 | Parametersatz 4->f<> | 018.147 | f¦0;f mit df/dt¦1;f m. Delta f/Delta t¦2 |  | Betriebsart f2 PS4 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real | 1 | x003_u002E_060 | E | Parameter subset 4 | 0 | 1 | E | 0 | Frequency\df2/dt | outserv | Real | 0 | 1 |  | x003_u002E_060 |  |  | E | Parameter subset 4 | 3 | Frequency\f2 | outserv | Real | E | 1 | 0 | 0
[30 empty] | Frequency\df2/dt | outserv | Real | E | 1 | 0 | 0
[30 empty] | Frequency\df2/dt | outserv | Real |  |  | 0 | 1
x018_u002E_127 | Parametersatz 4->f<> | 018.127 | 40-70:0.01;blockiert=70.02 | Hz | f2 PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 4 | 49.8 | 3 | SE | 70 | Frequency\f2 | Fset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Frequency\f2 | outserv | Real | E | 1 | 0 | 70.02
[16 empty] | SE | 70 | Frequency\f2 | outserv | Real | 0 | 0 | [7 empty] | Frequency\f2 | Fset | Real |  |  | 1 | 0
[16 empty] | GE | 70.02 | Frequency\f2 | outserv | Real | 0 | 1
x018_u002E_131 | Parametersatz 4->f<> | 018.131 | 0-10:0.001;blockiert=10.002 | s | tf2 PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 4 | 0 | 4 | SE | 10 | Frequency\f2 | Tdel | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 4 | Frequency\f2 | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | GE | 10.002 | Frequency\f2 | Tdel | Real | 0 | 9999999 | [7 empty] | Frequency\f2 | Tdel | Real |  |  | 0 | 10.002
[16 empty] | SE | 10 | Frequency\df2/dt | Tdel | Real | 1 | 0 | [7 empty] | Frequency\df2/dt | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | GE | 10.002 | Frequency\df2/dt | Tdel | Real | 0 | 9999999 | [7 empty] | Frequency\df2/dt | Tdel | Real |  |  | 0 | 10.002
x018_u002E_135 | Parametersatz 4->f<> | 018.135 | 0.1-10:0.001;blockiert=10.002 | Hz/s | df2/dt PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x018_u002E_147 | E;E | Parameter subset 4;1 | 2 | 3 | SE | 10 | Frequency\df2/dt | dFset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Frequency\df2/dt | outserv | Real | E | 1 | 0 | 10.002
[16 empty] | SE | 10 | Frequency\df2/dt | outserv | Real | 0 | 0 | [7 empty] | Frequency\df2/dt | dFset | Real |  |  | 1 | 0
[16 empty] | GE | 10.002 | Frequency\df2/dt | outserv | Real | 0 | 1
x018_u002E_171 | Parametersatz 4->f<> | 018.171 | f¦0;f mit df/dt¦1;f m. Delta f/Delta t¦2 |  | Betriebsart f3 PS4 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real | 1 | x003_u002E_060 | E | Parameter subset 4 | 0 | 1 | E | 0 | Frequency\df3/dt | outserv | Real | 0 | 1 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Frequency\f3 | outserv | Real | E | 1 | 0 | 0
[30 empty] | Frequency\df3/dt | outserv | Real | E | 1 | 0 | 0
[30 empty] | Frequency\df3/dt | outserv | Real |  |  | 0 | 1
x018_u002E_151 | Parametersatz 4->f<> | 018.151 | 40-70:0.01;blockiert=70.02 | Hz | f3 PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 4 | 49.8 | 3 | SE | 70 | Frequency\f3 | Fset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Frequency\f3 | outserv | Real | E | 1 | 0 | 70.02
[16 empty] | SE | 70 | Frequency\f3 | outserv | Real | 0 | 0 | [7 empty] | Frequency\f3 | Fset | Real |  |  | 1 | 0
[16 empty] | GE | 70.02 | Frequency\f3 | outserv | Real | 0 | 1
x018_u002E_155 | Parametersatz 4->f<> | 018.155 | 0-10:0.001;blockiert=10.002 | s | tf3 PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 4 | 0 | 4 | SE | 10 | Frequency\f3 | Tdel | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 4 | Frequency\f3 | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | GE | 10.002 | Frequency\f3 | Tdel | Real | 0 | 9999999 | [7 empty] | Frequency\f3 | Tdel | Real |  |  | 0 | 10.002
[16 empty] | SE | 10 | Frequency\df3/dt | Tdel | Real | 1 | 0 | [7 empty] | Frequency\df3/dt | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | GE | 10.002 | Frequency\df3/dt | Tdel | Real | 0 | 9999999 | [7 empty] | Frequency\df3/dt | Tdel | Real |  |  | 0 | 10.002
x018_u002E_159 | Parametersatz 4->f<> | 018.159 | 0.1-10:0.001;blockiert=10.002 | Hz/s | df3/dt PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x018_u002E_171 | E;E | Parameter subset 4;1 | 2 | 3 | SE | 10 | Frequency\df3/dt | dFset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Frequency\df3/dt | outserv | Real | E | 1 | 0 | 10.002
[16 empty] | SE | 10 | Frequency\df3/dt | outserv | Real | 0 | 0 | [7 empty] | Frequency\df3/dt | dFset | Real |  |  | 1 | 0
[16 empty] | GE | 10.002 | Frequency\df3/dt | outserv | Real | 0 | 1
x018_u002E_195 | Parametersatz 4->f<> | 018.195 | f¦0;f mit df/dt¦1;f m. Delta f/Delta t¦2 |  | Betriebsart f4 PS4 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real | 1 | x003_u002E_060 | E | Parameter subset 4 | 0 | 1 | E | 0 | Frequency\df4/dt | outserv | Real | 0 | 1 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Frequency\f4 | outserv | Real | E | 1 | 0 | 0
[30 empty] | Frequency\df4/dt | outserv | Real | E | 1 | 0 | 0
[30 empty] | Frequency\df4/dt | outserv | Real |  |  | 0 | 1
x018_u002E_175 | Parametersatz 4->f<> | 018.175 | 40-70:0.01;blockiert=70.02 | Hz | f4 PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 4 | 49.8 | 3 | SE | 70 | Frequency\f4 | Fset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Frequency\f4 | outserv | Real | E | 1 | 0 | 70.02
[16 empty] | SE | 70 | Frequency\f4 | outserv | Real | 0 | 0 | [7 empty] | Frequency\f4 | Fset | Real |  |  | 1 | 0
[16 empty] | GE | 70.02 | Frequency\f4 | outserv | Real | 0 | 1
x018_u002E_179 | Parametersatz 4->f<> | 018.179 | 0-10:0.001;blockiert=10.002 | s | tf4 PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060 | E | Parameter subset 4 | 0 | 4 | SE | 10 | Frequency\f4 | Tdel | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 4 | Frequency\f4 | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | GE | 10.002 | Frequency\f4 | Tdel | Real | 0 | 9999999 | [7 empty] | Frequency\f4 | Tdel | Real |  |  | 0 | 10.002
[16 empty] | SE | 10 | Frequency\df4/dt | Tdel | Real | 1 | 0 | [7 empty] | Frequency\df4/dt | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | GE | 10.002 | Frequency\df4/dt | Tdel | Real | 0 | 9999999 | [7 empty] | Frequency\df4/dt | Tdel | Real |  |  | 0 | 10.002
x018_u002E_183 | Parametersatz 4->f<> | 018.183 | 0.1-10:0.001;blockiert=10.002 | Hz/s | df4/dt PS4 | Real | Parameter__Funktionsparameter |  |  | 1 | x003_u002E_060;x018_u002E_195 | E;E | Parameter subset 4;1 | 2 | 3 | SE | 10 | Frequency\df4/dt | dFset | Real | 1 | 0 | 1 | x003_u002E_060 |  |  | E | Parameter subset 4 | 2 | Frequency\df4/dt | outserv | Real | E | 1 | 0 | 10.002
[16 empty] | SE | 10 | Frequency\df4/dt | outserv | Real | 0 | 0 | [7 empty] | Frequency\df4/dt | dFset | Real |  |  | 1 | 0
[16 empty] | GE | 10.002 | Frequency\df4/dt | outserv | Real | 0 | 1
_END_