## Mapping
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37
StationWare | [6 empty] | Common |  |  | Import | [12 empty] | Export
[8 empty] | Enumeration |  | Pre-Condition |  |  |  |  | Instruction | [7 empty] | Pre-Condition | [5 empty] | Instruction
Key | Chapter | Display name | Range | Unit | Description | Type | Group | Mapping | Type |  | Setting | Operator | Value | Default |  | Operator | Value | Target | Parameter | Type | Scale | Offset |  | Source | Parameter | Type | Operator | Value |  | Source | Parameter | Type | Operator | Value | Scale | Offset
x056_u002E_014 | DIST | 056.014 | ohne¦0;mit¦1 |  | Fkt.gruppe DIST |  | Parameter__Konfig_parameter | 1;0 | Real |  |  |  |  | 1 | 6 | E | 1 | Distance Circular | outserv | Real | 0 | 1
[16 empty] | E | 1 | Distance Polygonal | outserv | Real | 0 | 1
[18 empty] | Distance Polygonal\Z7 | outserv | Real | 0 | 1
[18 empty] | Distance Circular\Z7 | outserv | Real | 0 | 1
[18 empty] | Distance Polygonal\Z8 | outserv | Real | 0 | 1
[18 empty] | Distance Circular\Z8 | outserv | Real | 0 | 1
x056_u002E_004 | SV | 056.004 | ohne¦0;mit¦1 |  | Fkt.gruppe SV | Enum | Parameter__Konfig_parameter | 1;0 | Real |  |  |  |  | 1 | 4 | E | 1 | Distance Circular\PSIG Receive | outserv | Real | 0 | 1
[16 empty] | E | 1 | Distance Circular\PSIG Send | outserv | Real | 0 | 1
[16 empty] | E | 1 | Distance Polygonal\PSIG Receive | outserv | Real | 0 | 1
[16 empty] | E | 1 | Distance Polygonal\PSIG Send | outserv | Real | 0 | 1
x056_u002E_008 | UMZ | 056.008 | ohne¦0;mit¦1 |  | Fkt.gruppe UMZ | Enum | Parameter__Konfig_parameter | 1;0 | Real |  |  |  |  | 1 | 12 | E | 1 | Overcurrent\I> | outserv | Real | 0 | 1
[16 empty] | E | 1 | Overcurrent\I>> | outserv | Real | 0 | 1
[16 empty] | E | 1 | Overcurrent\I>>> | outserv | Real | 0 | 1
[16 empty] | E | 1 | Overcurrent\I>>>> | outserv | Real | 0 | 1
[16 empty] | E | 1 | Overcurrent\IN> | outserv | Real | 0 | 1
[16 empty] | E | 1 | Overcurrent\IN>> | outserv | Real | 0 | 1
[16 empty] | E | 1 | Overcurrent\IN>>> | outserv | Real | 0 | 1
[16 empty] | E | 1 | Overcurrent\IN>>>> | outserv | Real | 0 | 1
[16 empty] | E | 1 | Overcurrent\Ineg> | outserv | Real | 0 | 1
[16 empty] | E | 1 | Overcurrent\Ineg>> | outserv | Real | 0 | 1
[16 empty] | E | 1 | Overcurrent\Ineg>>> | outserv | Real | 0 | 1
[16 empty] | E | 1 | Overcurrent\Ineg>>>> | outserv | Real | 0 | 1
x056_u002E_009 | AMZ | 056.009 | ohne¦0;mit¦1 |  | Fkt.gruppe AMZ | Enum | Parameter__Konfig_parameter | 1;0 | Real |  |  |  |  | 1 | 3 | E | 1 | Overcurrent\IDMT P | outserv | Real | 0 | 1
[16 empty] | E | 1 | Overcurrent\IDMT N | outserv | Real | 0 | 1
[16 empty] | E | 1 | Overcurrent\IDMT neg | outserv | Real | 0 | 1
x056_u002E_010 | U<> | 056.010 | ohne¦0;mit¦1 |  | Fkt.gruppe U<> | Enum | Parameter__Konfig_parameter | 1;0 | Real |  |  |  |  | 1 | 5 | E | 1 | Voltage | outserv | Real | 0 | 1
[18 empty] | Voltage\V<<< LE | outserv | Real | 0 | 1
[18 empty] | Voltage\V<<< LL | outserv | Real | 0 | 1
[18 empty] | Voltage\V>>> LE | outserv | Real | 0 | 1
[18 empty] | Voltage\V>>> LL | outserv | Real | 0 | 1
x056_u002E_033 | f<> | 056.033 | ohne¦0;mit¦1 |  | Fkt.gruppe f<> | Enum | Parameter__Konfig_parameter | 1;0 | Real |  |  |  |  | 1 | 2 | E | 1 | Frequency | outserv | Real | 0 | 1
[18 empty] | Frequency\f5 | outserv | Real | 0 | 1
x010_u002E_009 | Global->GRUND | 010.009 | 50-130:1 | V | Unom Wandler sek. | Real | Parameter__Funktionsparameter | [6 empty] | 100 | 4 |  |  | Measurement | Unom | Real | 1 | 0 | [7 empty] | Measurement | Unom | Real |  |  | 1 | 0
[18 empty] | Measurement Delta | Unom | Real | 1 | 0
[18 empty] | Measurement Sequence | Unom | Real | 1 | 0
[18 empty] | Measurement Frequency | Unom | Real | 1 | 0
x010_u002E_028 | Global->GRUND | 010.028 | 50-130:1 | V | UNE,nom Wandler sek. | Real | Parameter__Funktionsparameter | [6 empty] | 100 |  |  |  | Measurement Neutral | Unom | Real | 1 | 0 | [7 empty] | Measurement Neutral | Unom | Real |  |  | 1 | 0
x010_u002E_030 | Global->GRUND | 010.030 | 50 Hz¦0;60 Hz¦1 | Hz | Nennfrequenz fnom | Enum | Parameter__Funktionsparameter | 0;1 | Real
x018_u002E_202 | Hauptfunktionen->f<> | 018.202 | Spannung U1E¦0;Spannung U2E¦1;Spannung U3E¦2;Spannung U12¦3;Spannung U23¦4;Spannung U31¦5 |  | Meßspannungsauswahl | Enum | Parameter__Funktionsparameter | 3;4;5;0;1;2 | Real |  |  |  |  | 0 |  |  |  | Measurement Frequency | imeasv | Real | 1 | 0 | [7 empty] | Measurement Frequency | imeasv | Real |  |  | 1 | 0
x018_u002E_201 | Hauptfunktionen->f<> | 018.201 | 3-6:1 | Perioden | Auswertezeit | Real | Parameter__Funktionsparameter |  |  |  | x010_u002E_030 | E | 0 | 4 |  |  |  | Measurement Frequency | Tfe | Real | 0.02 | 0 |  | x010_u002E_030 |  |  | E | 0 |  | Measurement Frequency | Tfe | Real |  |  | 50 | 0
x031_u002E_073 | Hauptfunktionen->DIST | 031.073 | nein¦0;ja¦1 |  | eingeschaltet BED | Enum | Parameter__Funktionsparameter | 1;0 | Real |  | x056_u002E_014 | E | 0 | 0 | 2 | E | 1 | Distance Circular | outserv | Real | 0 | 1 |  | x056_u002E_014 |  |  | E | 0 | 2 | Distance Circular\Starting | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Distance Polygonal | outserv | Real | 0 | 1 | [7 empty] | Distance Polygonal\Starting | outserv | Real |  |  | 1 | 0
x003_u002E_060 | Global->PSU | 003.060 | Parametersatz 1¦0;Parametersatz 2¦1;Parametersatz 3¦2;Parametersatz 4¦3 |  | Auswahl PS BED | Enum | Parameter__Funktionsparameter | 1;2;3;4 | Real |  |  |  |  | 1
x010_u002E_048 | Parametersatz 1->GRUND | 010.048 | niederohmig geerdet¦0;isol/komp m.Anreg.LE¦1;isol/komp o.Anreg.LE¦2;Kurzzeiterdung¦3 |  | Sternpunktbeh. PS1 | Enum | Parameter__Funktionsparameter | 0;1;2;3;4 | Real |  | x003_u002E_060 | E | 1 | 0 | 4 | E | 0 | Distance Circular\Starting | isysstar | Real | 0 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Circular\Starting | isysstar | Real | E | 0 | 1 | 0
[16 empty] | E | 0 | Distance Polygonal\Starting | isysstar | Real | 0 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Polygonal\Starting | isysstar | Real | E | 0 | 1 | 0
[16 empty] | NE | 0 | Distance Circular\Starting | isysstar | Real | 0 | 1
[16 empty] | NE | 0 | Distance Polygonal\Starting | isysstar | Real | 0 | 1
x010_u002E_040 | Parametersatz 1->GRUND | 010.040 | Erde¦0;LvE=f(Imittel,Imax)¦1 |  | Mitnahme bei 1p PS1 | Enum | Parameter__Funktionsparameter | 0;1 | Real |  | x003_u002E_060 | E | 1 | 0 | 2 |  |  | Distance Circular\Starting | itransf1p | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Circular\Starting | itransf1p | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | itransf1p | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Polygonal\Starting | itransf1p | Real |  |  | 1 | 0
x010_u002E_054 | Parametersatz 1->DIST | 010.054 | 0.1-20:0.01 | Inom | I>> PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 |  |  | Distance Circular\Starting | IMM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Circular\Starting | IMM | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | IMM | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Polygonal\Starting | IMM | Real |  |  | 1 | 0
x010_u002E_068 | Parametersatz 1->DIST | 010.068 | 0.1-1:0.01 | Inom | I> (IF)(max.Ber.)PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 0.2 | 2 |  |  | Distance Circular\Starting | IM1 | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;1 | 2 | Distance Circular\Starting | IM1 | Real | GE | 0.1 | 1 | 0
[18 empty] | Distance Polygonal\Starting | IM1 | Real | 1 | 0 | [13 empty] | 0.1
[24 empty] | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;1 | 2 | Distance Polygonal\Starting | IM1 | Real | GE | 0.1 | 1 | 0
0.1
x010_u002E_119 | Parametersatz 1->DIST | 010.119 | 0.05-1:0.01 | Inom | I> (IF)(emp.Ber.)PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 0.2 | 2 |  |  | Distance Circular\Starting | IM2 | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Circular\Starting | IM2 | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | IM2 | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Polygonal\Starting | IM2 | Real |  |  | 1 | 0
x010_u002E_067 | Parametersatz 1->DIST | 010.067 | ohne U<-Anregung¦0;mit U<-Anreg. nur LE¦1;mit U<-Anreg. LE, LL¦2 |  | Betriebsart U< PS1 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 1 | 2 | 8 | E | 0 | Distance Circular\Starting | iopt_u | Real | 0 | 0 | 4 | Distance Circular;Distance Circular\Starting;x003_u002E_060 | outserv;iopt_u | Real | E;E;E | 0;0;1 | [7 empty] | 0
[16 empty] | E | 0 | Distance Polygonal\Starting | iopt_u | Real | 0 | 0 |  | Distance Circular;Distance Circular\Starting;x003_u002E_060 | outserv;iopt_u | Real | E;E;E | 0;1;1 | 2 | Distance Circular\Starting | iVOpMode | Real | E | 0 | 0 | 1
[16 empty] | NE | 0 | Distance Circular\Starting | iopt_u | Real | 0 | 1 | [7 empty] | Distance Circular\Starting | iVOpMode | Real | E | 1 | 0 | 2
[16 empty] | NE | 0 | Distance Polygonal\Starting | iopt_u | Real | 0 | 1 |  | Distance Polygonal;Distance Polygonal\Starting;x003_u002E_060 | outserv;iopt_u | Real | E;E;E | 0;0;1 | [7 empty] | 0
[16 empty] | E | 1 | Distance Circular\Starting | iVOpMode | Real | 0 | 0 |  | Distance Polygonal;Distance Polygonal\Starting;x003_u002E_060 | outserv;iopt_u | Real | E;E;E | 0;1;1 | 2 | Distance Polygonal\Starting | iVOpMode | Real | E | 0 | 0 | 1
[16 empty] | E | 1 | Distance Polygonal\Starting | iVOpMode | Real | 0 | 0 | [7 empty] | Distance Polygonal\Starting | iVOpMode | Real | E | 1 | 0 | 2
[16 empty] | E | 2 | Distance Circular\Starting | iVOpMode | Real | 0 | 1
[16 empty] | E | 2 | Distance Polygonal\Starting | iVOpMode | Real | 0 | 1
x010_u002E_069 | Parametersatz 1->DIST | 010.069 | 0.1-0.9:0.01 | Unom(/©3) | U< PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 0.7 | 2 |  |  | Distance Circular\Starting | Um | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Circular\Starting | Um | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | Um | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Polygonal\Starting | Um | Real |  |  | 1 | 0
x010_u002E_066 | Parametersatz 1->DIST | 010.066 | ohne Z<-Anregung¦0;mit Z<-Anreg. nur LE¦1;mit Z<-Anreg. LE, LL¦2 |  | Betriebsart Z< PS1 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 1 | 2 | 8 | E | 0 | Distance Circular\Starting | iopt_z | Real | 0 | 0 | 4 | Distance Circular;Distance Circular\Starting;x003_u002E_060 | outserv;iopt_z | Real | E;E;E | 0;0;1 | [7 empty] | 0
[16 empty] | E | 0 | Distance Polygonal\Starting | iopt_z | Real | 0 | 0 |  | Distance Circular;Distance Circular\Starting;x003_u002E_060 | outserv;iopt_z | Real | E;E;E | 0;1;1 | 2 | Distance Circular\Starting | iZOpMode | Real | E | 0 | 0 | 1
[16 empty] | NE | 0 | Distance Circular\Starting | iopt_z | Real | 0 | 1 | [7 empty] | Distance Circular\Starting | iZOpMode | Real | E | 1 | 0 | 2
[16 empty] | NE | 0 | Distance Polygonal\Starting | iopt_z | Real | 0 | 1 |  | Distance Polygonal;Distance Polygonal\Starting;x003_u002E_060 | outserv;iopt_z | Real | E;E;E | 0;0;1 | [7 empty] | 0
[16 empty] | E | 1 | Distance Circular\Starting | iZOpMode | Real | 0 | 0 |  | Distance Polygonal;Distance Polygonal\Starting;x003_u002E_060 | outserv;iopt_z | Real | E;E;E | 0;1;1 | 2 | Distance Polygonal\Starting | iZOpMode | Real | E | 0 | 0 | 1
[16 empty] | E | 1 | Distance Polygonal\Starting | iZOpMode | Real | 0 | 0 | [7 empty] | Distance Polygonal\Starting | iZOpMode | Real | E | 1 | 0 | 2
[16 empty] | E | 2 | Distance Circular\Starting | iZOpMode | Real | 0 | 1
[16 empty] | E | 2 | Distance Polygonal\Starting | iZOpMode | Real | 0 | 1
x010_u002E_050 | Parametersatz 1->DIST | 010.050 | 0.1-300:0.01 | — | Xv PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 10 | 2 |  |  | Distance Circular\Starting | Xfw | Real | 0.2 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;1 | 2 | Distance Circular\Starting | Xfw | Real | SE | 60 | 5 | 0
[18 empty] | Distance Polygonal\Starting | Xfw | Real | 0.2 | 0 | [13 empty] | 300
[24 empty] | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;1 | 2 | Distance Polygonal\Starting | Xfw | Real | SE | 60 | 5 | 0
300
x010_u002E_051 | Parametersatz 1->DIST | 010.051 | 0.1-300:0.01 | — | Rv,LE PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 10 | 2 |  |  | Distance Circular\Starting | RfPG | Real | 0.2 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;1 | 2 | Distance Circular\Starting | RfPG | Real | SE | 60 | 5 | 0
[18 empty] | Distance Polygonal\Starting | RfPG | Real | 0.2 | 0 | [13 empty] | 300
[24 empty] | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;1 | 2 | Distance Polygonal\Starting | RfPG | Real | SE | 60 | 5 | 0
300
x010_u002E_052 | Parametersatz 1->DIST | 010.052 | 0.1-300:0.01 | — | Rv,LL PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 10 | 2 |  |  | Distance Circular\Starting | RfPP | Real | 0.2 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;1 | 2 | Distance Circular\Starting | RfPP | Real | SE | 60 | 5 | 0
[18 empty] | Distance Polygonal\Starting | RfPP | Real | 0.2 | 0 | [13 empty] | 300
[24 empty] | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;1 | 2 | Distance Polygonal\Starting | RfPP | Real | SE | 60 | 5 | 0
300
x010_u002E_063 | Parametersatz 1->DIST | 010.063 | 15-65:1 | ° | ß PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 30 | 2 |  |  | Distance Circular\Starting | Beta | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Circular\Starting | Beta | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | Beta | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Polygonal\Starting | Beta | Real |  |  | 1 | 0
x010_u002E_101 | Parametersatz 1->DIST | 010.101 | 0-300:0.01 | — | Zv,LE PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 0 | 2 |  |  | Distance Circular\Starting | ZfPG | Real | 0.2 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;1 | 2 | Distance Circular\Starting | ZfPG | Real | SE | 60 | 5 | 0
[18 empty] | Distance Polygonal\Starting | ZfPG | Real | 0.2 | 0 | [13 empty] | 300
[24 empty] | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;1 | 2 | Distance Polygonal\Starting | ZfPG | Real | SE | 60 | 5 | 0
300
x010_u002E_105 | Parametersatz 1->DIST | 010.105 | 0-300:0.01 | — | Zv,LL PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 0 | 2 |  |  | Distance Circular\Starting | ZfPP | Real | 0.2 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;1 | 2 | Distance Circular\Starting | ZfPP | Real | SE | 60 | 5 | 0
[18 empty] | Distance Polygonal\Starting | ZfPP | Real | 0.2 | 0 | [13 empty] | 300
[24 empty] | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;1 | 2 | Distance Polygonal\Starting | ZfPP | Real | SE | 60 | 5 | 0
300
x010_u002E_053 | Parametersatz 1->DIST | 010.053 | 0.1-4:0.01 |  | Zr/Zv PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 0.5 | 2 |  |  | Distance Circular\Starting | ZbwZfw | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;1 | 2 | Distance Circular\Starting | ZbwZfw | Real | GE | 0.1 | 1 | 0
[18 empty] | Distance Polygonal\Starting | ZbwZfw | Real | 1 | 0 | [13 empty] | 0.1
[24 empty] | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;1 | 2 | Distance Polygonal\Starting | ZbwZfw | Real | GE | 0.1 | 1 | 0
0.1
x010_u002E_055 | Parametersatz 1->DIST | 010.055 | 0.1-2:0.01 | Inom | IE> (max.Ber.) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 0.2 | 2 |  |  | Distance Circular\Starting | INMM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;1 | 2 | Distance Circular\Starting | INMM | Real | GE | 0.1 | 1 | 0
[18 empty] | Distance Polygonal\Starting | INMM | Real | 1 | 0 | [13 empty] | 0.1
[24 empty] | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;1 | 2 | Distance Polygonal\Starting | INMM | Real | GE | 0.1 | 1 | 0
0.1
x010_u002E_123 | Parametersatz 1->DIST | 010.123 | 0.05-2:0.01 | Inom | IE> (emp.Ber.) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 0.2 | 2 |  |  | Distance Circular\Starting | INM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Circular\Starting | INM | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | INM | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Polygonal\Starting | INM | Real |  |  | 1 | 0
x010_u002E_057 | Parametersatz 1->DIST | 010.057 | 0-0.5:0.001 | s | tIE> PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 0.1 | 2 |  |  | Distance Circular\Starting | tINM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Circular\Starting | tINM | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | tINM | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Polygonal\Starting | tINM | Real |  |  | 1 | 0
x010_u002E_056 | Parametersatz 1->DIST | 010.056 | 0.02-1:0.01 | Unom/©3 | UNE> PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 0.1 | 2 |  |  | Distance Circular\Starting | VNGM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;1 | 2 | Distance Circular\Starting | VNGM | Real | GE | 0.02 | 1 | 0
[18 empty] | Distance Polygonal\Starting | VNGM | Real | 1 | 0 | [13 empty] | 0.02
[24 empty] | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;1 | 2 | Distance Polygonal\Starting | VNGM | Real | GE | 0.02 | 1 | 0
0.02
x010_u002E_062 | Parametersatz 1->DIST | 010.062 | 0.2-1:0.01 | Unom/©3 | UNE>> PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 0.5 | 2 |  |  | Distance Circular\Starting | VNGMM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Circular\Starting | VNGMM | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | VNGMM | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Polygonal\Starting | VNGMM | Real |  |  | 1 | 0
x010_u002E_061 | Parametersatz 1->DIST | 010.061 | 0-60:0.001 | s | tUNE>> PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 |  |  | Distance Circular\Starting | tVNGMM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Circular\Starting | tVNGMM | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | tVNGMM | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Polygonal\Starting | tVNGMM | Real |  |  | 1 | 0
x012_u002E_037 | Parametersatz 1->DIST | 012.037 | 0-8:0.01 |  | Betrag kE PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 |  |  | Distance Circular\Polarisation | k0 | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Circular\Polarisation | k0 | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Polarisation | k0 | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Polygonal\Polarisation | k0 | Real |  |  | 1 | 0
x012_u002E_036 | Parametersatz 1->DIST | 012.036 | -180-180:1 | ° | Winkel kE PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 0 | 2 |  |  | Distance Circular\Polarisation | phik0 | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Circular\Polarisation | phik0 | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Polarisation | phik0 | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Polygonal\Polarisation | phik0 | Real |  |  | 1 | 0
x012_u002E_040 | Parametersatz 1->DIST | 012.040 | Kreis¦0;Polygon¦1 |  | Kennlinientyp PS1 | Enum | Parameter__Funktionsparameter | 0;1 | Real |  | x056_u002E_014;x031_u002E_073;x003_u002E_060 | E;E;E | 0;0;1 | 1 | 4 | E | 0 | Distance Circular | outserv | Real | 0 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Distance Circular | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 0 | Distance Polygonal | outserv | Real | 0 | 1 | [13 empty] | 1
[16 empty] | E | 1 | Distance Circular | outserv | Real | 0 | 1
[16 empty] | E | 1 | Distance Polygonal | outserv | Real | 0 | 0
x012_u002E_001 | Parametersatz 1->DIST | 012.001 | 0.1-200:0.01 | — | X1 (Polygon) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 10 |  |  |  | Distance Polygonal\Z1 | Xmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Polygonal\Z1 | Xmax | Real | SE | 40 | 5 | 0
200
x012_u002E_002 | Parametersatz 1->DIST | 012.002 | 0.1-200:0.01 | — | X2 (Polygon) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 20 |  |  |  | Distance Polygonal\Z2 | Xmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Polygonal\Z2 | Xmax | Real | SE | 40 | 5 | 0
200
x012_u002E_003 | Parametersatz 1->DIST | 012.003 | 0.1-200:0.01 | — | X3 (Polygon) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 30 |  |  |  | Distance Polygonal\Z3 | Xmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Polygonal\Z3 | Xmax | Real | SE | 40 | 5 | 0
200
x012_u002E_004 | Parametersatz 1->DIST | 012.004 | 0.1-200:0.01 | — | X4 (Polygon) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 40 |  |  |  | Distance Polygonal\Z4 | Xmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Polygonal\Z4 | Xmax | Real | SE | 40 | 5 | 0
200
x012_u002E_100 | Parametersatz 1->DIST | 012.100 | 0.1-200:0.01 | — | X5 (Polygon) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 50 |  |  |  | Distance Polygonal\Z5 | Xmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Polygonal\Z5 | Xmax | Real | SE | 40 | 5 | 0
200
x012_u002E_104 | Parametersatz 1->DIST | 012.104 | 0.1-200:0.01 | — | X6 (Polygon) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 60 |  |  |  | Distance Polygonal\Z6 | Xmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Polygonal\Z6 | Xmax | Real | SE | 40 | 5 | 0
200
x012_u002E_005 | Parametersatz 1->DIST | 012.005 | 0.1-200:0.01 | — | R1,LE (Polygon) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 10 |  |  |  | Distance Polygonal\Z1 | REmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Polygonal\Z1 | REmax | Real | SE | 40 | 5 | 0
200
x012_u002E_006 | Parametersatz 1->DIST | 012.006 | 0.1-200:0.01 | — | R1,LL (Polygon) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 10 |  |  |  | Distance Polygonal\Z1 | Rmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Polygonal\Z1 | Rmax | Real | SE | 40 | 5 | 0
200
x012_u002E_007 | Parametersatz 1->DIST | 012.007 | 0.1-200:0.01 | — | R2,LE (Polygon) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 20 |  |  |  | Distance Polygonal\Z2 | REmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Polygonal\Z2 | REmax | Real | SE | 40 | 5 | 0
200
x012_u002E_008 | Parametersatz 1->DIST | 012.008 | 0.1-200:0.01 | — | R2,LL (Polygon) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 20 |  |  |  | Distance Polygonal\Z2 | Rmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Polygonal\Z2 | Rmax | Real | SE | 40 | 5 | 0
200
x012_u002E_009 | Parametersatz 1->DIST | 012.009 | 0.1-200:0.01 | — | R3,LE (Polygon) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 30 |  |  |  | Distance Polygonal\Z3 | REmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Polygonal\Z3 | REmax | Real | SE | 40 | 5 | 0
200
x012_u002E_010 | Parametersatz 1->DIST | 012.010 | 0.1-200:0.01 | — | R3,LL (Polygon) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 30 |  |  |  | Distance Polygonal\Z3 | Rmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Polygonal\Z3 | Rmax | Real | SE | 40 | 5 | 0
200
x012_u002E_011 | Parametersatz 1->DIST | 012.011 | 0.1-200:0.01 | — | R4,LE (Polygon) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 40 |  |  |  | Distance Polygonal\Z4 | REmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Polygonal\Z4 | REmax | Real | SE | 40 | 5 | 0
200
x012_u002E_012 | Parametersatz 1->DIST | 012.012 | 0.1-200:0.01 | — | R4,LL (Polygon) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 40 |  |  |  | Distance Polygonal\Z4 | Rmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Polygonal\Z4 | Rmax | Real | SE | 40 | 5 | 0
200
x012_u002E_108 | Parametersatz 1->DIST | 012.108 | 0.1-200:0.01 | — | R5,LE (Polygon) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 50 |  |  |  | Distance Polygonal\Z5 | REmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Polygonal\Z5 | REmax | Real | SE | 40 | 5 | 0
200
x012_u002E_112 | Parametersatz 1->DIST | 012.112 | 0.1-200:0.01 | — | R5,LL (Polygon) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 50 |  |  |  | Distance Polygonal\Z5 | Rmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Polygonal\Z5 | Rmax | Real | SE | 40 | 5 | 0
200
x012_u002E_116 | Parametersatz 1->DIST | 012.116 | 0.1-200:0.01 | — | R6,LE (Polygon) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 60 |  |  |  | Distance Polygonal\Z6 | REmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Polygonal\Z6 | REmax | Real | SE | 40 | 5 | 0
200
x012_u002E_120 | Parametersatz 1->DIST | 012.120 | 0.1-200:0.01 | — | R6,LL (Polygon) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 60 |  |  |  | Distance Polygonal\Z6 | Rmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Polygonal\Z6 | Rmax | Real | SE | 40 | 5 | 0
200
x012_u002E_013 | Parametersatz 1->DIST | 012.013 | 40-90:1 | ° | €1 (Polygon) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 75 |  |  |  | Distance Polygonal\Z1 | phi | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Polygonal\Z1 | phi | Real | GE | 40 | 1 | 0
40
x012_u002E_014 | Parametersatz 1->DIST | 012.014 | 40-90:1 | ° | €2 (Polygon) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 75 |  |  |  | Distance Polygonal\Z2 | phi | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Polygonal\Z2 | phi | Real | GE | 40 | 1 | 0
40
x012_u002E_015 | Parametersatz 1->DIST | 012.015 | 40-90:1 | ° | €3 (Polygon) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 75 |  |  |  | Distance Polygonal\Z3 | phi | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Polygonal\Z3 | phi | Real | GE | 40 | 1 | 0
40
x012_u002E_016 | Parametersatz 1->DIST | 012.016 | 40-90:1 | ° | €4 (Polygon) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 75 |  |  |  | Distance Polygonal\Z4 | phi | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Polygonal\Z4 | phi | Real | GE | 40 | 1 | 0
40
x012_u002E_124 | Parametersatz 1->DIST | 012.124 | 40-90:1 | ° | €5 (Polygon) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 75 |  |  |  | Distance Polygonal\Z5 | phi | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Polygonal\Z5 | phi | Real | GE | 40 | 1 | 0
40
x012_u002E_128 | Parametersatz 1->DIST | 012.128 | 40-90:1 | ° | €6 (Polygon) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 75 |  |  |  | Distance Polygonal\Z6 | phi | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Polygonal\Z6 | phi | Real | GE | 40 | 1 | 0
40
x072_u002E_086 | Parametersatz 1->DIST | 072.086 | -20-20:1 | ° | ‹1 (Polygon) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 0 |  |  |  | Distance Polygonal\Z1 | beta | Real | -1 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\Z1 | beta | Real |  |  | -1 | 0
x072_u002E_087 | Parametersatz 1->DIST | 072.087 | -20-20:1 | ° | ‹2 (Polygon) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 0 |  |  |  | Distance Polygonal\Z2 | beta | Real | -1 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\Z2 | beta | Real |  |  | -1 | 0
x072_u002E_088 | Parametersatz 1->DIST | 072.088 | -20-20:1 | ° | ‹3 (Polygon) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 0 |  |  |  | Distance Polygonal\Z3 | beta | Real | -1 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\Z3 | beta | Real |  |  | -1 | 0
x072_u002E_089 | Parametersatz 1->DIST | 072.089 | -20-20:1 | ° | ‹4 (Polygon) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 0 |  |  |  | Distance Polygonal\Z4 | beta | Real | -1 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\Z4 | beta | Real |  |  | -1 | 0
x012_u002E_156 | Parametersatz 1->DIST | 012.156 | -20-20:1 | ° | ‹5 (Polygon) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 0 |  |  |  | Distance Polygonal\Z5 | beta | Real | -1 | 0 |  | Distance Polygonal;Distance Polygonal\Z5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\Z5 | beta | Real |  |  | -1 | 0
x012_u002E_160 | Parametersatz 1->DIST | 012.160 | -20-20:1 | ° | ‹6 (Polygon) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 0 |  |  |  | Distance Polygonal\Z6 | beta | Real | -1 | 0 |  | Distance Polygonal;Distance Polygonal\Z6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\Z6 | beta | Real |  |  | -1 | 0
x012_u002E_042 | Parametersatz 1->DIST | 012.042 | 0.05-200:0.01 | — | Z1 (Kreis) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 10 |  |  |  | Distance Circular\Z1 | Zm | Real | 0.2 | 0 |  | Distance Circular;Distance Circular\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Circular\Z1 | Zm | Real | SE | 40 | 5 | 0
200
x012_u002E_043 | Parametersatz 1->DIST | 012.043 | 0.05-200:0.01 | — | Z2 (Kreis) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 20 |  |  |  | Distance Circular\Z2 | Zm | Real | 0.2 | 0 |  | Distance Circular;Distance Circular\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Circular\Z2 | Zm | Real | SE | 40 | 5 | 0
200
x012_u002E_044 | Parametersatz 1->DIST | 012.044 | 0.05-200:0.01 | — | Z3 (Kreis) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 30 |  |  |  | Distance Circular\Z3 | Zm | Real | 0.2 | 0 |  | Distance Circular;Distance Circular\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Circular\Z3 | Zm | Real | SE | 40 | 5 | 0
200
x012_u002E_045 | Parametersatz 1->DIST | 012.045 | 0.05-200:0.01 | — | Z4 (Kreis) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 40 |  |  |  | Distance Circular\Z4 | Zm | Real | 0.2 | 0 |  | Distance Circular;Distance Circular\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Circular\Z4 | Zm | Real | SE | 40 | 5 | 0
200
x012_u002E_148 | Parametersatz 1->DIST | 012.148 | 0.05-200:0.01 | — | Z5 (Kreis) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 50 |  |  |  | Distance Circular\Z5 | Zm | Real | 0.2 | 0 |  | Distance Circular;Distance Circular\Z5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Circular\Z5 | Zm | Real | SE | 40 | 5 | 0
200
x012_u002E_152 | Parametersatz 1->DIST | 012.152 | 0.05-200:0.01 | — | Z6 (Kreis) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 60 |  |  |  | Distance Circular\Z6 | Zm | Real | 0.2 | 0 |  | Distance Circular;Distance Circular\Z6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Circular\Z6 | Zm | Real | SE | 40 | 5 | 0
200
x072_u002E_090 | Parametersatz 1->DIST | 072.090 | 10-90:1 | ° | €1 (Kreis) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 75 | 2 |  |  | Distance Circular\Z1 | arcalpha | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Circular\Z1 | arcalpha | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z1E | arcalpha | Real | 1 | 0
x072_u002E_095 | Parametersatz 1->DIST | 072.095 | 10-90:1 | ° | €2 (Kreis) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 75 |  |  |  | Distance Circular\Z2 | arcalpha | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Circular\Z2 | arcalpha | Real |  |  | 1 | 0
x072_u002E_096 | Parametersatz 1->DIST | 072.096 | 10-90:1 | ° | €3 (Kreis) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 75 |  |  |  | Distance Circular\Z3 | arcalpha | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Circular\Z3 | arcalpha | Real |  |  | 1 | 0
x072_u002E_099 | Parametersatz 1->DIST | 072.099 | 10-90:1 | ° | €4 (Kreis) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 75 |  |  |  | Distance Circular\Z4 | arcalpha | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Circular\Z4 | arcalpha | Real |  |  | 1 | 0
x012_u002E_164 | Parametersatz 1->DIST | 012.164 | 10-90:1 | ° | €5 (Kreis) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 75 |  |  |  | Distance Circular\Z5 | arcalpha | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Circular\Z5 | arcalpha | Real |  |  | 1 | 0
x012_u002E_168 | Parametersatz 1->DIST | 012.168 | 10-90:1 | ° | €6 (Kreis) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 75 |  |  |  | Distance Circular\Z6 | arcalpha | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Circular\Z6 | arcalpha | Real |  |  | 1 | 0
x012_u002E_038 | Parametersatz 1->DIST | 012.038 | nein¦0;ja¦1 |  | Li.bo.komp. Kr. PS1 | Enum | Parameter__Funktionsparameter | 0;1 | Real |  | x003_u002E_060 | E | 1 | 0 | 7 |  |  | Distance Circular\Z1 | arcen | Real | 1 | 0 | 6 | Distance Circular;Distance Circular\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Circular\Z1 | arcen | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z1E | arcen | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Circular\Z2 | arcen | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z2 | arcen | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Circular\Z3 | arcen | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z3 | arcen | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Circular\Z4 | arcen | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z4 | arcen | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Circular\Z5 | arcen | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z5 | arcen | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Circular\Z6 | arcen | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z6 | arcen | Real | 1 | 0
x012_u002E_023 | Parametersatz 1->DIST | 012.023 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung N1 PS1 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 1 | 0 | 4 | NE | 2 | Distance Circular\Z1 | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Circular\Z1 | idir | Real |  |  | 1 | 0
[16 empty] | NE | 2 | Distance Circular\Z1E | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\Z1 | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z1 | idir | Real | 1 | 0
[18 empty] | Distance Polygonal\Z1E | idir | Real | 1 | 0
x012_u002E_024 | Parametersatz 1->DIST | 012.024 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung N2 PS1 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 1 | 0 |  | NE | 2 | Distance Circular\Z2 | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Circular\Z2 | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z2 | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\Z2 | idir | Real |  |  | 1 | 0
x012_u002E_025 | Parametersatz 1->DIST | 012.025 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung N3 PS1 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 1 | 0 |  | NE | 2 | Distance Circular\Z3 | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Circular\Z3 | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z3 | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\Z3 | idir | Real |  |  | 1 | 0
x012_u002E_026 | Parametersatz 1->DIST | 012.026 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung N4 PS1 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 1 | 0 |  | NE | 2 | Distance Circular\Z4 | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Circular\Z4 | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z4 | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\Z4 | idir | Real |  |  | 1 | 0
x012_u002E_027 | Parametersatz 1->DIST | 012.027 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung N5 PS1 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 1 | 0 |  | NE | 2 | Distance Circular\Z5 | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Circular\Z5 | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z5 | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\Z5 | idir | Real |  |  | 1 | 0
x012_u002E_132 | Parametersatz 1->DIST | 012.132 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung N6 PS1 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 1 | 0 |  | NE | 2 | Distance Circular\Z6 | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Circular\Z6 | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z6 | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\Z6 | idir | Real |  |  | 1 | 0
x012_u002E_136 | Parametersatz 1->DIST | 012.136 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung N7 PS1 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 1 | 0 |  |  |  | Distance Circular\Directional | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Directional;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Circular\Directional | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Directional | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Directional;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\Directional | idir | Real |  |  | 1 | 0
x012_u002E_028 | Parametersatz 1->DIST | 012.028 | 0-60:0.001;blockiert=60.002 | s | t1 PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 0 | 4 | SE | 60 | Distance Circular\T1 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Circular\T1 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Circular\T1 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
[16 empty] | SE | 60 | Distance Polygonal\T1 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Polygonal\T1 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Polygonal\T1 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
x012_u002E_029 | Parametersatz 1->DIST | 012.029 | 0-60:0.001;blockiert=60.002 | s | t2 PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1 | 4 | SE | 60 | Distance Circular\T2 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Circular\T2 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Circular\T2 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
[16 empty] | SE | 60 | Distance Polygonal\T2 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Polygonal\T2 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Polygonal\T2 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
x012_u002E_030 | Parametersatz 1->DIST | 012.030 | 0-60:0.001;blockiert=60.002 | s | t3 PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 2 | 4 | SE | 60 | Distance Circular\T3 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Circular\T3 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Circular\T3 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
[16 empty] | SE | 60 | Distance Polygonal\T3 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Polygonal\T3 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Polygonal\T3 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
x012_u002E_031 | Parametersatz 1->DIST | 012.031 | 0-60:0.001;blockiert=60.002 | s | t4 PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 3 | 4 | SE | 60 | Distance Circular\T4 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Circular\T4 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Circular\T4 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
[16 empty] | SE | 60 | Distance Polygonal\T4 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Polygonal\T4 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Polygonal\T4 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
x012_u002E_032 | Parametersatz 1->DIST | 012.032 | 0-60:0.001;blockiert=60.002 | s | t5 PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 4 | 4 | SE | 60 | Distance Circular\T5 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Circular\T5 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Circular\T5 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
[16 empty] | SE | 60 | Distance Polygonal\T5 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Polygonal\T5 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Polygonal\T5 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
x012_u002E_033 | Parametersatz 1->DIST | 012.033 | 0-60:0.001;blockiert=60.002 | s | t6 PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 5 | 4 | SE | 60 | Distance Circular\T6 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Circular\T6 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Circular\T6 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
[16 empty] | SE | 60 | Distance Polygonal\T6 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Polygonal\T6 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Polygonal\T6 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
x012_u002E_140 | Parametersatz 1->DIST | 012.140 | 0-60:0.001;blockiert=60.002 | s | t7 PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 6 | 4 | SE | 60 | Distance Circular\T9 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T9;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Circular\T9 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Circular\T9 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
[16 empty] | SE | 60 | Distance Polygonal\T9 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T9;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Polygonal\T9 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Polygonal\T9 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
x012_u002E_144 | Parametersatz 1->DIST | 012.144 | 0-60:0.001;blockiert=60.002 | s | t8 PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 7 | 4 | SE | 60 | Distance Circular\T10 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T10;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Circular\T10 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Circular\T10 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
[16 empty] | SE | 60 | Distance Polygonal\T10 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T10;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Polygonal\T10 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Polygonal\T10 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
x012_u002E_035 | Parametersatz 1->DIST | 012.035 | 1-450:0.01 |  | kÜ,LL KU PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1.2 | 3 |  |  | Distance Circular\Z1E | kZ | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z1E;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Circular\Z1E | kZ | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z1E | kX | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z1E;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\Z1E | kX | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z1E | kR | Real | 1 | 0
x015_u002E_014 | Parametersatz 1->SV | 015.014 | nein¦0;ja¦1 |  | Freigabe PS1 | Enum | Parameter__Funktionsparameter | 0;1 | String |  | x003_u002E_060 | E | 1 | 0 | 2 |  |  | Distance Circular\PSIG Connect | aDipset | String |  |  | 2 | Distance Circular;Distance Circular\PSIG Connect;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Circular\PSIG Connect | aDipset | String
[18 empty] | Distance Polygonal\PSIG Connect | aDipset | String |  |  |  | Distance Polygonal;Distance Polygonal\PSIG Connect;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\PSIG Connect | aDipset | String
x015_u002E_000 | Parametersatz 1->SV | 015.000 | keine¦0;direkte Schaltermitn¦1;anregeabh. Mitnahme¦2;Meßbereichserweiter.¦3;Freigabeverfahren¦4;Sperrverfahren¦5;GS-Schleife¦6;rückwärtige Verrieg.¦7;Richtungsvergleich¦8 |  | Betriebsart PS1 | Enum | Parameter__Funktionsparameter | ;DIRECT = TRIP;PUTT = TRIP;POTT = TRIP;COMP_RELEASE = TRIP;COMP_BLOCK = TRIP;COMP_PILOT = TRIP; | String |  | x003_u002E_060 | E | 1 | PUTT = TRIP | 4 |  |  | Distance Circular\PSIG Receive | sLogic | String |  |  | 2 | Distance Circular;Distance Circular\PSIG Receive;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Circular\PSIG Receive | sLogic | String
[18 empty] | Distance Circular\PSIG Send | sLogic | String |  |  |  | Distance Polygonal;Distance Polygonal\PSIG Receive;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\PSIG Receive | sLogic | String
[18 empty] | Distance Polygonal\PSIG Receive | sLogic | String
[18 empty] | Distance Polygonal\PSIG Send | sLogic | String
x015_u002E_011 | Parametersatz 1->SV | 015.011 | 0-60:0.001;blockiert=60.002 | s | Startzeit PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 0.08 | 4 | SE | 60 | Distance Circular\PSIG T | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\PSIG T;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Circular\PSIG T | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Circular\PSIG T | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
[16 empty] | SE | 60 | Distance Polygonal\PSIG T | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\PSIG T;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Polygonal\PSIG T | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Polygonal\PSIG T | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
x015_u002E_002 | Parametersatz 1->SV | 015.002 | 0-10:0.001 | s | Rückf.zeit Send. PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 0.25 | 2 |  |  | Distance Circular\PSIG T Reset | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\PSIG T Reset;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Circular\PSIG T Reset | Tdelay | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\PSIG T Reset | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\PSIG T Reset;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\PSIG T Reset | Tdelay | Real |  |  | 1 | 0
x072_u002E_098 | Parametersatz 1->UMZ | 072.098 | nein¦0;ja¦1 |  | Freigabe PS1 | Enum | Parameter__Funktionsparameter | 1;0 | Real |  | x056_u002E_008;x003_u002E_060 | E;E | 0;1 | 1 | 12 |  |  | Overcurrent\I> | outserv | Real | 1 | 0 |  | x056_u002E_008;x003_u002E_060 |  |  | E;E | 0;1 | 12 | Overcurrent\I> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\I>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\I>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\I>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\I>>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\I>>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\I>>>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\IN> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\IN> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\IN>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\IN>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\IN>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\IN>>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\IN>>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\IN>>>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\Ineg> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\Ineg> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\Ineg>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\Ineg>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\Ineg>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\Ineg>>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\Ineg>>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\Ineg>>>> | outserv | Real |  |  | 1 | 0
x072_u002E_007 | Parametersatz 1->UMZ | 072.007 | 0.1-20:0.01 | Inom | I> PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 |  |  | Overcurrent\I> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 3 | Overcurrent\I> | Ipset | Real | G | 20 | 0 | 20
[18 empty] | Overcurrent\I> | idir | Real | 0 | 0 | [7 empty] | Overcurrent\I> | Ipset | Real | S | 0.1 | 0 | 0.1
[30 empty] | Overcurrent\I> | Ipset | Real |  |  | 1 | 0
x072_u002E_008 | Parametersatz 1->UMZ | 072.008 | 0.1-20:0.01 | Inom | I>> PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 |  |  | Overcurrent\I>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 3 | Overcurrent\I>> | Ipset | Real | G | 20 | 0 | 20
[18 empty] | Overcurrent\I>> | idir | Real | 0 | 0 | [7 empty] | Overcurrent\I>> | Ipset | Real | S | 0.1 | 0 | 0.1
[30 empty] | Overcurrent\I>> | Ipset | Real |  |  | 1 | 0
x072_u002E_009 | Parametersatz 1->UMZ | 072.009 | 0.1-20:0.01 | Inom | I>>> PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 |  |  | Overcurrent\I>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 3 | Overcurrent\I>>> | Ipset | Real | G | 20 | 0 | 20
[18 empty] | Overcurrent\I>>> | idir | Real | 0 | 0 | [7 empty] | Overcurrent\I>>> | Ipset | Real | S | 0.1 | 0 | 0.1
[30 empty] | Overcurrent\I>>> | Ipset | Real |  |  | 1 | 0
x072_u002E_010 | Parametersatz 1->UMZ | 072.010 | 0.1-20:0.01 | Inom | I>>>> PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 |  |  | Overcurrent\I>>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 3 | Overcurrent\I>>>> | Ipset | Real | G | 20 | 0 | 20
[18 empty] | Overcurrent\I>>>> | idir | Real | 0 | 0 | [7 empty] | Overcurrent\I>>>> | Ipset | Real | S | 0.1 | 0 | 0.1
[30 empty] | Overcurrent\I>>>> | Ipset | Real |  |  | 1 | 0
x072_u002E_019 | Parametersatz 1->UMZ | 072.019 | 0-30:0.001;blockiert=30.002 | s | tI> PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 | SE | 30 | Overcurrent\I> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Overcurrent\I> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\I> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x072_u002E_020 | Parametersatz 1->UMZ | 072.020 | 0-30:0.001;blockiert=30.002 | s | tI>> PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 | SE | 30 | Overcurrent\I>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Overcurrent\I>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\I>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x072_u002E_021 | Parametersatz 1->UMZ | 072.021 | 0-30:0.001;blockiert=30.002 | s | tI>>> PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 | SE | 30 | Overcurrent\I>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Overcurrent\I>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\I>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x072_u002E_022 | Parametersatz 1->UMZ | 072.022 | 0-30:0.001;blockiert=30.002 | s | tI>>>> PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 | SE | 30 | Overcurrent\I>>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Overcurrent\I>>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\I>>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x072_u002E_011 | Parametersatz 1->UMZ | 072.011 | 0.1-20:0.01 | Inom | Igegen> PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1 |  |  |  | Overcurrent\IN> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\IN> | Ipset | Real |  |  | 1 | 0
x072_u002E_012 | Parametersatz 1->UMZ | 072.012 | 0.1-20:0.01 | Inom | Igegen>> PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1 |  |  |  | Overcurrent\IN>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\IN>> | Ipset | Real |  |  | 1 | 0
x072_u002E_013 | Parametersatz 1->UMZ | 072.013 | 0.1-20:0.01 | Inom | Igegen>>> PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1 |  |  |  | Overcurrent\IN>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\IN>>> | Ipset | Real |  |  | 1 | 0
x072_u002E_014 | Parametersatz 1->UMZ | 072.014 | 0.1-20:0.01 | Inom | Igegen>>>> PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1 |  |  |  | Overcurrent\IN>>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\IN>>>> | Ipset | Real |  |  | 1 | 0
x072_u002E_023 | Parametersatz 1->UMZ | 072.023 | 0-30:0.001;blockiert=30.002 | s | tIgegen> PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 | SE | 30 | Overcurrent\IN> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Overcurrent\IN> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\IN> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x072_u002E_024 | Parametersatz 1->UMZ | 072.024 | 0-30:0.001;blockiert=30.002 | s | tIgegen>> PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 | SE | 30 | Overcurrent\IN>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Overcurrent\IN>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\IN>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x072_u002E_025 | Parametersatz 1->UMZ | 072.025 | 0-30:0.001;blockiert=30.002 | s | tIgegen>>> PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 | SE | 30 | Overcurrent\IN>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Overcurrent\IN>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\IN>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x072_u002E_026 | Parametersatz 1->UMZ | 072.026 | 0-30:0.001;blockiert=30.002 | s | tIgegen>>>> PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 | SE | 30 | Overcurrent\IN>>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Overcurrent\IN>>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\IN>>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x072_u002E_015 | Parametersatz 1->UMZ | 072.015 | 0.1-20:0.01 | Inom | IE> PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1 |  |  |  | Overcurrent\Ineg> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\Ineg> | Ipset | Real |  |  | 1 | 0
x072_u002E_016 | Parametersatz 1->UMZ | 072.016 | 0.1-20:0.01 | Inom | IE>> PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1 |  |  |  | Overcurrent\Ineg>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\Ineg>> | Ipset | Real |  |  | 1 | 0
x072_u002E_017 | Parametersatz 1->UMZ | 072.017 | 0.1-20:0.01 | Inom | IE>>> PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1 |  |  |  | Overcurrent\Ineg>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\Ineg>>> | Ipset | Real |  |  | 1 | 0
x072_u002E_018 | Parametersatz 1->UMZ | 072.018 | 0.1-20:0.01 | Inom | IE>>>> PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1 |  |  |  | Overcurrent\Ineg>>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\Ineg>>>> | Ipset | Real |  |  | 1 | 0
x072_u002E_027 | Parametersatz 1->UMZ | 072.027 | 0-30:0.001;blockiert=30.002 | s | tIE> PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 | SE | 30 | Overcurrent\Ineg> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Overcurrent\Ineg> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\Ineg> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x072_u002E_028 | Parametersatz 1->UMZ | 072.028 | 0-30:0.001;blockiert=30.002 | s | tIE>> PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 | SE | 30 | Overcurrent\Ineg>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Overcurrent\Ineg>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\Ineg>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x072_u002E_029 | Parametersatz 1->UMZ | 072.029 | 0-30:0.001;blockiert=30.002 | s | tIE>>> PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 | SE | 30 | Overcurrent\Ineg>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Overcurrent\Ineg>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\Ineg>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x072_u002E_030 | Parametersatz 1->UMZ | 072.030 | 0-30:0.001;blockiert=30.002 | s | tIE>>>> PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 | SE | 30 | Overcurrent\Ineg>>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Overcurrent\Ineg>>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\Ineg>>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x010_u002E_045 | Parametersatz 1->UMZ | 010.045 | 0.01-0.5:0.001 | Unom/©3 | UNE> PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 0.03 |  |  |  | Overcurrent\Directional N | upolu | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\Directional N | upolu | Real |  |  | 1 | 0
x004_u002E_092 | Parametersatz 1->UMZ | 004.092 | -90-90:1 | ° | Winkel phiE PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 0 |  |  |  | Overcurrent\Directional N | mtau | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\Directional N | mtau | Real |  |  | 1 | 0
x072_u002E_032 | Parametersatz 1->UMZ | 072.032 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung tIE> PS1 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real |  | x003_u002E_060 | E | 1 | 1 |  |  |  | Overcurrent\IN> | idir | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\IN> | idir | Real |  |  | 1 | 0
x072_u002E_033 | Parametersatz 1->UMZ | 072.033 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung tIE>> PS1 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real |  | x003_u002E_060 | E | 1 | 1 |  |  |  | Overcurrent\IN>> | idir | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\IN>> | idir | Real |  |  | 1 | 0
x072_u002E_034 | Parametersatz 1->UMZ | 072.034 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung tIE>>> PS1 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real |  | x003_u002E_060 | E | 1 | 1 |  |  |  | Overcurrent\IN>>> | idir | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\IN>>> | idir | Real |  |  | 1 | 0
x072_u002E_035 | Parametersatz 1->UMZ | 072.035 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung tIE>>>> PS1 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real |  | x003_u002E_060 | E | 1 | 1 |  |  |  | Overcurrent\IN>>>> | idir | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\IN>>>> | idir | Real |  |  | 1 | 0
x072_u002E_000 | Parametersatz 1->AMZ | 072.000 | nein¦0;ja¦1 |  | Freigabe PS1 | Enum | Parameter__Funktionsparameter | 1;0 | Real |  | x056_u002E_009;x003_u002E_060 | E;E | 0;1 | 1 |  |  |  | Overcurrent\IDMT P | outserv | Real | 1 | 0 |  | x056_u002E_009;x003_u002E_060 |  |  | E;E | 0;1 | 3 | Overcurrent\IDMT P | outserv | Real | E | 0 |  | 0
[18 empty] | Overcurrent\IDMT neg | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\IDMT neg | outserv | Real | E | 0 |  | 0
[18 empty] | Overcurrent\IDMT N | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\IDMT N | outserv | Real |  |  | 1 | 0
x072_u002E_050 | Parametersatz 1->AMZ | 072.050 | 0.1-4:0.01;blockiert=4.02 | Inom | IB,L PS1 | Real | Parameter__Funktionsparameter |  |  |  | x072_u002E_000;x003_u002E_060 | E;E | 0;1 | 1 | 4 | SE | 4 | Overcurrent\IDMT P | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Overcurrent\IDMT P | outserv | Real | E | 1 | 0 | 4.02
[16 empty] | SE | 4 | Overcurrent\IDMT P | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\IDMT P | Ipset | Real |  |  | 1 | 0
[16 empty] | G | 4 | Overcurrent\IDMT P | outserv | Real | 0 | 1
[18 empty] | Overcurrent\IDMT KI P | outserv | Real | 0 | 1
x072_u002E_056 | Parametersatz 1->AMZ | 072.056 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Kennlinientyp L PS1 | Enum | Parameter__Funktionsparameter | Definite Time;IEC 255-3 Standard Inverse;IEC 255-3 Very Inverse;IEC 255-3 Extremly Inverse;IEC 255-3 Long-Time Inverse;IEEE C37.112 Moderately Inverse;IEEE C37.112 Very Inverse;IEEE C37.112 Extremely Inverse;ANSI Normally Inverse;ANSI Short-Time Inverse;ANSI Long-Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | [8 empty] | Overcurrent\IDMT P | pcharac |  |  |  |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\IDMT P | pcharac
x072_u002E_053 | Parametersatz 1->AMZ | 072.053 | 0.01-10:0.01 |  | Kennl.fakt. kt,L PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1 |  |  | 2 | Overcurrent\IDMT P | Tpset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\IDMT P | Tpset | Real |  |  | 1 | 0
[18 empty] | Overcurrent\IDMT P | udeftmin | Real | 0 | 0
x072_u002E_059 | Parametersatz 1->AMZ | 072.059 | unverzögert¦0;verzögert gem. Kennl¦1 |  | Rückfallen L PS1 | Enum | Parameter__Funktionsparameter | 0;1 | Real | 3 | x003_u002E_060;x072_u002E_056 | E;SW | 1;IEEE | 0 |  |  |  | Overcurrent\IDMT P | resetdis | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\IDMT P | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x072_u002E_056 | E;SW | 1;ANSI |  |  |  |  | Overcurrent\IDMT P | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | 1 |  |  |  |  | Overcurrent\IDMT P | resetdis | Real | 0 | 0
x072_u002E_062 | Parametersatz 1->AMZ | 072.062 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung L PS1 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real |  | x003_u002E_060 | E | 1 | 1 |  |  |  | Overcurrent\IDMT P | idir | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\IDMT P | idir | Real |  |  | 1 | 0
x072_u002E_051 | Parametersatz 1->AMZ | 072.051 | 0.1-4:0.01;blockiert=4.02 | Inom | IB,gegen PS1 | Real | Parameter__Funktionsparameter |  |  |  | x072_u002E_000;x003_u002E_060 | E;E | 0;1 | 1 | 4 | SE | 4 | Overcurrent\IDMT neg | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 3 | Overcurrent\IDMT neg | outserv | Real | E | 1 | 0 | 4.02
[16 empty] | SE | 4 | Overcurrent\IDMT neg | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\IDMT neg | Ipset | Real | GE | 0.1 | 1 | 0
[16 empty] | G | 4 | Overcurrent\IDMT neg | outserv | Real | 0 | 1 | [13 empty] | 0.1
[18 empty] | Overcurrent\IDMT KI neg | outserv | Real | 0 | 1
x072_u002E_057 | Parametersatz 1->AMZ | 072.057 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Kennl.typ gegen PS1 | Enum | Parameter__Funktionsparameter | Definite Time;IEC 255-3 Standard Inverse;IEC 255-3 Very Inverse;IEC 255-3 Extremly Inverse;IEC 255-3 Long-Time Inverse;IEEE C37.112 Moderately Inverse;IEEE C37.112 Very Inverse;IEEE C37.112 Extremely Inverse;ANSI Normally Inverse;ANSI Short-Time Inverse;ANSI Long-Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | [8 empty] | Overcurrent\IDMT neg | pcharac |  |  |  |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\IDMT neg | pcharac
x072_u002E_054 | Parametersatz 1->AMZ | 072.054 | 0.01-10:0.01 |  | Kennl.f. kt,gegn PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1 |  |  | 2 | Overcurrent\IDMT neg | Tpset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\IDMT neg | Tpset | Real |  |  | 1 | 0
[18 empty] | Overcurrent\IDMT neg | udeftmin | Real | 0 | 0
x072_u002E_060 | Parametersatz 1->AMZ | 072.060 | unverzögert¦0;verzögert gem. Kennl¦1 |  | Rückfallen gegen PS1 | Enum | Parameter__Funktionsparameter | 0;1 | Real | 3 | x003_u002E_060;x072_u002E_057 | E;SW | 1;IEEE | 0 |  |  |  | Overcurrent\IDMT neg | resetdis | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\IDMT neg | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x072_u002E_057 | E;SW | 1;ANSI |  |  |  |  | Overcurrent\IDMT neg | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | 1 |  |  |  |  | Overcurrent\IDMT neg | resetdis | Real | 0 | 0
x072_u002E_052 | Parametersatz 1->AMZ | 072.052 | 0.1-4:0.01;blockiert=4.02 | Inom | IB,E (gerechnet) PS1 | Real | Parameter__Funktionsparameter |  |  |  | x072_u002E_000;x003_u002E_060 | E;E | 0;1 | 1 | 4 | SE | 4 | Overcurrent\IDMT N | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 3 | Overcurrent\IDMT N | outserv | Real | E | 1 | 0 | 4.02
[16 empty] | SE | 4 | Overcurrent\IDMT N | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\IDMT N | Ipset | Real | GE | 0.1 | 1 | 0
[16 empty] | G | 4 | Overcurrent\IDMT N | outserv | Real | 0 | 1 | [13 empty] | 0.1
[18 empty] | Overcurrent\IDMT KI N | outserv | Real | 0 | 1
x072_u002E_058 | Parametersatz 1->AMZ | 072.058 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Kennlinientyp E PS1 | Enum | Parameter__Funktionsparameter | Definite Time;IEC 255-3 Standard Inverse;IEC 255-3 Very Inverse;IEC 255-3 Extremly Inverse;IEC 255-3 Long-Time Inverse;IEEE C37.112 Moderately Inverse;IEEE C37.112 Very Inverse;IEEE C37.112 Extremely Inverse;ANSI Normally Inverse;ANSI Short-Time Inverse;ANSI Long-Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | [8 empty] | Overcurrent\IDMT N | pcharac |  |  |  |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\IDMT N | pcharac
x072_u002E_055 | Parametersatz 1->AMZ | 072.055 | 0.01-10:0.01 |  | Kennl.f. kt,E PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1 |  |  | 2 | Overcurrent\IDMT N | Tpset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\IDMT N | Tpset | Real |  |  | 1 | 0
[18 empty] | Overcurrent\IDMT N | udeftmin | Real | 0 | 0
x072_u002E_061 | Parametersatz 1->AMZ | 072.061 | unverzögert¦0;verzögert gem. Kennl¦1 |  | Rückfallen E PS1 | Enum | Parameter__Funktionsparameter | 0;1 | Real | 3 | x003_u002E_060;x072_u002E_058 | E;SW | 1;IEEE | 0 |  |  |  | Overcurrent\IDMT N | resetdis | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\IDMT N | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x072_u002E_058 | E;SW | 1;ANSI |  |  |  |  | Overcurrent\IDMT N | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | 1 |  |  |  |  | Overcurrent\IDMT N | resetdis | Real | 0 | 0
x072_u002E_064 | Parametersatz 1->AMZ | 072.064 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung E PS1 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real |  | x003_u002E_060 | E | 1 | 1 |  |  |  | Overcurrent\IDMT N | idir | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\IDMT N | idir | Real |  |  | 1 | 0
x076_u002E_000 | Parametersatz 1->U<> | 076.000 | nein¦0;ja¦1 |  | Freigabe PS1 | Enum | Parameter__Funktionsparameter | 1;0 | Real |  | x056_u002E_010;x003_u002E_060 | E;E | 0;1 | 1 |  |  |  | Voltage | outserv | Real | 1 | 0 |  | x056_u002E_010;x003_u002E_060 |  |  | E;E | 0;1 |  | Voltage | outserv | Real |  |  | 1 | 0
x076_u002E_001 | Parametersatz 1->U<> | 076.001 | Dreieck¦0;Stern¦1 |  | Betriebsart PS1 | Enum | Parameter__Funktionsparameter | 0;1 | Real |  | x076_u002E_000;x003_u002E_060 | E;E | 0;1 | 0 | 16 | E | 0 | Voltage\V< LE | outserv | Real | 0 | 1
[16 empty] | E | 0 | Voltage\V< LL | outserv | Real | 0 | 0
[16 empty] | E | 0 | Voltage\V<< LE | outserv | Real | 0 | 1
[16 empty] | E | 0 | Voltage\V<< LL | outserv | Real | 0 | 0
[16 empty] | E | 0 | Voltage\V> LE | outserv | Real | 0 | 1
[16 empty] | E | 0 | Voltage\V> LL | outserv | Real | 0 | 0
[16 empty] | E | 0 | Voltage\V>> LE | outserv | Real | 0 | 1
[16 empty] | E | 0 | Voltage\V>> LL | outserv | Real | 0 | 0
[16 empty] | E | 1 | Voltage\V< LE | outserv | Real | 0 | 0
[16 empty] | E | 1 | Voltage\V< LL | outserv | Real | 0 | 1
[16 empty] | E | 1 | Voltage\V<< LE | outserv | Real | 0 | 0
[16 empty] | E | 1 | Voltage\V<< LL | outserv | Real | 0 | 1
[16 empty] | E | 1 | Voltage\V> LE | outserv | Real | 0 | 0
[16 empty] | E | 1 | Voltage\V> LL | outserv | Real | 0 | 1
[16 empty] | E | 1 | Voltage\V>> LE | outserv | Real | 0 | 0
[16 empty] | E | 1 | Voltage\V>> LL | outserv | Real | 0 | 1
x076_u002E_003 | Parametersatz 1->U<> | 076.003 | 0.2-1.5:0.01;blockiert=1.52 | Unom(/©3) | U> PS1 | Real | Parameter__Funktionsparameter |  |  | 2 | x076_u002E_001;x003_u002E_060 | E;E | 0;1 | 1.1 | 3 | SE | 1.5 | Voltage\V> LL | Uset | Real | 1 | 0 | 2 | x076_u002E_001;x003_u002E_060 |  |  | E;E | 0;1 | 3 | Voltage\V> LL | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V> LL | outserv | Real | 0 | 0 | [7 empty] | Voltage\V> LL | Uset | Real | GE | 0.2 | 1 | 0
[16 empty] | G | 1.5 | Voltage\V> LL | outserv | Real | 0 | 1 | [13 empty] | 0.2
[11 empty] | x076_u002E_001;x003_u002E_060 | E;E | 1;1 |  | 3 | SE | 1.5 | Voltage\V> LE | Uset | Real | 1 | 0 |  | x076_u002E_001;x003_u002E_060 |  |  | E;E | 1;1 | 3 | Voltage\V> LE | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V> LE | outserv | Real | 0 | 0 | [7 empty] | Voltage\V> LE | Uset | Real | GE | 0.2 | 1 | 0
[16 empty] | G | 1.5 | Voltage\V> LE | outserv | Real | 0 | 1 | [13 empty] | 0.2
x076_u002E_004 | Parametersatz 1->U<> | 076.004 | 0.2-1.5:0.01;blockiert=1.52 | Unom(/©3) | U>> PS1 | Real | Parameter__Funktionsparameter |  |  | 2 | x076_u002E_001;x003_u002E_060 | E;E | 0;1 | 1.1 | 3 | SE | 1.5 | Voltage\V>> LL | Uset | Real | 1 | 0 | 2 | x076_u002E_001;x003_u002E_060 |  |  | E;E | 0;1 | 3 | Voltage\V>> LL | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V>> LL | outserv | Real | 0 | 0 | [7 empty] | Voltage\V>> LL | Uset | Real | GE | 0.2 | 1 | 0
[16 empty] | G | 1.5 | Voltage\V>> LL | outserv | Real | 0 | 1 | [13 empty] | 0.2
[11 empty] | x076_u002E_001;x003_u002E_060 | E;E | 1;1 |  | 3 | SE | 1.5 | Voltage\V>> LE | Uset | Real | 1 | 0 |  | x076_u002E_001;x003_u002E_060 |  |  | E;E | 1;1 | 3 | Voltage\V>> LE | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V>> LE | outserv | Real | 0 | 0 | [7 empty] | Voltage\V>> LE | Uset | Real | GE | 0.2 | 1 | 0
[16 empty] | G | 1.5 | Voltage\V>> LE | outserv | Real | 0 | 1 | [13 empty] | 0.2
x076_u002E_005 | Parametersatz 1->U<> | 076.005 | 0-100:0.01;blockiert=100.02 | s | tU> PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1 | 4 | SE | 100 | Voltage\V> LL | Tdel | Real | 1 | 0 | 2 | x076_u002E_001;x003_u002E_060 |  |  | E;E | 0;1 | 2 | Voltage\V> LL | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V> LL | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
[16 empty] | SE | 100 | Voltage\V> LE | Tdel | Real | 1 | 0 |  | x076_u002E_001;x003_u002E_060 |  |  | E;E | 1;1 | 2 | Voltage\V> LE | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V> LE | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x076_u002E_006 | Parametersatz 1->U<> | 076.006 | 0-100:0.01;blockiert=100.02 | s | tU>> PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1 | 4 | SE | 100 | Voltage\V>> LL | Tdel | Real | 1 | 0 |  | x076_u002E_001;x003_u002E_060 |  |  | E;E | 0;1 | 2 | Voltage\V>> LL | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V>> LL | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
[16 empty] | SE | 100 | Voltage\V>> LE | Tdel | Real | 1 | 0 |  | x076_u002E_001;x003_u002E_060 |  |  | E;E | 1;1 | 2 | Voltage\V>> LE | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V>> LE | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x076_u002E_007 | Parametersatz 1->U<> | 076.007 | 0.2-1.5:0.01;blockiert=1.52 | Unom(/©3) | U< PS1 | Real | Parameter__Funktionsparameter |  |  | 2 | x076_u002E_001;x003_u002E_060 | E;E | 0;1 | 0.8 | 3 | SE | 1.5 | Voltage\V< LL | Uset | Real | 1 | 0 | 2 | x076_u002E_001;x003_u002E_060 |  |  | E;E | 0;1 | 2 | Voltage\V< LL | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V< LL | outserv | Real | 0 | 0 | [7 empty] | Voltage\V< LL | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\V< LL | outserv | Real | 0 | 1 |  | x076_u002E_001;x003_u002E_060 |  |  | E;E | 1;1 | 2 | Voltage\V< LE | outserv | Real | E | 1 | 0 | 1.52
[11 empty] | x076_u002E_001;x003_u002E_060 | E;E | 1;1 | 0.8 |  | SE | 1.5 | Voltage\V< LE | Uset | Real | 1 | 0 | [7 empty] | Voltage\V< LE | Uset | Real |  |  | 1 | 0
[16 empty] | SE | 1.5 | Voltage\V< LE | outserv | Real | 0 | 0
[16 empty] | G | 1.5 | Voltage\V< LE | outserv | Real | 0 | 1
x076_u002E_008 | Parametersatz 1->U<> | 076.008 | 0.2-1.5:0.01;blockiert=1.52 | Unom(/©3) | U<< PS1 | Real | Parameter__Funktionsparameter |  |  | 2 | x076_u002E_001;x003_u002E_060 | E;E | 0;1 | 0.8 | 3 | SE | 1.5 | Voltage\V<< LL | Uset | Real | 1 | 0 | 2 | x076_u002E_001;x003_u002E_060 |  |  | E;E | 0;1 | 2 | Voltage\V<< LL | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V<< LL | outserv | Real | 0 | 0 | [7 empty] | Voltage\V<< LL | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\V<< LL | outserv | Real | 0 | 1 |  | x076_u002E_001;x003_u002E_060 |  |  | E;E | 1;1 | 2 | Voltage\V<< LE | outserv | Real | E | 1 | 0 | 1.52
[11 empty] | x076_u002E_001;x003_u002E_060 | E;E | 1;1 | 0.8 |  | SE | 1.5 | Voltage\V<< LE | Uset | Real | 1 | 0 | [7 empty] | Voltage\V<< LE | Uset | Real |  |  | 1 | 0
[16 empty] | SE | 1.5 | Voltage\V<< LE | outserv | Real | 0 | 0
[16 empty] | G | 1.5 | Voltage\V<< LE | outserv | Real | 0 | 1
x076_u002E_009 | Parametersatz 1->U<> | 076.009 | 0-100:0.01;blockiert=100.02 | s | tU< PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1 | 4 | SE | 100 | Voltage\V< LL | Tdel | Real | 1 | 0 |  | x076_u002E_001;x003_u002E_060 |  |  | E;E | 0;1 | 2 | Voltage\V< LL | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V< LL | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
[16 empty] | SE | 100 | Voltage\V< LE | Tdel | Real | 1 | 0 |  | x076_u002E_001;x003_u002E_060 |  |  | E;E | 1;1 | 2 | Voltage\V< LE | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V< LE | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x076_u002E_010 | Parametersatz 1->U<> | 076.010 | 0-100:0.01;blockiert=100.02 | s | tU<< PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1 | 4 | SE | 100 | Voltage\V<< LL | Tdel | Real | 1 | 0 |  | x076_u002E_001;x003_u002E_060 |  |  | E;E | 0;1 | 2 | Voltage\V<< LL | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V<< LL | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
[16 empty] | SE | 100 | Voltage\V<< LE | Tdel | Real | 1 | 0 |  | x076_u002E_001;x003_u002E_060 |  |  | E;E | 1;1 | 2 | Voltage\V<< LE | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V<< LE | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x076_u002E_015 | Parametersatz 1->U<> | 076.015 | 0.2-1.5:0.01;blockiert=1.52 | Unom/©3 | Umit> PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1.1 | 3 | SE | 1.5 | Voltage\Vpos> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 3 | Voltage\Vpos> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos> | Uset | Real | GE | 0.2 | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vpos> | outserv | Real | 0 | 1 | [13 empty] | 0.2
x076_u002E_016 | Parametersatz 1->U<> | 076.016 | 0.2-1.5:0.01;blockiert=1.52 | Unom/©3 | Umit>> PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1.1 | 3 | SE | 1.5 | Voltage\Vpos>> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 3 | Voltage\Vpos>> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos>> | Uset | Real | GE | 0.2 | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vpos>> | outserv | Real | 0 | 1 | [13 empty] | 0.2
x076_u002E_017 | Parametersatz 1->U<> | 076.017 | 0-100:0.01;blockiert=100.02 | s | tUmit> PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 | SE | 100 | Voltage\Vpos> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Voltage\Vpos> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vpos> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x076_u002E_018 | Parametersatz 1->U<> | 076.018 | 0-100:0.01;blockiert=100.02 | s | tUmit>> PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 | SE | 100 | Voltage\Vpos>> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Voltage\Vpos>> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vpos>> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x076_u002E_019 | Parametersatz 1->U<> | 076.019 | 0.2-1.5:0.01;blockiert=1.52 | Unom/©3 | Umit< PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 0.8 | 3 | SE | 1.5 | Voltage\Vpos< | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 3 | Voltage\Vpos< | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos< | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos< | Uset | Real | GE | 0.2 | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vpos< | outserv | Real | 0 | 1 | [13 empty] | 0.2
x076_u002E_020 | Parametersatz 1->U<> | 076.020 | 0.2-1.5:0.01;blockiert=1.52 | Unom/©3 | Umit<< PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 0.8 | 3 | SE | 1.5 | Voltage\Vpos<< | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 3 | Voltage\Vpos<< | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos<< | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos<< | Uset | Real | GE | 0.2 | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vpos<< | outserv | Real | 0 | 1 | [13 empty] | 0.2
x076_u002E_021 | Parametersatz 1->U<> | 076.021 | 0-100:0.01;blockiert=100.02 | s | tUmit< PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 | SE | 100 | Voltage\Vpos< | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Voltage\Vpos< | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vpos< | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x076_u002E_022 | Parametersatz 1->U<> | 076.022 | 0-100:0.01;blockiert=100.02 | s | tUmit<< PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 | SE | 100 | Voltage\Vpos<< | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Voltage\Vpos<< | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vpos<< | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x076_u002E_023 | Parametersatz 1->U<> | 076.023 | 0.2-1.5:0.01;blockiert=1.52 | Unom/©3 | Ugegen> PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1.52 | 3 | SE | 1.5 | Voltage\Vneg> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 3 | Voltage\Vneg> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vneg> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vneg> | Uset | Real | GE | 0.2 | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vneg> | outserv | Real | 0 | 1 | [13 empty] | 0.2
x076_u002E_024 | Parametersatz 1->U<> | 076.024 | 0.2-1.5:0.01;blockiert=1.52 | Unom/©3 | Ugegen>> PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1.52 | 3 | SE | 1.5 | Voltage\Vneg>> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 3 | Voltage\Vneg>> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vneg>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vneg>> | Uset | Real | GE | 0.2 | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vneg>> | outserv | Real | 0 | 1 | [13 empty] | 0.2
x076_u002E_025 | Parametersatz 1->U<> | 076.025 | 0-100:0.01;blockiert=100.02 | s | tUgegen> PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 | SE | 100 | Voltage\Vneg> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Voltage\Vneg> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vneg> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x076_u002E_026 | Parametersatz 1->U<> | 076.026 | 0-100:0.01;blockiert=100.02 | s | tUgegen>> PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 | SE | 100 | Voltage\Vneg>> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Voltage\Vneg>> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vneg>> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x076_u002E_011 | Parametersatz 1->U<> | 076.011 | 0.02-1:0.01;blockiert=1.02 | Unom(/©3) | UNE> PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1.02 | 3 | SE | 1 | Voltage\VNG> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Voltage\VNG> | outserv | Real | E | 1 | 0 | 1.02
[16 empty] | SE | 1 | Voltage\VNG> | outserv | Real | 0 | 0 | [7 empty] | Voltage\VNG> | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1 | Voltage\VNG> | outserv | Real | 0 | 1
x076_u002E_012 | Parametersatz 1->U<> | 076.012 | 0.02-1:0.01;blockiert=1.02 | Unom(/©3) | UNE>> PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1.02 | 3 | SE | 1 | Voltage\VNG>> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Voltage\VNG>> | outserv | Real | E | 1 | 0 | 1.02
[16 empty] | SE | 1 | Voltage\VNG>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\VNG>> | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1 | Voltage\VNG>> | outserv | Real | 0 | 1
x076_u002E_013 | Parametersatz 1->U<> | 076.013 | 0-100:0.01;blockiert=100.02 | s | tUNE> PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 | SE | 100 | Voltage\VNG> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Voltage\VNG> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\VNG> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x076_u002E_014 | Parametersatz 1->U<> | 076.014 | 0-100:0.01;blockiert=100.02 | s | tUNE>> PS1 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 | SE | 100 | Voltage\VNG>> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Voltage\VNG>> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\VNG>> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x018_u002E_196 | Parametersatz 1->f<> | 018.196 | nein¦0;ja¦1 |  | Freigabe PS1 | Enum | Parameter__Funktionsparameter | 1;0 | Real |  | x056_u002E_033;x003_u002E_060 | E;E | 0;1 | 1 |  |  |  | Frequency | outserv | Real | 1 | 0 |  | x056_u002E_033;x003_u002E_060 |  |  | E;E | 0;1 |  | Frequency | outserv | Real |  |  | 1 | 0
x018_u002E_120 | Parametersatz 1->f<> | 018.120 | f¦0;f mit df/dt¦1;f m. Delta f/Delta t¦2 |  | Betriebsart f1 PS1 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 1 | 0 |  | NE | 0 | Frequency\f1 | outserv | Real | 0 | 1
x018_u002E_100 | Parametersatz 1->f<> | 018.100 | 40-70:0.01;blockiert=70.02 | Hz | f1 PS1 | Real | Parameter__Funktionsparameter |  |  |  | x018_u002E_120;x003_u002E_060 | E;E | 0;1 | 49.8 | 3 | SE | 70 | Frequency\f1 | Fset | Real | 1 | 0 |  | x018_u002E_120;x003_u002E_060 |  |  | E;E | 0;1 | 2 | Frequency\f1 | outserv | Real | E | 1 | 0 | 70.02
[16 empty] | SE | 70 | Frequency\f1 | outserv | Real | 0 | 0 | [7 empty] | Frequency\f1 | Uset | Real |  |  | 1 | 0
[16 empty] | G | 70 | Frequency\f1 | outserv | Real | 0 | 1
x018_u002E_104 | Parametersatz 1->f<> | 018.104 | 0-10:0.001;blockiert=10.002 | s | tf1 PS1 | Real | Parameter__Funktionsparameter |  |  |  | x018_u002E_120;x003_u002E_060 | E;E | 0;1 | 0 | 2 | SE | 10 | Frequency\f1 | Tdel | Real | 1 | 0 |  | x018_u002E_120;x003_u002E_060 |  |  | E;E | 0;1 | 2 | Frequency\f1 | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Frequency\f1 | Tdel | Real | 0 | 9999999 | [13 empty] | 10.002
x018_u002E_144 | Parametersatz 1->f<> | 018.144 | f¦0;f mit df/dt¦1;f m. Delta f/Delta t¦2 |  | Betriebsart f2 PS1 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 1 | 0 |  | NE | 0 | Frequency\f2 | outserv | Real | 0 | 1
x018_u002E_124 | Parametersatz 1->f<> | 018.124 | 40-70:0.01;blockiert=70.02 | Hz | f2 PS1 | Real | Parameter__Funktionsparameter |  |  |  | x018_u002E_144;x003_u002E_060 | E;E | 0;1 | 49.8 | 3 | SE | 70 | Frequency\f2 | Fset | Real | 1 | 0 |  | x018_u002E_144;x003_u002E_060 |  |  | E;E | 0;1 | 2 | Frequency\f2 | outserv | Real | E | 1 | 0 | 70.02
[16 empty] | SE | 70 | Frequency\f2 | outserv | Real | 0 | 0 | [7 empty] | Frequency\f2 | Uset | Real |  |  | 1 | 0
[16 empty] | G | 70 | Frequency\f2 | outserv | Real | 0 | 1
x018_u002E_128 | Parametersatz 1->f<> | 018.128 | 0-10:0.001;blockiert=10.002 | s | tf2 PS1 | Real | Parameter__Funktionsparameter |  |  |  | x018_u002E_144;x003_u002E_060 | E;E | 0;1 | 0 | 2 | SE | 10 | Frequency\f2 | Tdel | Real | 1 | 0 |  | x018_u002E_144;x003_u002E_060 |  |  | E;E | 0;1 | 2 | Frequency\f2 | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Frequency\f2 | Tdel | Real | 0 | 9999999 | [13 empty] | 10.002
x018_u002E_168 | Parametersatz 1->f<> | 018.168 | f¦0;f mit df/dt¦1;f m. Delta f/Delta t¦2 |  | Betriebsart f3 PS1 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 1 | 0 |  | NE | 0 | Frequency\f3 | outserv | Real | 0 | 1
x018_u002E_148 | Parametersatz 1->f<> | 018.148 | 40-70:0.01;blockiert=70.02 | Hz | f3 PS1 | Real | Parameter__Funktionsparameter |  |  |  | x018_u002E_168;x003_u002E_060 | E;E | 0;1 | 49.8 | 3 | SE | 70 | Frequency\f3 | Fset | Real | 1 | 0 |  | x018_u002E_168;x003_u002E_060 |  |  | E;E | 0;1 | 2 | Frequency\f3 | outserv | Real | E | 1 | 0 | 70.02
[16 empty] | SE | 70 | Frequency\f3 | outserv | Real | 0 | 0 | [7 empty] | Frequency\f3 | Uset | Real |  |  | 1 | 0
[16 empty] | G | 70 | Frequency\f3 | outserv | Real | 0 | 1
x018_u002E_152 | Parametersatz 1->f<> | 018.152 | 0-10:0.001;blockiert=10.002 | s | tf3 PS1 | Real | Parameter__Funktionsparameter |  |  |  | x018_u002E_168;x003_u002E_060 | E;E | 0;1 | 0 | 2 | SE | 10 | Frequency\f3 | Tdel | Real | 1 | 0 |  | x018_u002E_168;x003_u002E_060 |  |  | E;E | 0;1 | 2 | Frequency\f3 | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Frequency\f3 | Tdel | Real | 0 | 9999999 | [13 empty] | 10.002
x018_u002E_192 | Parametersatz 1->f<> | 018.192 | f¦0;f mit df/dt¦1;f m. Delta f/Delta t¦2 |  | Betriebsart f4 PS1 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 1 | 0 |  | NE | 0 | Frequency\f4 | outserv | Real | 0 | 1
x018_u002E_172 | Parametersatz 1->f<> | 018.172 | 40-70:0.01;blockiert=70.02 | Hz | f4 PS1 | Real | Parameter__Funktionsparameter |  |  |  | x018_u002E_192;x003_u002E_060 | E;E | 0;1 | 49.8 | 3 | SE | 70 | Frequency\f4 | Fset | Real | 1 | 0 |  | x018_u002E_192;x003_u002E_060 |  |  | E;E | 0;1 | 2 | Frequency\f4 | outserv | Real | E | 1 | 0 | 70.02
[16 empty] | SE | 70 | Frequency\f4 | outserv | Real | 0 | 0 | [7 empty] | Frequency\f4 | Uset | Real |  |  | 1 | 0
[16 empty] | G | 70 | Frequency\f4 | outserv | Real | 0 | 1
x018_u002E_176 | Parametersatz 1->f<> | 018.176 | 0-10:0.001;blockiert=10.002 | s | tf4 PS1 | Real | Parameter__Funktionsparameter |  |  |  | x018_u002E_192;x003_u002E_060 | E;E | 0;1 | 0 | 2 | SE | 10 | Frequency\f4 | Tdel | Real | 1 | 0 |  | x018_u002E_192;x003_u002E_060 |  |  | E;E | 0;1 | 2 | Frequency\f4 | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Frequency\f4 | Tdel | Real | 0 | 9999999 | [13 empty] | 10.002
x001_u002E_076 | Parametersatz 2->GRUND | 001.076 | niederohmig geerdet¦0;isol/komp m.Anreg.LE¦1;isol/komp o.Anreg.LE¦2;Kurzzeiterdung¦3 |  | Sternpunktbeh. PS2 | Enum | Parameter__Funktionsparameter | 0;1;2;3;4 | Real |  | x003_u002E_060 | E | 2 | 0 | 4 | E | 0 | Distance Circular\Starting | isysstar | Real | 0 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Circular\Starting | isysstar | Real |  | 0 | 1 | 0
[16 empty] | E | 0 | Distance Polygonal\Starting | isysstar | Real | 0 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Polygonal\Starting | isysstar | Real | E | 0 | 1 | 0
[16 empty] | NE | 0 | Distance Circular\Starting | isysstar | Real | 0 | 1
[16 empty] | NE | 0 | Distance Polygonal\Starting | isysstar | Real | 0 | 1
x001_u002E_079 | Parametersatz 2->GRUND | 001.079 | Erde¦0;LvE=f(Imittel,Imax)¦1 |  | Mitnahme bei 1p PS2 | Enum | Parameter__Funktionsparameter | 0;1 | Real |  | x003_u002E_060 | E | 2 | 0 | 2 |  |  | Distance Circular\Starting | itransf1p | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Circular\Starting | itransf1p | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | itransf1p | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Polygonal\Starting | itransf1p | Real |  |  | 1 | 0
x010_u002E_074 | Parametersatz 2->DIST | 010.074 | 0.1-20:0.01 | Inom | I>> PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 |  |  | Distance Circular\Starting | IMM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Circular\Starting | IMM | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | IMM | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Polygonal\Starting | IMM | Real |  |  | 1 | 0
x010_u002E_088 | Parametersatz 2->DIST | 010.088 | 0.1-1:0.01 | Inom | I> (IF)(max.Ber.)PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 0.2 | 2 |  |  | Distance Circular\Starting | IM1 | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;2 | 2 | Distance Circular\Starting | IM1 | Real | GE | 0.1 | 1 | 0
[18 empty] | Distance Polygonal\Starting | IM1 | Real | 1 | 0 | [13 empty] | 0.1
[24 empty] | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;2 | 2 | Distance Polygonal\Starting | IM1 | Real | GE | 0.1 | 1 | 0
0.1
x010_u002E_120 | Parametersatz 2->DIST | 010.120 | 0.05-1:0.01 | Inom | I> (IF)(emp.Ber.)PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 0.2 | 2 |  |  | Distance Circular\Starting | IM2 | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Circular\Starting | IM2 | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | IM2 | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Polygonal\Starting | IM2 | Real |  |  | 1 | 0
x010_u002E_087 | Parametersatz 2->DIST | 010.087 | ohne U<-Anregung¦0;mit U<-Anreg. nur LE¦1;mit U<-Anreg. LE, LL¦2 |  | Betriebsart U< PS2 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 2 | 2 | 8 | E | 0 | Distance Circular\Starting | iopt_u | Real | 0 | 0 | 4 | Distance Circular;Distance Circular\Starting;x003_u002E_060 | outserv;iopt_u | Real | E;E;E | 0;0;2 | [7 empty] | 0
[16 empty] | E | 0 | Distance Polygonal\Starting | iopt_u | Real | 0 | 0 |  | Distance Circular;Distance Circular\Starting;x003_u002E_060 | outserv;iopt_u | Real | E;E;E | 0;1;2 | 2 | Distance Circular\Starting | iVOpMode | Real | E | 0 | 0 | 1
[16 empty] | NE | 0 | Distance Circular\Starting | iopt_u | Real | 0 | 1 | [7 empty] | Distance Circular\Starting | iVOpMode | Real | E | 1 | 0 | 2
[16 empty] | NE | 0 | Distance Polygonal\Starting | iopt_u | Real | 0 | 1 |  | Distance Polygonal;Distance Polygonal\Starting;x003_u002E_060 | outserv;iopt_u | Real | E;E;E | 0;0;2 | [7 empty] | 0
[16 empty] | E | 1 | Distance Circular\Starting | iVOpMode | Real | 0 | 0 |  | Distance Polygonal;Distance Polygonal\Starting;x003_u002E_060 | outserv;iopt_u | Real | E;E;E | 0;1;2 | 2 | Distance Polygonal\Starting | iVOpMode | Real | E | 0 | 0 | 1
[16 empty] | E | 1 | Distance Polygonal\Starting | iVOpMode | Real | 0 | 0 | [7 empty] | Distance Polygonal\Starting | iVOpMode | Real | E | 1 | 0 | 2
[16 empty] | E | 2 | Distance Circular\Starting | iVOpMode | Real | 0 | 1
[16 empty] | E | 2 | Distance Polygonal\Starting | iVOpMode | Real | 0 | 1
x010_u002E_089 | Parametersatz 2->DIST | 010.089 | 0.1-0.9:0.01 | Unom(/©3) | U< PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 0.7 | 2 |  |  | Distance Circular\Starting | Um | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Circular\Starting | Um | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | Um | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Polygonal\Starting | Um | Real |  |  | 1 | 0
x010_u002E_086 | Parametersatz 2->DIST | 010.086 | ohne Z<-Anregung¦0;mit Z<-Anreg. nur LE¦1;mit Z<-Anreg. LE, LL¦2 |  | Betriebsart Z< PS2 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 2 | 2 | 8 | E | 0 | Distance Circular\Starting | iopt_z | Real | 0 | 0 | 4 | Distance Circular;Distance Circular\Starting;x003_u002E_060 | outserv;iopt_z | Real | E;E;E | 0;0;2 | [7 empty] | 0
[16 empty] | E | 0 | Distance Polygonal\Starting | iopt_z | Real | 0 | 0 |  | Distance Circular;Distance Circular\Starting;x003_u002E_060 | outserv;iopt_z | Real | E;E;E | 0;1;2 | 2 | Distance Circular\Starting | iZOpMode | Real | E | 0 | 0 | 1
[16 empty] | NE | 0 | Distance Circular\Starting | iopt_z | Real | 0 | 1 | [7 empty] | Distance Circular\Starting | iZOpMode | Real | E | 1 | 0 | 2
[16 empty] | NE | 0 | Distance Polygonal\Starting | iopt_z | Real | 0 | 1 |  | Distance Polygonal;Distance Polygonal\Starting;x003_u002E_060 | outserv;iopt_z | Real | E;E;E | 0;0;2 | [7 empty] | 0
[16 empty] | E | 1 | Distance Circular\Starting | iZOpMode | Real | 0 | 0 |  | Distance Polygonal;Distance Polygonal\Starting;x003_u002E_060 | outserv;iopt_z | Real | E;E;E | 0;1;2 | 2 | Distance Polygonal\Starting | iZOpMode | Real | E | 0 | 0 | 1
[16 empty] | E | 1 | Distance Polygonal\Starting | iZOpMode | Real | 0 | 0 | [7 empty] | Distance Polygonal\Starting | iZOpMode | Real | E | 1 | 0 | 2
[16 empty] | E | 2 | Distance Circular\Starting | iZOpMode | Real | 0 | 1
[16 empty] | E | 2 | Distance Polygonal\Starting | iZOpMode | Real | 0 | 1
x010_u002E_070 | Parametersatz 2->DIST | 010.070 | 0.1-300:0.01 | — | Xv PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 10 | 2 |  |  | Distance Circular\Starting | Xfw | Real | 0.2 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;2 | 2 | Distance Circular\Starting | Xfw | Real | SE | 60 | 5 | 0
[18 empty] | Distance Polygonal\Starting | Xfw | Real | 0.2 | 0 | [13 empty] | 300
[24 empty] | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;2 | 2 | Distance Polygonal\Starting | Xfw | Real | SE | 60 | 5 | 0
300
x010_u002E_071 | Parametersatz 2->DIST | 010.071 | 0.1-300:0.01 | — | Rv,LE PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 10 | 2 |  |  | Distance Circular\Starting | RfPG | Real | 0.2 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;2 | 2 | Distance Circular\Starting | RfPG | Real | SE | 60 | 5 | 0
[18 empty] | Distance Polygonal\Starting | RfPG | Real | 0.2 | 0 | [13 empty] | 300
[24 empty] | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;2 | 2 | Distance Polygonal\Starting | RfPG | Real | SE | 60 | 5 | 0
300
x010_u002E_072 | Parametersatz 2->DIST | 010.072 | 0.1-300:0.01 | — | Rv,LL PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 10 | 2 |  |  | Distance Circular\Starting | RfPP | Real | 0.2 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;2 | 2 | Distance Circular\Starting | RfPP | Real | SE | 60 | 5 | 0
[18 empty] | Distance Polygonal\Starting | RfPP | Real | 0.2 | 0 | [13 empty] | 300
[24 empty] | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;2 | 2 | Distance Polygonal\Starting | RfPP | Real | SE | 60 | 5 | 0
300
x010_u002E_083 | Parametersatz 2->DIST | 010.083 | 15-65:1 | ° | ß PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 30 |  |  |  | Distance Circular\Starting | Beta | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Circular\Starting | Beta | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | Beta | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Polygonal\Starting | Beta | Real |  |  | 1 | 0
x010_u002E_102 | Parametersatz 2->DIST | 010.102 | 0-300:0.01 | — | Zv,LE PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 0 | 2 |  |  | Distance Circular\Starting | ZfPG | Real | 0.2 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;2 | 2 | Distance Circular\Starting | ZfPG | Real | SE | 60 | 5 | 0
[18 empty] | Distance Polygonal\Starting | ZfPG | Real | 0.2 | 0 | [13 empty] | 300
[24 empty] | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;2 | 2 | Distance Polygonal\Starting | ZfPG | Real | SE | 60 | 5 | 0
300
x010_u002E_106 | Parametersatz 2->DIST | 010.106 | 0-300:0.01 | — | Zv,LL PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 0 | 2 |  |  | Distance Circular\Starting | ZfPP | Real | 0.2 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;2 | 2 | Distance Circular\Starting | ZfPP | Real | SE | 60 | 5 | 0
[18 empty] | Distance Polygonal\Starting | ZfPP | Real | 0.2 | 0 | [13 empty] | 300
[24 empty] | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;2 | 2 | Distance Polygonal\Starting | ZfPP | Real | SE | 60 | 5 | 0
300
x010_u002E_073 | Parametersatz 2->DIST | 010.073 | 0.1-4:0.01 |  | Zr/Zv PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 0.5 | 2 |  |  | Distance Circular\Starting | ZbwZfw | Real | 0.2 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;2 | 2 | Distance Circular\Starting | ZbwZfw | Real | GE | 0.1 | 1 | 0
[18 empty] | Distance Polygonal\Starting | ZbwZfw | Real | 0.2 | 0 | [13 empty] | 0.1
[24 empty] | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;2 | 2 | Distance Polygonal\Starting | ZbwZfw | Real | GE | 0.1 | 1 | 0
0.1
x010_u002E_075 | Parametersatz 2->DIST | 010.075 | 0.1-2:0.01 | Inom | IE> (max.Ber.) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 0.2 | 2 |  |  | Distance Circular\Starting | INMM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;2 | 2 | Distance Circular\Starting | INMM | Real | GE | 0.1 | 1 | 0
[18 empty] | Distance Polygonal\Starting | INMM | Real | 1 | 0 | [13 empty] | 0.1
[24 empty] | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;2 | 2 | Distance Polygonal\Starting | INMM | Real | GE | 0.1 | 1 | 0
0.1
x010_u002E_124 | Parametersatz 2->DIST | 010.124 | 0.05-2:0.01 | Inom | IE> (emp.Ber.) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 0.2 | 2 |  |  | Distance Circular\Starting | INM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Circular\Starting | INM | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | INM | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Polygonal\Starting | INM | Real |  |  | 1 | 0
x010_u002E_077 | Parametersatz 2->DIST | 010.077 | 0-0.5:0.001 | s | tIE> PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 0.1 | 2 |  |  | Distance Circular\Starting | tINM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Circular\Starting | tINM | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | tINM | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Polygonal\Starting | tINM | Real |  |  | 1 | 0
x010_u002E_076 | Parametersatz 2->DIST | 010.076 | 0.02-1:0.01 | Unom/©3 | UNE> PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 0.1 | 2 |  |  | Distance Circular\Starting | VNGM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;2 | 2 | Distance Circular\Starting | VNGM | Real | GE | 0.02 | 1 | 0
[18 empty] | Distance Polygonal\Starting | VNGM | Real | 1 | 0 | [13 empty] | 0.02
[24 empty] | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;2 | 2 | Distance Polygonal\Starting | VNGM | Real | GE | 0.02 | 1 | 0
0.02
x010_u002E_082 | Parametersatz 2->DIST | 010.082 | 0.2-1:0.01 | Unom/©3 | UNE>> PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 0.5 | 2 |  |  | Distance Circular\Starting | VNGMM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Circular\Starting | VNGMM | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | VNGMM | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Polygonal\Starting | VNGMM | Real |  |  | 1 | 0
x010_u002E_081 | Parametersatz 2->DIST | 010.081 | 0-60:0.001 | s | tUNE>> PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 |  |  | Distance Circular\Starting | tVNGMM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Circular\Starting | tVNGMM | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | tVNGMM | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Polygonal\Starting | tVNGMM | Real |  |  | 1 | 0
x012_u002E_087 | Parametersatz 2->DIST | 012.087 | 0-8:0.01 |  | Betrag kE PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 |  |  | Distance Circular\Polarisation | k0 | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Circular\Polarisation | k0 | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Polarisation | k0 | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Polygonal\Polarisation | k0 | Real |  |  | 1 | 0
x012_u002E_086 | Parametersatz 2->DIST | 012.086 | -180-180:1 | ° | Winkel kE PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 0 | 2 |  |  | Distance Circular\Polarisation | phik0 | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Circular\Polarisation | phik0 | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Polarisation | phik0 | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Polygonal\Polarisation | phik0 | Real |  |  | 1 | 0
x073_u002E_097 | Parametersatz 2->DIST | 073.097 | Kreis¦0;Polygon¦1 |  | Kennlinientyp PS2 | Enum | Parameter__Funktionsparameter | 0;1 | Real |  | x056_u002E_014;x031_u002E_073;x003_u002E_060 | E;E;E | 0;0;2 | 1 | 4 | E | 0 | Distance Circular | outserv | Real | 0 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Distance Circular | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 0 | Distance Polygonal | outserv | Real | 0 | 1 | [13 empty] | 1
[16 empty] | E | 1 | Distance Circular | outserv | Real | 0 | 1
[16 empty] | E | 1 | Distance Polygonal | outserv | Real | 0 | 0
x012_u002E_051 | Parametersatz 2->DIST | 012.051 | 0.1-200:0.01 | — | X1 (Polygon) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 10 |  |  |  | Distance Polygonal\Z1 | Xmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Polygonal\Z1 | Xmax | Real | SE | 40 | 5 | 0
200
x012_u002E_052 | Parametersatz 2->DIST | 012.052 | 0.1-200:0.01 | — | X2 (Polygon) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 20 |  |  |  | Distance Polygonal\Z2 | Xmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Polygonal\Z2 | Xmax | Real | SE | 40 | 5 | 0
200
x012_u002E_053 | Parametersatz 2->DIST | 012.053 | 0.1-200:0.01 | — | X3 (Polygon) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 30 |  |  |  | Distance Polygonal\Z3 | Xmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Polygonal\Z3 | Xmax | Real | SE | 40 | 5 | 0
200
x012_u002E_054 | Parametersatz 2->DIST | 012.054 | 0.1-200:0.01 | — | X4 (Polygon) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 40 |  |  |  | Distance Polygonal\Z4 | Xmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Polygonal\Z4 | Xmax | Real | SE | 40 | 5 | 0
200
x012_u002E_101 | Parametersatz 2->DIST | 012.101 | 0.1-200:0.01 | — | X5 (Polygon) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 50 |  |  |  | Distance Polygonal\Z5 | Xmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Polygonal\Z5 | Xmax | Real | SE | 40 | 5 | 0
200
x012_u002E_105 | Parametersatz 2->DIST | 012.105 | 0.1-200:0.01 | — | X6 (Polygon) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 60 |  |  |  | Distance Polygonal\Z6 | Xmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Polygonal\Z6 | Xmax | Real | SE | 40 | 5 | 0
200
x012_u002E_055 | Parametersatz 2->DIST | 012.055 | 0.1-200:0.01 | — | R1,LE (Polygon) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 10 |  |  |  | Distance Polygonal\Z1 | REmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Polygonal\Z1 | REmax | Real | SE | 40 | 5 | 0
200
x012_u002E_056 | Parametersatz 2->DIST | 012.056 | 0.1-200:0.01 | — | R1,LL (Polygon) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 10 |  |  |  | Distance Polygonal\Z1 | Rmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Polygonal\Z1 | Rmax | Real | SE | 40 | 5 | 0
200
x012_u002E_057 | Parametersatz 2->DIST | 012.057 | 0.1-200:0.01 | — | R2,LE (Polygon) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 20 |  |  |  | Distance Polygonal\Z2 | REmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Polygonal\Z2 | REmax | Real | SE | 40 | 5 | 0
200
x012_u002E_058 | Parametersatz 2->DIST | 012.058 | 0.1-200:0.01 | — | R2,LL (Polygon) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 20 |  |  |  | Distance Polygonal\Z2 | Rmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Polygonal\Z2 | Rmax | Real | SE | 40 | 5 | 0
200
x012_u002E_059 | Parametersatz 2->DIST | 012.059 | 0.1-200:0.01 | — | R3,LE (Polygon) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 30 |  |  |  | Distance Polygonal\Z3 | REmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Polygonal\Z3 | REmax | Real | SE | 40 | 5 | 0
200
x012_u002E_060 | Parametersatz 2->DIST | 012.060 | 0.1-200:0.01 | — | R3,LL (Polygon) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 30 |  |  |  | Distance Polygonal\Z3 | Rmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Polygonal\Z3 | Rmax | Real | SE | 40 | 5 | 0
200
x012_u002E_061 | Parametersatz 2->DIST | 012.061 | 0.1-200:0.01 | — | R4,LE (Polygon) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 40 |  |  |  | Distance Polygonal\Z4 | REmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Polygonal\Z4 | REmax | Real | SE | 40 | 5 | 0
200
x012_u002E_062 | Parametersatz 2->DIST | 012.062 | 0.1-200:0.01 | — | R4,LL (Polygon) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 40 |  |  |  | Distance Polygonal\Z4 | Rmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Polygonal\Z4 | Rmax | Real | SE | 40 | 5 | 0
200
x012_u002E_109 | Parametersatz 2->DIST | 012.109 | 0.1-200:0.01 | — | R5,LE (Polygon) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 50 |  |  |  | Distance Polygonal\Z5 | REmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Polygonal\Z5 | REmax | Real | SE | 40 | 5 | 0
200
x012_u002E_113 | Parametersatz 2->DIST | 012.113 | 0.1-200:0.01 | — | R5,LL (Polygon) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 50 |  |  |  | Distance Polygonal\Z5 | Rmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Polygonal\Z5 | Rmax | Real | SE | 40 | 5 | 0
200
x012_u002E_117 | Parametersatz 2->DIST | 012.117 | 0.1-200:0.01 | — | R6,LE (Polygon) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 60 |  |  |  | Distance Polygonal\Z6 | REmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Polygonal\Z6 | REmax | Real | SE | 40 | 5 | 0
200
x012_u002E_121 | Parametersatz 2->DIST | 012.121 | 0.1-200:0.01 | — | R6,LL (Polygon) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 60 |  |  |  | Distance Polygonal\Z6 | Rmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Polygonal\Z6 | Rmax | Real | SE | 40 | 5 | 0
200
x012_u002E_063 | Parametersatz 2->DIST | 012.063 | 40-90:1 | ° | €1 (Polygon) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 75 |  |  |  | Distance Polygonal\Z1 | phi | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Polygonal\Z1 | phi | Real | GE | 40 | 1 | 0
40
x012_u002E_064 | Parametersatz 2->DIST | 012.064 | 40-90:1 | ° | €2 (Polygon) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 75 |  |  |  | Distance Polygonal\Z2 | phi | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Polygonal\Z2 | phi | Real | GE | 40 | 1 | 0
40
x012_u002E_065 | Parametersatz 2->DIST | 012.065 | 40-90:1 | ° | €3 (Polygon) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 75 |  |  |  | Distance Polygonal\Z3 | phi | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Polygonal\Z3 | phi | Real | GE | 40 | 1 | 0
40
x012_u002E_066 | Parametersatz 2->DIST | 012.066 | 40-90:1 | ° | €4 (Polygon) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 75 |  |  |  | Distance Polygonal\Z4 | phi | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Polygonal\Z4 | phi | Real | GE | 40 | 1 | 0
40
x012_u002E_125 | Parametersatz 2->DIST | 012.125 | 40-90:1 | ° | €5 (Polygon) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 75 |  |  |  | Distance Polygonal\Z5 | phi | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Polygonal\Z5 | phi | Real | GE | 40 | 1 | 0
40
x012_u002E_129 | Parametersatz 2->DIST | 012.129 | 40-90:1 | ° | €6 (Polygon) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 75 |  |  |  | Distance Polygonal\Z6 | phi | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Polygonal\Z6 | phi | Real | GE | 40 | 1 | 0
40
x073_u002E_086 | Parametersatz 2->DIST | 073.086 | -20-20:1 | ° | ‹1 (Polygon) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 0 |  |  |  | Distance Polygonal\Z1 | beta | Real | -1 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\Z1 | beta | Real |  |  | -1 | 0
x073_u002E_087 | Parametersatz 2->DIST | 073.087 | -20-20:1 | ° | ‹2 (Polygon) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 0 |  |  |  | Distance Polygonal\Z2 | beta | Real | -1 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\Z2 | beta | Real |  |  | -1 | 0
x073_u002E_088 | Parametersatz 2->DIST | 073.088 | -20-20:1 | ° | ‹3 (Polygon) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 0 |  |  |  | Distance Polygonal\Z3 | beta | Real | -1 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\Z3 | beta | Real |  |  | -1 | 0
x073_u002E_089 | Parametersatz 2->DIST | 073.089 | -20-20:1 | ° | ‹4 (Polygon) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 0 |  |  |  | Distance Polygonal\Z4 | beta | Real | -1 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\Z4 | beta | Real |  |  | -1 | 0
x012_u002E_157 | Parametersatz 2->DIST | 012.157 | -20-20:1 | ° | ‹5 (Polygon) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 0 |  |  |  | Distance Polygonal\Z5 | beta | Real | -1 | 0 |  | Distance Polygonal;Distance Polygonal\Z5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\Z5 | beta | Real |  |  | -1 | 0
x012_u002E_161 | Parametersatz 2->DIST | 012.161 | -20-20:1 | ° | ‹6 (Polygon) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 0 |  |  |  | Distance Polygonal\Z6 | beta | Real | -1 | 0 |  | Distance Polygonal;Distance Polygonal\Z6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\Z6 | beta | Real |  |  | -1 | 0
x073_u002E_091 | Parametersatz 2->DIST | 073.091 | 0.05-200:0.01 | — | Z1 (Kreis) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 10 |  |  |  | Distance Circular\Z1 | Zm | Real | 0.2 | 0 |  | Distance Circular;Distance Circular\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Circular\Z1 | Zm | Real | SE | 40 | 5 | 0
200
x073_u002E_092 | Parametersatz 2->DIST | 073.092 | 0.05-200:0.01 | — | Z2 (Kreis) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 20 |  |  |  | Distance Circular\Z2 | Zm | Real | 0.2 | 0 |  | Distance Circular;Distance Circular\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Circular\Z2 | Zm | Real | SE | 40 | 5 | 0
200
x073_u002E_093 | Parametersatz 2->DIST | 073.093 | 0.05-200:0.01 | — | Z3 (Kreis) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 30 |  |  |  | Distance Circular\Z3 | Zm | Real | 0.2 | 0 |  | Distance Circular;Distance Circular\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Circular\Z3 | Zm | Real | SE | 40 | 5 | 0
200
x073_u002E_094 | Parametersatz 2->DIST | 073.094 | 0.05-200:0.01 | — | Z4 (Kreis) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 40 |  |  |  | Distance Circular\Z4 | Zm | Real | 0.2 | 0 |  | Distance Circular;Distance Circular\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Circular\Z4 | Zm | Real | SE | 40 | 5 | 0
200
x012_u002E_149 | Parametersatz 2->DIST | 012.149 | 0.05-200:0.01 | — | Z5 (Kreis) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 50 |  |  |  | Distance Circular\Z5 | Zm | Real | 0.2 | 0 |  | Distance Circular;Distance Circular\Z5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Circular\Z5 | Zm | Real | SE | 40 | 5 | 0
200
x012_u002E_153 | Parametersatz 2->DIST | 012.153 | 0.05-200:0.01 | — | Z6 (Kreis) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 60 |  |  |  | Distance Circular\Z6 | Zm | Real | 0.2 | 0 |  | Distance Circular;Distance Circular\Z6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Circular\Z6 | Zm | Real | SE | 40 | 5 | 0
200
x073_u002E_090 | Parametersatz 2->DIST | 073.090 | 10-90:1 | ° | €1 (Kreis) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 75 | 2 |  |  | Distance Circular\Z1 | arcalpha | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Circular\Z1 | arcalpha | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z1E | arcalpha | Real | 1 | 0
x073_u002E_095 | Parametersatz 2->DIST | 073.095 | 10-90:1 | ° | €2 (Kreis) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 75 |  |  |  | Distance Circular\Z2 | arcalpha | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Circular\Z2 | arcalpha | Real |  |  | 1 | 0
x073_u002E_096 | Parametersatz 2->DIST | 073.096 | 10-90:1 | ° | €3 (Kreis) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 75 |  |  |  | Distance Circular\Z3 | arcalpha | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Circular\Z3 | arcalpha | Real |  |  | 1 | 0
x073_u002E_099 | Parametersatz 2->DIST | 073.099 | 10-90:1 | ° | €4 (Kreis) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 75 |  |  |  | Distance Circular\Z4 | arcalpha | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Circular\Z4 | arcalpha | Real |  |  | 1 | 0
x012_u002E_165 | Parametersatz 2->DIST | 012.165 | 10-90:1 | ° | €5 (Kreis) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 75 |  |  |  | Distance Circular\Z5 | arcalpha | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Circular\Z5 | arcalpha | Real |  |  | 1 | 0
x012_u002E_169 | Parametersatz 2->DIST | 012.169 | 10-90:1 | ° | €6 (Kreis) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 75 |  |  |  | Distance Circular\Z6 | arcalpha | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Circular\Z6 | arcalpha | Real |  |  | 1 | 0
x012_u002E_090 | Parametersatz 2->DIST | 012.090 | nein¦0;ja¦1 |  | Li.bo.komp. Kr. PS2 | Enum | Parameter__Funktionsparameter | 0;1 | Real |  | x003_u002E_060 | E | 2 | 0 | 7 |  |  | Distance Circular\Z1 | arcen | Real | 1 | 0 | 6 | Distance Circular;Distance Circular\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Circular\Z1 | arcen | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z1E | arcen | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Circular\Z2 | arcen | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z2 | arcen | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Circular\Z3 | arcen | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z3 | arcen | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Circular\Z4 | arcen | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z4 | arcen | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Circular\Z5 | arcen | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z5 | arcen | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Circular\Z6 | arcen | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z6 | arcen | Real | 1 | 0
x012_u002E_073 | Parametersatz 2->DIST | 012.073 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung N1 PS2 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 2 | 0 | 4 | NE | 2 | Distance Circular\Z1 | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Circular\Z1 | idir | Real |  |  | 1 | 0
[16 empty] | NE | 2 | Distance Circular\Z1E | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\Z1 | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z1 | idir | Real | 1 | 0
[18 empty] | Distance Polygonal\Z1E | idir | Real | 1 | 0
x012_u002E_074 | Parametersatz 2->DIST | 012.074 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung N2 PS2 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 2 | 0 |  | NE | 2 | Distance Circular\Z2 | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Circular\Z2 | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z2 | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\Z2 | idir | Real |  |  | 1 | 0
x012_u002E_075 | Parametersatz 2->DIST | 012.075 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung N3 PS2 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 2 | 0 |  | NE | 2 | Distance Circular\Z3 | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Circular\Z3 | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z3 | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\Z3 | idir | Real |  |  | 1 | 0
x012_u002E_076 | Parametersatz 2->DIST | 012.076 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung N4 PS2 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 2 | 0 |  | NE | 2 | Distance Circular\Z4 | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Circular\Z4 | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z4 | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\Z4 | idir | Real |  |  | 1 | 0
x012_u002E_077 | Parametersatz 2->DIST | 012.077 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung N5 PS2 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 2 | 0 |  | NE | 2 | Distance Circular\Z5 | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Circular\Z5 | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z5 | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\Z5 | idir | Real |  |  | 1 | 0
x012_u002E_133 | Parametersatz 2->DIST | 012.133 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung N6 PS2 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 2 | 0 |  | NE | 2 | Distance Circular\Z6 | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Circular\Z6 | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z6 | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\Z6 | idir | Real |  |  | 1 | 0
x012_u002E_137 | Parametersatz 2->DIST | 012.137 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung N7 PS2 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 2 | 0 |  |  |  | Distance Circular\Directional | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Directional;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Circular\Directional | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Directional | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Directional;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\Directional | idir | Real |  |  | 1 | 0
x012_u002E_078 | Parametersatz 2->DIST | 012.078 | 0-60:0.001;blockiert=60.002 | s | t1 PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 0 | 4 | SE | 60 | Distance Circular\T1 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Circular\T1 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Circular\T1 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
[16 empty] | SE | 60 | Distance Polygonal\T1 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Polygonal\T1 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Polygonal\T1 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
x012_u002E_079 | Parametersatz 2->DIST | 012.079 | 0-60:0.001;blockiert=60.002 | s | t2 PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1 | 4 | SE | 60 | Distance Circular\T2 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Circular\T2 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Circular\T2 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
[16 empty] | SE | 60 | Distance Polygonal\T2 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Polygonal\T2 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Polygonal\T2 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
x012_u002E_080 | Parametersatz 2->DIST | 012.080 | 0-60:0.001;blockiert=60.002 | s | t3 PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 2 | 4 | SE | 60 | Distance Circular\T3 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Circular\T3 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Circular\T3 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
[16 empty] | SE | 60 | Distance Polygonal\T3 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Polygonal\T3 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Polygonal\T3 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
x012_u002E_081 | Parametersatz 2->DIST | 012.081 | 0-60:0.001;blockiert=60.002 | s | t4 PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 3 | 4 | SE | 60 | Distance Circular\T4 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Circular\T4 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Circular\T4 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
[16 empty] | SE | 60 | Distance Polygonal\T4 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Polygonal\T4 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Polygonal\T4 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
x012_u002E_082 | Parametersatz 2->DIST | 012.082 | 0-60:0.001;blockiert=60.002 | s | t5 PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 4 | 4 | SE | 60 | Distance Circular\T5 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Circular\T5 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Circular\T5 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
[16 empty] | SE | 60 | Distance Polygonal\T5 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Polygonal\T5 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Polygonal\T5 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
x012_u002E_083 | Parametersatz 2->DIST | 012.083 | 0-60:0.001;blockiert=60.002 | s | t6 PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 5 | 4 | SE | 60 | Distance Circular\T6 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Circular\T6 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Circular\T6 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
[16 empty] | SE | 60 | Distance Polygonal\T6 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Polygonal\T6 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Polygonal\T6 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
x012_u002E_141 | Parametersatz 2->DIST | 012.141 | 0-60:0.001;blockiert=60.002 | s | t7 PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 6 | 4 | SE | 60 | Distance Circular\T9 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T9;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Circular\T9 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Circular\T9 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
[16 empty] | SE | 60 | Distance Polygonal\T9 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T9;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Polygonal\T9 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Polygonal\T9 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
x012_u002E_145 | Parametersatz 2->DIST | 012.145 | 0-60:0.001;blockiert=60.002 | s | t8 PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 7 | 4 | SE | 60 | Distance Circular\T10 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T10;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Circular\T10 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Circular\T10 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
[16 empty] | SE | 60 | Distance Polygonal\T10 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T10;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Polygonal\T10 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Polygonal\T10 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
x012_u002E_085 | Parametersatz 2->DIST | 012.085 | 1-450:0.01 |  | kÜ,LL KU PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1.2 | 3 |  |  | Distance Circular\Z1E | kZ | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z1E;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Circular\Z1E | kZ | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z1E | kX | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z1E;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\Z1E | kX | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z1E | kR | Real | 1 | 0
x015_u002E_015 | Parametersatz 2->SV | 015.015 | nein¦0;ja¦1 |  | Freigabe PS2 | Enum | Parameter__Funktionsparameter | 0;1 | String |  | x003_u002E_060 | E | 2 | 0 | 2 |  |  | Distance Circular\PSIG Connect | aDipset | String |  |  | 2 | Distance Circular;Distance Circular\PSIG Connect;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Circular\PSIG Connect | aDipset | String
[18 empty] | Distance Polygonal\PSIG Connect | aDipset | String |  |  |  | Distance Polygonal;Distance Polygonal\PSIG Connect;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\PSIG Connect | aDipset | String
x024_u002E_000 | Parametersatz 2->SV | 024.000 | keine¦0;direkte Schaltermitn¦1;anregeabh. Mitnahme¦2;Meßbereichserweiter.¦3;Freigabeverfahren¦4;Sperrverfahren¦5;GS-Schleife¦6;rückwärtige Verrieg.¦7;Richtungsvergleich¦8 |  | Betriebsart PS2 | Enum | Parameter__Funktionsparameter | ;DIRECT = TRIP;PUTT = TRIP;POTT = TRIP;COMP_RELEASE = TRIP;COMP_BLOCK = TRIP;COMP_PILOT = TRIP; | String |  | x003_u002E_060 | E | 2 | PUTT = TRIP | 4 |  |  | Distance Circular\PSIG Receive | sLogic | String |  |  | 2 | Distance Circular;Distance Circular\PSIG Receive;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Circular\PSIG Receive | sLogic | String
[18 empty] | Distance Circular\PSIG Send | sLogic | String |  |  |  | Distance Polygonal;Distance Polygonal\PSIG Receive;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\PSIG Receive | sLogic | String
[18 empty] | Distance Polygonal\PSIG Receive | sLogic | String
[18 empty] | Distance Polygonal\PSIG Send | sLogic | String
x024_u002E_003 | Parametersatz 2->SV | 024.003 | 0-60:0.001;blockiert=60.002 | s | Startzeit PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 0.08 | 4 | SE | 60 | Distance Circular\PSIG T | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\PSIG T;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Circular\PSIG T | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Circular\PSIG T | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
[16 empty] | SE | 60 | Distance Polygonal\PSIG T | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\PSIG T;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Polygonal\PSIG T | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Polygonal\PSIG T | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
x024_u002E_001 | Parametersatz 2->SV | 024.001 | 0-10:0.001 | s | Rückf.zeit Send. PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 0.25 | 2 |  |  | Distance Circular\PSIG T Reset | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\PSIG T Reset;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Circular\PSIG T Reset | Tdelay | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\PSIG T Reset | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\PSIG T Reset;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\PSIG T Reset | Tdelay | Real |  |  | 1 | 0
x073_u002E_098 | Parametersatz 2->UMZ | 073.098 | nein¦0;ja¦1 |  | Freigabe PS2 | Enum | Parameter__Funktionsparameter | 1;0 | Real |  | x056_u002E_008;x003_u002E_060 | E;E | 0;2 | 1 | 12 |  |  | Overcurrent\I> | outserv | Real | 1 | 0 |  | x056_u002E_008;x003_u002E_060 |  |  | E;E | 0;2 | 12 | Overcurrent\I> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\I>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\I>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\I>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\I>>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\I>>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\I>>>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\IN> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\IN> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\IN>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\IN>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\IN>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\IN>>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\IN>>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\IN>>>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\Ineg> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\Ineg> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\Ineg>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\Ineg>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\Ineg>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\Ineg>>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\Ineg>>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\Ineg>>>> | outserv | Real |  |  | 1 | 0
x073_u002E_007 | Parametersatz 2->UMZ | 073.007 | 0.1-20:0.01 | Inom | I> PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 |  |  | Overcurrent\I> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 3 | Overcurrent\I> | Ipset | Real | G | 20 | 0 | 20
[18 empty] | Overcurrent\I> | idir | Real | 0 | 0 | [7 empty] | Overcurrent\I> | Ipset | Real | S | 0.1 | 0 | 0.1
[30 empty] | Overcurrent\I> | Ipset | Real |  |  | 1 | 0
x073_u002E_008 | Parametersatz 2->UMZ | 073.008 | 0.1-20:0.01 | Inom | I>> PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 |  |  | Overcurrent\I>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 3 | Overcurrent\I>> | Ipset | Real | G | 20 | 0 | 20
[18 empty] | Overcurrent\I>> | idir | Real | 0 | 0 | [7 empty] | Overcurrent\I>> | Ipset | Real | S | 0.1 | 0 | 0.1
[30 empty] | Overcurrent\I>> | Ipset | Real |  |  | 1 | 0
x073_u002E_009 | Parametersatz 2->UMZ | 073.009 | 0.1-20:0.01 | Inom | I>>> PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 |  |  | Overcurrent\I>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 3 | Overcurrent\I>>> | Ipset | Real | G | 20 | 0 | 20
[18 empty] | Overcurrent\I>>> | idir | Real | 0 | 0 | [7 empty] | Overcurrent\I>>> | Ipset | Real | S | 0.1 | 0 | 0.1
[30 empty] | Overcurrent\I>>> | Ipset | Real |  |  | 1 | 0
x073_u002E_010 | Parametersatz 2->UMZ | 073.010 | 0.1-20:0.01 | Inom | I>>>> PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 |  |  | Overcurrent\I>>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 3 | Overcurrent\I>>>> | Ipset | Real | G | 20 | 0 | 20
[18 empty] | Overcurrent\I>>>> | idir | Real | 0 | 0 | [7 empty] | Overcurrent\I>>>> | Ipset | Real | S | 0.1 | 0 | 0.1
[30 empty] | Overcurrent\I>>>> | Ipset | Real |  |  | 1 | 0
x073_u002E_019 | Parametersatz 2->UMZ | 073.019 | 0-30:0.001;blockiert=30.002 | s | tI> PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 | SE | 30 | Overcurrent\I> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Overcurrent\I> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\I> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x073_u002E_020 | Parametersatz 2->UMZ | 073.020 | 0-30:0.001;blockiert=30.002 | s | tI>> PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 | SE | 30 | Overcurrent\I>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Overcurrent\I>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\I>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x073_u002E_021 | Parametersatz 2->UMZ | 073.021 | 0-30:0.001;blockiert=30.002 | s | tI>>> PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 | SE | 30 | Overcurrent\I>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Overcurrent\I>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\I>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x073_u002E_022 | Parametersatz 2->UMZ | 073.022 | 0-30:0.001;blockiert=30.002 | s | tI>>>> PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 | SE | 30 | Overcurrent\I>>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Overcurrent\I>>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\I>>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x073_u002E_011 | Parametersatz 2->UMZ | 073.011 | 0.1-20:0.01 | Inom | Igegen> PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1 |  |  |  | Overcurrent\IN> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\IN> | Ipset | Real |  |  | 1 | 0
x073_u002E_012 | Parametersatz 2->UMZ | 073.012 | 0.1-20:0.01 | Inom | Igegen>> PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1 |  |  |  | Overcurrent\IN>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\IN>> | Ipset | Real |  |  | 1 | 0
x073_u002E_013 | Parametersatz 2->UMZ | 073.013 | 0.1-20:0.01 | Inom | Igegen>>> PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1 |  |  |  | Overcurrent\IN>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\IN>>> | Ipset | Real |  |  | 1 | 0
x073_u002E_014 | Parametersatz 2->UMZ | 073.014 | 0.1-20:0.01 | Inom | Igegen>>>> PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1 |  |  |  | Overcurrent\IN>>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\IN>>>> | Ipset | Real |  |  | 1 | 0
x073_u002E_023 | Parametersatz 2->UMZ | 073.023 | 0-30:0.001;blockiert=30.002 | s | tIgegen> PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 | SE | 30 | Overcurrent\IN> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Overcurrent\IN> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\IN> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x073_u002E_024 | Parametersatz 2->UMZ | 073.024 | 0-30:0.001;blockiert=30.002 | s | tIgegen>> PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 | SE | 30 | Overcurrent\IN>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Overcurrent\IN>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\IN>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x073_u002E_025 | Parametersatz 2->UMZ | 073.025 | 0-30:0.001;blockiert=30.002 | s | tIgegen>>> PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 | SE | 30 | Overcurrent\IN>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Overcurrent\IN>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\IN>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x073_u002E_026 | Parametersatz 2->UMZ | 073.026 | 0-30:0.001;blockiert=30.002 | s | tIgegen>>>> PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 | SE | 30 | Overcurrent\IN>>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Overcurrent\IN>>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\IN>>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x073_u002E_015 | Parametersatz 2->UMZ | 073.015 | 0.1-20:0.01 | Inom | IE> PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1 |  |  |  | Overcurrent\Ineg> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\Ineg> | Ipset | Real |  |  | 1 | 0
x073_u002E_016 | Parametersatz 2->UMZ | 073.016 | 0.1-20:0.01 | Inom | IE>> PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1 |  |  |  | Overcurrent\Ineg>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\Ineg>> | Ipset | Real |  |  | 1 | 0
x073_u002E_017 | Parametersatz 2->UMZ | 073.017 | 0.1-20:0.01 | Inom | IE>>> PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1 |  |  |  | Overcurrent\Ineg>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\Ineg>>> | Ipset | Real |  |  | 1 | 0
x073_u002E_018 | Parametersatz 2->UMZ | 073.018 | 0.1-20:0.01 | Inom | IE>>>> PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1 |  |  |  | Overcurrent\Ineg>>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\Ineg>>>> | Ipset | Real |  |  | 1 | 0
x073_u002E_027 | Parametersatz 2->UMZ | 073.027 | 0-30:0.001;blockiert=30.002 | s | tIE> PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 | SE | 30 | Overcurrent\Ineg> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Overcurrent\Ineg> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\Ineg> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x073_u002E_028 | Parametersatz 2->UMZ | 073.028 | 0-30:0.001;blockiert=30.002 | s | tIE>> PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 | SE | 30 | Overcurrent\Ineg>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Overcurrent\Ineg>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\Ineg>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x073_u002E_029 | Parametersatz 2->UMZ | 073.029 | 0-30:0.001;blockiert=30.002 | s | tIE>>> PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 | SE | 30 | Overcurrent\Ineg>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Overcurrent\Ineg>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\Ineg>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x073_u002E_030 | Parametersatz 2->UMZ | 073.030 | 0-30:0.001;blockiert=30.002 | s | tIE>>>> PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 | SE | 30 | Overcurrent\Ineg>>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Overcurrent\Ineg>>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\Ineg>>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x010_u002E_060 | Parametersatz 2->UMZ | 010.060 | 0.01-0.5:0.001 | Unom/©3 | UNE> PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 0.03 |  |  |  | Overcurrent\Directional N | upolu | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\Directional N | upolu | Real |  |  | 1 | 0
x004_u002E_247 | Parametersatz 2->UMZ | 004.247 | -90-90:1 | ° | Winkel phiE PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 0 |  |  |  | Overcurrent\Directional N | mtau | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\Directional N | mtau | Real |  |  | 1 | 0
x072_u002E_042 | Parametersatz 2->UMZ | 072.042 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung tIE> PS2 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real |  | x003_u002E_060 | E | 2 | 1 |  |  |  | Overcurrent\IN> | idir | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\IN> | idir | Real |  |  | 1 | 0
x072_u002E_043 | Parametersatz 2->UMZ | 072.043 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung tIE>> PS2 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real |  | x003_u002E_060 | E | 2 | 1 |  |  |  | Overcurrent\IN>> | idir | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\IN>> | idir | Real |  |  | 1 | 0
x072_u002E_044 | Parametersatz 2->UMZ | 072.044 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung tIE>>> PS2 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real |  | x003_u002E_060 | E | 2 | 1 |  |  |  | Overcurrent\IN>>> | idir | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\IN>>> | idir | Real |  |  | 1 | 0
x072_u002E_045 | Parametersatz 2->UMZ | 072.045 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung tIE>>>> PS2 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real |  | x003_u002E_060 | E | 2 | 1 |  |  |  | Overcurrent\IN>>>> | idir | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\IN>>>> | idir | Real |  |  | 1 | 0
x073_u002E_000 | Parametersatz 2->AMZ | 073.000 | nein¦0;ja¦1 |  | Freigabe PS2 | Enum | Parameter__Funktionsparameter | 1;0 | Real |  | x056_u002E_009;x003_u002E_060 | E;E | 0;2 | 1 |  |  |  | Overcurrent\IDMT P | outserv | Real | 1 | 0 |  | x056_u002E_009;x003_u002E_060 |  |  | E;E | 0;2 | 3 | Overcurrent\IDMT P | outserv | Real | E | 0 |  | 0
[18 empty] | Overcurrent\IDMT neg | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\IDMT neg | outserv | Real | E | 0 |  | 0
[18 empty] | Overcurrent\IDMT N | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\IDMT N | outserv | Real |  |  | 1 | 0
x073_u002E_050 | Parametersatz 2->AMZ | 073.050 | 0.1-4:0.01;blockiert=4.02 | Inom | IB,L PS2 | Real | Parameter__Funktionsparameter |  |  |  | x073_u002E_000;x003_u002E_060 | E;E | 0;2 | 1 | 4 | SE | 4 | Overcurrent\IDMT P | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Overcurrent\IDMT P | outserv | Real | E | 1 | 0 | 4.02
[16 empty] | SE | 4 | Overcurrent\IDMT P | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\IDMT P | Ipset | Real |  |  | 1 | 0
[16 empty] | G | 4 | Overcurrent\IDMT P | outserv | Real | 0 | 1
[18 empty] | Overcurrent\IDMT KI P | outserv | Real | 0 | 1
x073_u002E_056 | Parametersatz 2->AMZ | 073.056 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Kennlinientyp L PS2 | Enum | Parameter__Funktionsparameter | Definite Time;IEC 255-3 Standard Inverse;IEC 255-3 Very Inverse;IEC 255-3 Extremly Inverse;IEC 255-3 Long-Time Inverse;IEEE C37.112 Moderately Inverse;IEEE C37.112 Very Inverse;IEEE C37.112 Extremely Inverse;ANSI Normally Inverse;ANSI Short-Time Inverse;ANSI Long-Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | [8 empty] | Overcurrent\IDMT P | pcharac |  |  |  |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\IDMT P | pcharac
x073_u002E_053 | Parametersatz 2->AMZ | 073.053 | 0.01-10:0.01 |  | Kennl.fakt. kt,L PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 |  |  | Overcurrent\IDMT P | Tpset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\IDMT P | Tpset | Real |  |  | 1 | 0
[18 empty] | Overcurrent\IDMT P | udeftmin | Real | 0 | 0
x073_u002E_059 | Parametersatz 2->AMZ | 073.059 | unverzögert¦0;verzögert gem. Kennl¦1 |  | Rückfallen L PS2 | Enum | Parameter__Funktionsparameter | 0;1 | Real | 3 | x003_u002E_060;x073_u002E_056 | E;SW | 2;IEEE | 0 |  |  |  | Overcurrent\IDMT P | resetdis | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\IDMT P | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x073_u002E_056 | E;SW | 2;ANSI |  |  |  |  | Overcurrent\IDMT P | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | 2 |  |  |  |  | Overcurrent\IDMT P | resetdis | Real | 0 | 0
x073_u002E_062 | Parametersatz 2->AMZ | 073.062 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung L PS2 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real |  | x003_u002E_060 | E | 2 |  |  |  |  | Overcurrent\IDMT P | idir | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\IDMT P | idir | Real |  |  | 1 | 0
x073_u002E_051 | Parametersatz 2->AMZ | 073.051 | 0.1-4:0.01;blockiert=4.02 | Inom | IB,gegen PS2 | Real | Parameter__Funktionsparameter |  |  |  | x073_u002E_000;x003_u002E_060 | E;E | 0;2 | 1 | 4 | SE | 4 | Overcurrent\IDMT neg | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 3 | Overcurrent\IDMT neg | outserv | Real | E | 1 | 0 | 4.02
[16 empty] | SE | 4 | Overcurrent\IDMT neg | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\IDMT neg | Ipset | Real | GE | 0.1 | 1 | 0
[16 empty] | G | 4 | Overcurrent\IDMT neg | outserv | Real | 0 | 1 | [13 empty] | 0.1
[18 empty] | Overcurrent\IDMT KI neg | outserv | Real | 0 | 1
x073_u002E_057 | Parametersatz 2->AMZ | 073.057 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Kennl.typ gegen PS2 | Enum | Parameter__Funktionsparameter | Definite Time;IEC 255-3 Standard Inverse;IEC 255-3 Very Inverse;IEC 255-3 Extremly Inverse;IEC 255-3 Long-Time Inverse;IEEE C37.112 Moderately Inverse;IEEE C37.112 Very Inverse;IEEE C37.112 Extremely Inverse;ANSI Normally Inverse;ANSI Short-Time Inverse;ANSI Long-Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | [8 empty] | Overcurrent\IDMT neg | pcharac |  |  |  |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\IDMT neg | pcharac
x073_u002E_054 | Parametersatz 2->AMZ | 073.054 | 0.01-10:0.01 |  | Kennl.f. kt,gegn PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 |  |  | Overcurrent\IDMT neg | Tpset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\IDMT neg | Tpset | Real |  |  | 1 | 0
[18 empty] | Overcurrent\IDMT neg | udeftmin | Real | 0 | 0
x073_u002E_060 | Parametersatz 2->AMZ | 073.060 | unverzögert¦0;verzögert gem. Kennl¦1 |  | Rückfallen gegen PS2 | Enum | Parameter__Funktionsparameter | 0;1 | Real | 3 | x003_u002E_060;x073_u002E_057 | E;SW | 2;IEEE | 0 |  |  |  | Overcurrent\IDMT neg | resetdis | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\IDMT neg | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x073_u002E_057 | E;SW | 2;ANSI |  |  |  |  | Overcurrent\IDMT neg | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | 2 |  |  |  |  | Overcurrent\IDMT neg | resetdis | Real | 0 | 0
x073_u002E_052 | Parametersatz 2->AMZ | 073.052 | 0.1-4:0.01;blockiert=4.02 | Inom | IB,E (gerechnet) PS2 | Real | Parameter__Funktionsparameter |  |  |  | x073_u002E_000;x003_u002E_060 | E;E | 0;2 | 1 | 4 | SE | 4 | Overcurrent\IDMT N | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 3 | Overcurrent\IDMT N | outserv | Real | E | 1 | 0 | 4.02
[16 empty] | SE | 4 | Overcurrent\IDMT N | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\IDMT N | Ipset | Real | GE | 0.1 | 1 | 0
[16 empty] | G | 4 | Overcurrent\IDMT N | outserv | Real | 0 | 1 | [13 empty] | 0.1
[18 empty] | Overcurrent\IDMT KI N | outserv | Real | 0 | 1
x073_u002E_058 | Parametersatz 2->AMZ | 073.058 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Kennlinientyp E PS2 | Enum | Parameter__Funktionsparameter | Definite Time;IEC 255-3 Standard Inverse;IEC 255-3 Very Inverse;IEC 255-3 Extremly Inverse;IEC 255-3 Long-Time Inverse;IEEE C37.112 Moderately Inverse;IEEE C37.112 Very Inverse;IEEE C37.112 Extremely Inverse;ANSI Normally Inverse;ANSI Short-Time Inverse;ANSI Long-Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | [8 empty] | Overcurrent\IDMT N | pcharac |  |  |  |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\IDMT N | pcharac
x073_u002E_055 | Parametersatz 2->AMZ | 073.055 | 0.01-10:0.01 |  | Kennl.f. kt,E PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 |  |  | Overcurrent\IDMT N | Tpset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\IDMT N | Tpset | Real |  |  | 1 | 0
[18 empty] | Overcurrent\IDMT N | udeftmin | Real | 0 | 0
x073_u002E_061 | Parametersatz 2->AMZ | 073.061 | unverzögert¦0;verzögert gem. Kennl¦1 |  | Rückfallen E PS2 | Enum | Parameter__Funktionsparameter | 0;1 | Real | 3 | x003_u002E_060;x073_u002E_058 | E;SW | 2;IEEE | 0 |  |  |  | Overcurrent\IDMT N | resetdis | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\IDMT N | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x073_u002E_058 | E;SW | 2;ANSI |  |  |  |  | Overcurrent\IDMT N | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | 2 |  |  |  |  | Overcurrent\IDMT N | resetdis | Real | 0 | 0
x073_u002E_062 | Parametersatz 2->AMZ | 073.062 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung L PS2 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real |  | x003_u002E_060 | E | 2 |  |  |  |  | Overcurrent\IDMT N | idir | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\IDMT N | idir | Real |  |  | 1 | 0
x077_u002E_000 | Parametersatz 2->U<> | 077.000 | nein¦0;ja¦1 |  | Freigabe PS2 | Enum | Parameter__Funktionsparameter | 1;0 | Real |  | x056_u002E_010;x003_u002E_060 | E;E | 0;2 | 1 |  |  |  | Voltage | outserv | Real | 1 | 0 |  | x056_u002E_010;x003_u002E_060 |  |  | E;E | 0;2 |  | Voltage | outserv | Real |  |  | 1 | 0
x077_u002E_001 | Parametersatz 2->U<> | 077.001 | Dreieck¦0;Stern¦1 |  | Betriebsart PS2 | Enum | Parameter__Funktionsparameter | 0;1 | Real |  | x077_u002E_000;x003_u002E_060 | E;E | 0;2 | 0 | 16 | E | 0 | Voltage\V< LE | outserv | Real | 0 | 1
[16 empty] | E | 0 | Voltage\V< LL | outserv | Real | 0 | 0
[16 empty] | E | 0 | Voltage\V<< LE | outserv | Real | 0 | 1
[16 empty] | E | 0 | Voltage\V<< LL | outserv | Real | 0 | 0
[16 empty] | E | 0 | Voltage\V> LE | outserv | Real | 0 | 1
[16 empty] | E | 0 | Voltage\V> LL | outserv | Real | 0 | 0
[16 empty] | E | 0 | Voltage\V>> LE | outserv | Real | 0 | 1
[16 empty] | E | 0 | Voltage\V>> LL | outserv | Real | 0 | 0
[16 empty] | E | 1 | Voltage\V< LE | outserv | Real | 0 | 0
[16 empty] | E | 1 | Voltage\V< LL | outserv | Real | 0 | 1
[16 empty] | E | 1 | Voltage\V<< LE | outserv | Real | 0 | 0
[16 empty] | E | 1 | Voltage\V<< LL | outserv | Real | 0 | 1
[16 empty] | E | 1 | Voltage\V> LE | outserv | Real | 0 | 0
[16 empty] | E | 1 | Voltage\V> LL | outserv | Real | 0 | 1
[16 empty] | E | 1 | Voltage\V>> LE | outserv | Real | 0 | 0
[16 empty] | E | 1 | Voltage\V>> LL | outserv | Real | 0 | 1
x077_u002E_003 | Parametersatz 2->U<> | 077.003 | 0.2-1.5:0.01;blockiert=1.52 | Unom(/©3) | U> PS2 | Real | Parameter__Funktionsparameter |  |  | 2 | x077_u002E_001;x003_u002E_060 | E;E | 0;2 | 1.1 | 3 | SE | 1.5 | Voltage\V> LL | Uset | Real | 1 | 0 | 2 | x077_u002E_001;x003_u002E_060 |  |  | E;E | 0;2 | 3 | Voltage\V> LL | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V> LL | outserv | Real | 0 | 0 | [7 empty] | Voltage\V> LL | Uset | Real | GE | 0.2 | 1 | 0
[16 empty] | G | 1.5 | Voltage\V> LL | outserv | Real | 0 | 1 | [13 empty] | 0.2
[11 empty] | x077_u002E_001;x003_u002E_060 | E;E | 1;2 |  | 3 | SE | 1.5 | Voltage\V> LE | Uset | Real | 1 | 0 |  | x077_u002E_001;x003_u002E_060 |  |  | E;E | 1;2 | 3 | Voltage\V> LE | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V> LE | outserv | Real | 0 | 0 | [7 empty] | Voltage\V> LE | Uset | Real | GE | 0.2 | 1 | 0
[16 empty] | G | 1.5 | Voltage\V> LE | outserv | Real | 0 | 1 | [13 empty] | 0.2
x077_u002E_004 | Parametersatz 2->U<> | 077.004 | 0.2-1.5:0.01;blockiert=1.52 | Unom(/©3) | U>> PS2 | Real | Parameter__Funktionsparameter |  |  | 2 | x077_u002E_001;x003_u002E_060 | E;E | 0;2 | 1.1 | 3 | SE | 1.5 | Voltage\V>> LL | Uset | Real | 1 | 0 | 2 | x077_u002E_001;x003_u002E_060 |  |  | E;E | 0;2 | 3 | Voltage\V>> LL | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V>> LL | outserv | Real | 0 | 0 | [7 empty] | Voltage\V>> LL | Uset | Real | GE | 0.2 | 1 | 0
[16 empty] | G | 1.5 | Voltage\V>> LL | outserv | Real | 0 | 1 |  | x077_u002E_001;x003_u002E_060 | [11 empty] | 0.2
[11 empty] | x077_u002E_001;x003_u002E_060 | E;E | 1;2 |  | 3 | SE | 1.5 | Voltage\V>> LE | Uset | Real | 1 | 0 |  |  |  |  | E;E | 1;2 | 3 | Voltage\V>> LE | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V>> LE | outserv | Real | 0 | 0 | [7 empty] | Voltage\V>> LE | Uset | Real | GE | 0.2 | 1 | 0
[16 empty] | G | 1.5 | Voltage\V>> LE | outserv | Real | 0 | 1 | [13 empty] | 0.2
x077_u002E_005 | Parametersatz 2->U<> | 077.005 | 0-100:0.01;blockiert=100.02 | s | tU> PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1 | 4 | SE | 100 | Voltage\V> LL | Tdel | Real | 1 | 0 | 2 | x077_u002E_001;x003_u002E_060 |  |  | E;E | 0;2 | 2 | Voltage\V> LL | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V> LL | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
[16 empty] | SE | 100 | Voltage\V> LE | Tdel | Real | 1 | 0 |  | x077_u002E_001;x003_u002E_060 |  |  | E;E | 1;2 | 2 | Voltage\V> LE | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V> LE | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x077_u002E_006 | Parametersatz 2->U<> | 077.006 | 0-100:0.01;blockiert=100.02 | s | tU>> PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1 | 4 | SE | 100 | Voltage\V>> LL | Tdel | Real | 1 | 0 |  | x077_u002E_001;x003_u002E_060 |  |  | E;E | 0;2 | 2 | Voltage\V>> LL | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V>> LL | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
[16 empty] | SE | 100 | Voltage\V>> LE | Tdel | Real | 1 | 0 |  | x077_u002E_001;x003_u002E_060 |  |  | E;E | 1;2 | 2 | Voltage\V>> LE | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V>> LE | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x077_u002E_007 | Parametersatz 2->U<> | 077.007 | 0.2-1.5:0.01;blockiert=1.52 | Unom(/©3) | U< PS2 | Real | Parameter__Funktionsparameter |  |  | 2 | x077_u002E_001;x003_u002E_060 | E;E | 0;2 | 0.8 | 3 | SE | 1.5 | Voltage\V< LL | Uset | Real | 1 | 0 | 2 | x077_u002E_001;x003_u002E_060 |  |  | E;E | 0;2 | 2 | Voltage\V< LL | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V< LL | outserv | Real | 0 | 0 | [7 empty] | Voltage\V< LL | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\V< LL | outserv | Real | 0 | 1 |  | x077_u002E_001;x003_u002E_060 |  |  | E;E | 1;2 | 2 | Voltage\V< LE | outserv | Real | E | 1 | 0 | 1.52
[11 empty] | x077_u002E_001;x003_u002E_060 | E;E | 1;2 | 0.8 |  | SE | 1.5 | Voltage\V< LE | Uset | Real | 1 | 0 | [7 empty] | Voltage\V< LE | Uset | Real |  |  | 1 | 0
[16 empty] | SE | 1.5 | Voltage\V< LE | outserv | Real | 0 | 0
[16 empty] | G | 1.5 | Voltage\V< LE | outserv | Real | 0 | 1
x077_u002E_008 | Parametersatz 2->U<> | 077.008 | 0.2-1.5:0.01;blockiert=1.52 | Unom(/©3) | U<< PS2 | Real | Parameter__Funktionsparameter |  |  | 2 | x077_u002E_001;x003_u002E_060 | E;E | 0;2 | 0.8 | 3 | SE | 1.5 | Voltage\V<< LL | Uset | Real | 1 | 0 | 2 | x077_u002E_001;x003_u002E_060 |  |  | E;E | 0;2 | 2 | Voltage\V<< LL | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V<< LL | outserv | Real | 0 | 0 | [7 empty] | Voltage\V<< LL | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\V<< LL | outserv | Real | 0 | 1 |  | x077_u002E_001;x003_u002E_060 |  |  | E;E | 1;2 | 2 | Voltage\V<< LE | outserv | Real | E | 1 | 0 | 1.52
[11 empty] | x077_u002E_001;x003_u002E_060 | E;E | 1;2 | 0.8 |  | SE | 1.5 | Voltage\V<< LE | Uset | Real | 1 | 0 | [7 empty] | Voltage\V<< LE | Uset | Real |  |  | 1 | 0
[16 empty] | SE | 1.5 | Voltage\V<< LE | outserv | Real | 0 | 0
[16 empty] | G | 1.5 | Voltage\V<< LE | outserv | Real | 0 | 1
x077_u002E_009 | Parametersatz 2->U<> | 077.009 | 0-100:0.01;blockiert=100.02 | s | tU< PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1 | 4 | SE | 100 | Voltage\V< LL | Tdel | Real | 1 | 0 |  | x077_u002E_001;x003_u002E_060 |  |  | E;E | 0;2 | 2 | Voltage\V< LL | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V< LL | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
[16 empty] | SE | 100 | Voltage\V< LE | Tdel | Real | 1 | 0 |  | x077_u002E_001;x003_u002E_060 |  |  | E;E | 1;2 | 2 | Voltage\V< LE | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V< LE | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x077_u002E_010 | Parametersatz 2->U<> | 077.010 | 0-100:0.01;blockiert=100.02 | s | tU<< PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1 | 4 | SE | 100 | Voltage\V<< LL | Tdel | Real | 1 | 0 |  | x077_u002E_001;x003_u002E_060 |  |  | E;E | 0;2 | 2 | Voltage\V<< LL | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V<< LL | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
[16 empty] | SE | 100 | Voltage\V<< LE | Tdel | Real | 1 | 0 |  | x077_u002E_001;x003_u002E_060 |  |  | E;E | 1;2 | 2 | Voltage\V<< LE | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V<< LE | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x077_u002E_015 | Parametersatz 2->U<> | 077.015 | 0.2-1.5:0.01;blockiert=1.52 | Unom/©3 | Umit> PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1.1 | 3 | SE | 1.5 | Voltage\Vpos> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 3 | Voltage\Vpos> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos> | Uset | Real | GE | 0.2 | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vpos> | outserv | Real | 0 | 1 | [13 empty] | 0.2
x077_u002E_016 | Parametersatz 2->U<> | 077.016 | 0.2-1.5:0.01;blockiert=1.52 | Unom/©3 | Umit>> PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1.1 | 3 | SE | 1.5 | Voltage\Vpos>> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 3 | Voltage\Vpos>> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos>> | Uset | Real | GE | 0.2 | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vpos>> | outserv | Real | 0 | 1 | [13 empty] | 0.2
x077_u002E_017 | Parametersatz 2->U<> | 077.017 | 0-100:0.01;blockiert=100.02 | s | tUmit> PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 | SE | 100 | Voltage\Vpos> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Voltage\Vpos> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vpos> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x077_u002E_018 | Parametersatz 2->U<> | 077.018 | 0-100:0.01;blockiert=100.02 | s | tUmit>> PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 | SE | 100 | Voltage\Vpos>> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Voltage\Vpos>> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vpos>> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x077_u002E_019 | Parametersatz 2->U<> | 077.019 | 0.2-1.5:0.01;blockiert=1.52 | Unom/©3 | Umit< PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 0.8 | 3 | SE | 1.5 | Voltage\Vpos< | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 3 | Voltage\Vpos< | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos< | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos< | Uset | Real | GE | 0.2 | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vpos< | outserv | Real | 0 | 1 | [13 empty] | 0.2
x077_u002E_020 | Parametersatz 2->U<> | 077.020 | 0.2-1.5:0.01;blockiert=1.52 | Unom/©3 | Umit<< PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 0.8 | 3 | SE | 1.5 | Voltage\Vpos<< | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 3 | Voltage\Vpos<< | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos<< | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos<< | Uset | Real | GE | 0.2 | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vpos<< | outserv | Real | 0 | 1 | [13 empty] | 0.2
x077_u002E_021 | Parametersatz 2->U<> | 077.021 | 0-100:0.01;blockiert=100.02 | s | tUmit< PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 | SE | 100 | Voltage\Vpos< | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Voltage\Vpos< | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vpos< | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x077_u002E_022 | Parametersatz 2->U<> | 077.022 | 0-100:0.01;blockiert=100.02 | s | tUmit<< PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 | SE | 100 | Voltage\Vpos<< | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Voltage\Vpos<< | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vpos<< | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x077_u002E_023 | Parametersatz 2->U<> | 077.023 | 0.2-1.5:0.01;blockiert=1.52 | Unom/©3 | Ugegen> PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1.52 | 3 | SE | 1.5 | Voltage\Vneg> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 3 | Voltage\Vneg> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vneg> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vneg> | Uset | Real | GE | 0.2 | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vneg> | outserv | Real | 0 | 1 | [13 empty] | 0.2
x077_u002E_024 | Parametersatz 2->U<> | 077.024 | 0.2-1.5:0.01;blockiert=1.52 | Unom/©3 | Ugegen>> PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1.52 | 3 | SE | 1.5 | Voltage\Vneg>> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 3 | Voltage\Vneg>> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vneg>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vneg>> | Uset | Real | GE | 0.2 | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vneg>> | outserv | Real | 0 | 1 | [13 empty] | 0.2
x077_u002E_025 | Parametersatz 2->U<> | 077.025 | 0-100:0.01;blockiert=100.02 | s | tUgegen> PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 | SE | 100 | Voltage\Vneg> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Voltage\Vneg> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vneg> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x077_u002E_026 | Parametersatz 2->U<> | 077.026 | 0-100:0.01;blockiert=100.02 | s | tUgegen>> PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 | SE | 100 | Voltage\Vneg>> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Voltage\Vneg>> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vneg>> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x077_u002E_011 | Parametersatz 2->U<> | 077.011 | 0.02-1:0.01;blockiert=1.02 | Unom(/©3) | UNE> PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1.02 | 3 | SE | 1 | Voltage\VNG> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Voltage\VNG> | outserv | Real | E | 1 | 0 | 1.02
[16 empty] | SE | 1 | Voltage\VNG> | outserv | Real | 0 | 0 | [7 empty] | Voltage\VNG> | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1 | Voltage\VNG> | outserv | Real | 0 | 1
x077_u002E_012 | Parametersatz 2->U<> | 077.012 | 0.02-1:0.01;blockiert=1.02 | Unom(/©3) | UNE>> PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1.02 | 3 | SE | 1 | Voltage\VNG>> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Voltage\VNG>> | outserv | Real | E | 1 | 0 | 1.02
[16 empty] | SE | 1 | Voltage\VNG>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\VNG>> | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1 | Voltage\VNG>> | outserv | Real | 0 | 1
x077_u002E_013 | Parametersatz 2->U<> | 077.013 | 0-100:0.01;blockiert=100.02 | s | tUNE> PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 | SE | 100 | Voltage\VNG> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Voltage\VNG> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\VNG> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x077_u002E_014 | Parametersatz 2->U<> | 077.014 | 0-100:0.01;blockiert=100.02 | s | tUNE>> PS2 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 | SE | 100 | Voltage\VNG>> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Voltage\VNG>> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\VNG>> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x018_u002E_197 | Parametersatz 2->f<> | 018.197 | nein¦0;ja¦1 |  | Freigabe PS2 | Enum | Parameter__Funktionsparameter | 1;0 | Real |  | x056_u002E_033;x003_u002E_060 | E;E | 0;2 | 1 |  |  |  | Frequency | outserv | Real | 1 | 0 |  | x056_u002E_033;x003_u002E_060 |  |  | E;E | 0;2 |  | Frequency | outserv | Real |  |  | 1 | 0
x018_u002E_121 | Parametersatz 2->f<> | 018.121 | f¦0;f mit df/dt¦1;f m. Delta f/Delta t¦2 |  | Betriebsart f1 PS2 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 2 | 0 |  | NE | 0 | Frequency\f1 | outserv | Real | 0 | 1
x018_u002E_101 | Parametersatz 2->f<> | 018.101 | 40-70:0.01;blockiert=70.02 | Hz | f1 PS2 | Real | Parameter__Funktionsparameter |  |  |  | x018_u002E_121;x003_u002E_060 | E;E | 0;2 | 49.8 | 3 | SE | 70 | Frequency\f1 | Fset | Real | 1 | 0 |  | x018_u002E_121;x003_u002E_060 |  |  | E;E | 0;2 | 2 | Frequency\f1 | outserv | Real | E | 1 | 0 | 70.02
[16 empty] | SE | 70 | Frequency\f1 | outserv | Real | 0 | 0 | [7 empty] | Frequency\f1 | Uset | Real |  |  | 1 | 0
[16 empty] | G | 70 | Frequency\f1 | outserv | Real | 0 | 1
x018_u002E_105 | Parametersatz 2->f<> | 018.105 | 0-10:0.001;blockiert=10.002 | s | tf1 PS2 | Real | Parameter__Funktionsparameter |  |  |  | x018_u002E_121;x003_u002E_060 | E;E | 0;2 | 0 | 2 | SE | 10 | Frequency\f1 | Tdel | Real | 1 | 0 |  | x018_u002E_121;x003_u002E_060 |  |  | E;E | 0;2 | 2 | Frequency\f1 | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Frequency\f1 | Tdel | Real | 0 | 9999999 | [13 empty] | 10.002
x018_u002E_145 | Parametersatz 2->f<> | 018.145 | f¦0;f mit df/dt¦1;f m. Delta f/Delta t¦2 |  | Betriebsart f2 PS2 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 2 | 0 |  | NE | 0 | Frequency\f2 | outserv | Real | 0 | 1
x018_u002E_125 | Parametersatz 2->f<> | 018.125 | 40-70:0.01;blockiert=70.02 | Hz | f2 PS2 | Real | Parameter__Funktionsparameter |  |  |  | x018_u002E_145;x003_u002E_060 | E;E | 0;2 | 49.8 | 3 | SE | 70 | Frequency\f2 | Fset | Real | 1 | 0 |  | x018_u002E_145;x003_u002E_060 |  |  | E;E | 0;2 | 2 | Frequency\f2 | outserv | Real | E | 1 | 0 | 70.02
[16 empty] | SE | 70 | Frequency\f2 | outserv | Real | 0 | 0 | [7 empty] | Frequency\f2 | Uset | Real |  |  | 1 | 0
[16 empty] | G | 70 | Frequency\f2 | outserv | Real | 0 | 1
x018_u002E_129 | Parametersatz 2->f<> | 018.129 | 0-10:0.001;blockiert=10.002 | s | tf2 PS2 | Real | Parameter__Funktionsparameter |  |  |  | x018_u002E_145;x003_u002E_060 | E;E | 0;2 | 0 | 2 | SE | 10 | Frequency\f2 | Tdel | Real | 1 | 0 |  | x018_u002E_145;x003_u002E_060 |  |  | E;E | 0;2 | 2 | Frequency\f2 | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Frequency\f2 | Tdel | Real | 0 | 9999999 | [13 empty] | 10.002
x018_u002E_169 | Parametersatz 2->f<> | 018.169 | f¦0;f mit df/dt¦1;f m. Delta f/Delta t¦2 |  | Betriebsart f3 PS2 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 2 | 0 |  | NE | 0 | Frequency\f3 | outserv | Real | 0 | 1
x018_u002E_149 | Parametersatz 2->f<> | 018.149 | 40-70:0.01;blockiert=70.02 | Hz | f3 PS2 | Real | Parameter__Funktionsparameter |  |  |  | x018_u002E_169;x003_u002E_060 | E;E | 0;2 | 49.8 | 3 | SE | 70 | Frequency\f3 | Fset | Real | 1 | 0 |  | x018_u002E_169;x003_u002E_060 |  |  | E;E | 0;2 | 2 | Frequency\f3 | outserv | Real | E | 1 | 0 | 70.02
[16 empty] | SE | 70 | Frequency\f3 | outserv | Real | 0 | 0 | [7 empty] | Frequency\f3 | Uset | Real |  |  | 1 | 0
[16 empty] | G | 70 | Frequency\f3 | outserv | Real | 0 | 1
x018_u002E_153 | Parametersatz 2->f<> | 018.153 | 0-10:0.001;blockiert=10.002 | s | tf3 PS2 | Real | Parameter__Funktionsparameter |  |  |  | x018_u002E_169;x003_u002E_060 | E;E | 0;2 | 0 | 2 | SE | 10 | Frequency\f3 | Tdel | Real | 1 | 0 |  | x018_u002E_169;x003_u002E_060 |  |  | E;E | 0;2 | 2 | Frequency\f3 | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Frequency\f3 | Tdel | Real | 0 | 9999999 | [13 empty] | 10.002
x018_u002E_193 | Parametersatz 2->f<> | 018.193 | f¦0;f mit df/dt¦1;f m. Delta f/Delta t¦2 |  | Betriebsart f4 PS2 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 2 | 0 |  | NE | 0 | Frequency\f4 | outserv | Real | 0 | 1
x018_u002E_173 | Parametersatz 2->f<> | 018.173 | 40-70:0.01;blockiert=70.02 | Hz | f4 PS2 | Real | Parameter__Funktionsparameter |  |  |  | x018_u002E_193;x003_u002E_060 | E;E | 0;2 | 49.8 | 3 | SE | 70 | Frequency\f4 | Fset | Real | 1 | 0 |  | x018_u002E_193;x003_u002E_060 |  |  | E;E | 0;2 | 2 | Frequency\f4 | outserv | Real | E | 1 | 0 | 70.02
[16 empty] | SE | 70 | Frequency\f4 | outserv | Real | 0 | 0 | [7 empty] | Frequency\f4 | Uset | Real |  |  | 1 | 0
[16 empty] | G | 70 | Frequency\f4 | outserv | Real | 0 | 1
x018_u002E_177 | Parametersatz 2->f<> | 018.177 | 0-10:0.001;blockiert=10.002 | s | tf4 PS2 | Real | Parameter__Funktionsparameter |  |  |  | x018_u002E_193;x003_u002E_060 | E;E | 0;2 | 0 | 2 | SE | 10 | Frequency\f4 | Tdel | Real | 1 | 0 |  | x018_u002E_193;x003_u002E_060 |  |  | E;E | 0;2 | 2 | Frequency\f4 | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Frequency\f4 | Tdel | Real | 0 | 9999999 | [13 empty] | 10.002
x001_u002E_077 | Parametersatz 3->GRUND | 001.077 | niederohmig geerdet¦0;isol/komp m.Anreg.LE¦1;isol/komp o.Anreg.LE¦2;Kurzzeiterdung¦3 |  | Sternpunktbeh. PS3 | Enum | Parameter__Funktionsparameter | 0;1;2;3;4 | Real |  | x003_u002E_060 | E | 3 | 0 | 4 | E | 0 | Distance Circular\Starting | isysstar | Real | 0 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Circular\Starting | isysstar | Real | E | 0 | 1 | 0
[16 empty] | E | 0 | Distance Polygonal\Starting | isysstar | Real | 0 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Polygonal\Starting | isysstar | Real | E | 0 | 1 | 0
[16 empty] | NE | 0 | Distance Circular\Starting | isysstar | Real | 0 | 1
[16 empty] | NE | 0 | Distance Polygonal\Starting | isysstar | Real | 0 | 1
x001_u002E_080 | Parametersatz 3->GRUND | 001.080 | Erde¦0;LvE=f(Imittel,Imax)¦1 |  | Mitnahme bei 1p PS3 | Enum | Parameter__Funktionsparameter | 0;1 | Real |  | x003_u002E_060 | E | 3 | 0 | 2 |  |  | Distance Circular\Starting | itransf1p | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Circular\Starting | itransf1p | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | itransf1p | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Polygonal\Starting | itransf1p | Real |  |  | 1 | 0
x010_u002E_094 | Parametersatz 3->DIST | 010.094 | 0.1-20:0.01 | Inom | I>> PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 |  |  | Distance Circular\Starting | IMM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Circular\Starting | IMM | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | IMM | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Polygonal\Starting | IMM | Real |  |  | 1 | 0
x011_u002E_008 | Parametersatz 3->DIST | 011.008 | 0.1-1:0.01 | Inom | I> (IF)(max.Ber.)PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 0.2 | 2 |  |  | Distance Circular\Starting | IM1 | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;3 | 2 | Distance Circular\Starting | IM1 | Real | GE | 0.1 | 1 | 0
[18 empty] | Distance Polygonal\Starting | IM1 | Real | 1 | 0 | [13 empty] | 0.1
[24 empty] | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;3 | 2 | Distance Polygonal\Starting | IM1 | Real | GE | 0.1 | 1 | 0
0.1
x010_u002E_121 | Parametersatz 3->DIST | 010.121 | 0.05-1:0.01 | Inom | I> (IF)(emp.Ber.)PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 0.2 | 2 |  |  | Distance Circular\Starting | IM2 | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Circular\Starting | IM2 | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | IM2 | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Polygonal\Starting | IM2 | Real |  |  | 1 | 0
x011_u002E_007 | Parametersatz 3->DIST | 011.007 | ohne U<-Anregung¦0;mit U<-Anreg. nur LE¦1;mit U<-Anreg. LE, LL¦2 |  | Betriebsart U< PS3 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 3 | 2 | 8 | E | 0 | Distance Circular\Starting | iopt_u | Real | 0 | 0 | 4 | Distance Circular;Distance Circular\Starting;x003_u002E_060 | outserv;iopt_u | Real | E;E;E | 0;0;3 | [7 empty] | 0
[16 empty] | E | 0 | Distance Polygonal\Starting | iopt_u | Real | 0 | 0 |  | Distance Circular;Distance Circular\Starting;x003_u002E_060 | outserv;iopt_u | Real | E;E;E | 0;1;3 | 2 | Distance Circular\Starting | iVOpMode | Real | E | 0 | 0 | 1
[16 empty] | NE | 0 | Distance Circular\Starting | iopt_u | Real | 0 | 1 | [7 empty] | Distance Circular\Starting | iVOpMode | Real | E | 1 | 0 | 2
[16 empty] | NE | 0 | Distance Polygonal\Starting | iopt_u | Real | 0 | 1 |  | Distance Polygonal;Distance Polygonal\Starting;x003_u002E_060 | outserv;iopt_u | Real | E;E;E | 0;0;3 | [7 empty] | 0
[16 empty] | E | 1 | Distance Circular\Starting | iVOpMode | Real | 0 | 0 |  | Distance Polygonal;Distance Polygonal\Starting;x003_u002E_060 | outserv;iopt_u | Real | E;E;E | 0;1;3 | 2 | Distance Polygonal\Starting | iVOpMode | Real | E | 0 | 0 | 1
[16 empty] | E | 1 | Distance Polygonal\Starting | iVOpMode | Real | 0 | 0 | [7 empty] | Distance Polygonal\Starting | iVOpMode | Real | E | 1 | 0 | 2
[16 empty] | E | 2 | Distance Circular\Starting | iVOpMode | Real | 0 | 1
[16 empty] | E | 2 | Distance Polygonal\Starting | iVOpMode | Real | 0 | 1
x011_u002E_009 | Parametersatz 3->DIST | 011.009 | 0.1-0.9:0.01 | Unom(/©3) | U< PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 0.7 | 2 |  |  | Distance Circular\Starting | Um | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Circular\Starting | Um | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | Um | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Polygonal\Starting | Um | Real |  |  | 1 | 0
x011_u002E_006 | Parametersatz 3->DIST | 011.006 | ohne Z<-Anregung¦0;mit Z<-Anreg. nur LE¦1;mit Z<-Anreg. LE, LL¦2 |  | Betriebsart Z< PS3 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 3 | 2 | 8 | E | 0 | Distance Circular\Starting | iopt_z | Real | 0 | 0 | 4 | Distance Circular;Distance Circular\Starting;x003_u002E_060 | outserv;iopt_z | Real | E;E;E | 0;0;3 | [7 empty] | 0
[16 empty] | E | 0 | Distance Polygonal\Starting | iopt_z | Real | 0 | 0 |  | Distance Circular;Distance Circular\Starting;x003_u002E_060 | outserv;iopt_z | Real | E;E;E | 0;1;3 | 2 | Distance Circular\Starting | iZOpMode | Real | E | 0 | 0 | 1
[16 empty] | NE | 0 | Distance Circular\Starting | iopt_z | Real | 0 | 1 | [7 empty] | Distance Circular\Starting | iZOpMode | Real | E | 1 | 0 | 2
[16 empty] | NE | 0 | Distance Polygonal\Starting | iopt_z | Real | 0 | 1 |  | Distance Polygonal;Distance Polygonal\Starting;x003_u002E_060 | outserv;iopt_z | Real | E;E;E | 0;0;3 | [7 empty] | 0
[16 empty] | E | 1 | Distance Circular\Starting | iZOpMode | Real | 0 | 0 |  | Distance Polygonal;Distance Polygonal\Starting;x003_u002E_060 | outserv;iopt_z | Real | E;E;E | 0;1;3 | 2 | Distance Polygonal\Starting | iZOpMode | Real | E | 0 | 0 | 1
[16 empty] | E | 1 | Distance Polygonal\Starting | iZOpMode | Real | 0 | 0 | [7 empty] | Distance Polygonal\Starting | iZOpMode | Real | E | 1 | 0 | 2
[16 empty] | E | 2 | Distance Circular\Starting | iZOpMode | Real | 0 | 1
[16 empty] | E | 2 | Distance Polygonal\Starting | iZOpMode | Real | 0 | 1
x010_u002E_090 | Parametersatz 3->DIST | 010.090 | 0.1-300:0.01 | — | Xv PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 10 | 2 |  |  | Distance Circular\Starting | Xfw | Real | 0.2 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;3 | 2 | Distance Circular\Starting | Xfw | Real | SE | 60 | 5 | 0
[18 empty] | Distance Polygonal\Starting | Xfw | Real | 0.2 | 0 | [13 empty] | 300
[24 empty] | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;3 | 2 | Distance Polygonal\Starting | Xfw | Real | SE | 60 | 5 | 0
300
x010_u002E_091 | Parametersatz 3->DIST | 010.091 | 0.1-300:0.01 | — | Rv,LE PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 10 | 2 |  |  | Distance Circular\Starting | RfPG | Real | 0.2 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;3 | 2 | Distance Circular\Starting | RfPG | Real | SE | 60 | 5 | 0
[18 empty] | Distance Polygonal\Starting | RfPG | Real | 0.2 | 0 | [13 empty] | 300
[24 empty] | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;3 | 2 | Distance Polygonal\Starting | RfPG | Real | SE | 60 | 5 | 0
300
x010_u002E_092 | Parametersatz 3->DIST | 010.092 | 0.1-300:0.01 | — | Rv,LL PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 10 | 2 |  |  | Distance Circular\Starting | RfPP | Real | 0.2 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;3 | 2 | Distance Circular\Starting | RfPP | Real | SE | 60 | 5 | 0
[18 empty] | Distance Polygonal\Starting | RfPP | Real | 0.2 | 0 | [13 empty] | 300
[24 empty] | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;3 | 2 | Distance Polygonal\Starting | RfPP | Real | SE | 60 | 5 | 0
300
x011_u002E_003 | Parametersatz 3->DIST | 011.003 | 15-65:1 | ° | ß PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 30 | 2 |  |  | Distance Circular\Starting | Beta | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Circular\Starting | Beta | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | Beta | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Polygonal\Starting | Beta | Real |  |  | 1 | 0
x010_u002E_103 | Parametersatz 3->DIST | 010.103 | 0-300:0.01 | — | Zv,LE PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 0 | 2 |  |  | Distance Circular\Starting | ZfPG | Real | 0.2 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;3 | 2 | Distance Circular\Starting | ZfPG | Real | SE | 60 | 5 | 0
[18 empty] | Distance Polygonal\Starting | ZfPG | Real | 0.2 | 0 | [13 empty] | 300
[24 empty] | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;3 | 2 | Distance Polygonal\Starting | ZfPG | Real | SE | 60 | 5 | 0
300
x010_u002E_107 | Parametersatz 3->DIST | 010.107 | 0-300:0.01 | — | Zv,LL PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 0 | 2 |  |  | Distance Circular\Starting | ZfPP | Real | 0.2 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;3 | 2 | Distance Circular\Starting | ZfPP | Real | SE | 60 | 5 | 0
[18 empty] | Distance Polygonal\Starting | ZfPP | Real | 0.2 | 0 | [13 empty] | 300
[24 empty] | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;3 | 2 | Distance Polygonal\Starting | ZfPP | Real | SE | 60 | 5 | 0
300
x010_u002E_093 | Parametersatz 3->DIST | 010.093 | 0.1-4:0.01 |  | Zr/Zv PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 0.5 | 2 |  |  | Distance Circular\Starting | ZbwZfw | Real | 0.2 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;3 | 2 | Distance Circular\Starting | ZbwZfw | Real | GE | 0.1 | 1 | 0
[18 empty] | Distance Polygonal\Starting | ZbwZfw | Real | 0.2 | 0 | [13 empty] | 0.1
[24 empty] | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;3 | 2 | Distance Polygonal\Starting | ZbwZfw | Real | GE | 0.1 | 1 | 0
0.1
x010_u002E_095 | Parametersatz 3->DIST | 010.095 | 0.1-2:0.01 | Inom | IE> (max.Ber.) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 0.2 | 2 |  |  | Distance Circular\Starting | INMM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;3 | 2 | Distance Circular\Starting | INMM | Real | GE | 0.1 | 1 | 0
[18 empty] | Distance Polygonal\Starting | INMM | Real | 1 | 0 | [13 empty] | 0.1
[24 empty] | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;3 | 2 | Distance Polygonal\Starting | INMM | Real | GE | 0.1 | 1 | 0
0.1
x010_u002E_125 | Parametersatz 3->DIST | 010.125 | 0.05-2:0.01 | Inom | IE> (emp.Ber.) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 0.2 | 2 |  |  | Distance Circular\Starting | INM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Circular\Starting | INM | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | INM | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Polygonal\Starting | INM | Real |  |  | 1 | 0
x010_u002E_097 | Parametersatz 3->DIST | 010.097 | 0-0.5:0.001 | s | tIE> PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 0.1 | 2 |  |  | Distance Circular\Starting | tINM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Circular\Starting | tINM | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | tINM | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Polygonal\Starting | tINM | Real |  |  | 1 | 0
x010_u002E_096 | Parametersatz 3->DIST | 010.096 | 0.02-1:0.01 | Unom/©3 | UNE> PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 0.1 | 2 |  |  | Distance Circular\Starting | VNGM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;3 | 2 | Distance Circular\Starting | VNGM | Real | GE | 0.02 | 1 | 0
[18 empty] | Distance Polygonal\Starting | VNGM | Real | 1 | 0 | [13 empty] | 0.02
[24 empty] | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;3 | 2 | Distance Polygonal\Starting | VNGM | Real | GE | 0.02 | 1 | 0
0.02
x011_u002E_002 | Parametersatz 3->DIST | 011.002 | 0.2-1:0.01 | Unom/©3 | UNE>> PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 0.5 | 2 |  |  | Distance Circular\Starting | VNGMM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Circular\Starting | VNGMM | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | VNGMM | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Polygonal\Starting | VNGMM | Real |  |  | 1 | 0
x011_u002E_001 | Parametersatz 3->DIST | 011.001 | 0-60:0.001 | s | tUNE>> PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 |  |  | Distance Circular\Starting | tVNGMM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Circular\Starting | tVNGMM | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | tVNGMM | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Polygonal\Starting | tVNGMM | Real |  |  | 1 | 0
x013_u002E_037 | Parametersatz 3->DIST | 013.037 | 0-8:0.01 |  | Betrag kE PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 |  |  | Distance Circular\Polarisation | k0 | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Circular\Polarisation | k0 | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Polarisation | k0 | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Polygonal\Polarisation | k0 | Real |  |  | 1 | 0
x013_u002E_036 | Parametersatz 3->DIST | 013.036 | -180-180:1 | ° | Winkel kE PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 0 | 2 |  |  | Distance Circular\Polarisation | phik0 | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Circular\Polarisation | phik0 | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Polarisation | phik0 | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Polygonal\Polarisation | phik0 | Real |  |  | 1 | 0
x074_u002E_097 | Parametersatz 3->DIST | 074.097 | Kreis¦0;Polygon¦1 |  | Kennlinientyp PS3 | Enum | Parameter__Funktionsparameter | 0;1 | Real |  | x056_u002E_014;x031_u002E_073;x003_u002E_060 | E;E;E | 0;0;3 | 1 | 4 | E | 0 | Distance Circular | outserv | Real | 0 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Distance Circular | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 0 | Distance Polygonal | outserv | Real | 0 | 1 | [13 empty] | 1
[16 empty] | E | 1 | Distance Circular | outserv | Real | 0 | 1
[16 empty] | E | 1 | Distance Polygonal | outserv | Real | 0 | 0
x013_u002E_001 | Parametersatz 3->DIST | 013.001 | 0.1-200:0.01 | — | X1 (Polygon) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 10 |  |  |  | Distance Polygonal\Z1 | Xmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Polygonal\Z1 | Xmax | Real | SE | 40 | 5 | 0
200
x013_u002E_002 | Parametersatz 3->DIST | 013.002 | 0.1-200:0.01 | — | X2 (Polygon) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 20 |  |  |  | Distance Polygonal\Z2 | Xmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Polygonal\Z2 | Xmax | Real | SE | 40 | 5 | 0
200
x013_u002E_003 | Parametersatz 3->DIST | 013.003 | 0.1-200:0.01 | — | X3 (Polygon) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 30 |  |  |  | Distance Polygonal\Z3 | Xmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Polygonal\Z3 | Xmax | Real | SE | 40 | 5 | 0
200
x013_u002E_004 | Parametersatz 3->DIST | 013.004 | 0.1-200:0.01 | — | X4 (Polygon) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 40 |  |  |  | Distance Polygonal\Z4 | Xmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Polygonal\Z4 | Xmax | Real | SE | 40 | 5 | 0
200
x012_u002E_102 | Parametersatz 3->DIST | 012.102 | 0.1-200:0.01 | — | X5 (Polygon) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 50 |  |  |  | Distance Polygonal\Z5 | Xmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Polygonal\Z5 | Xmax | Real | SE | 40 | 5 | 0
200
x012_u002E_106 | Parametersatz 3->DIST | 012.106 | 0.1-200:0.01 | — | X6 (Polygon) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 60 |  |  |  | Distance Polygonal\Z6 | Xmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Polygonal\Z6 | Xmax | Real | SE | 40 | 5 | 0
200
x013_u002E_005 | Parametersatz 3->DIST | 013.005 | 0.1-200:0.01 | — | R1,LE (Polygon) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 10 |  |  |  | Distance Polygonal\Z1 | REmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Polygonal\Z1 | REmax | Real | SE | 40 | 5 | 0
200
x013_u002E_006 | Parametersatz 3->DIST | 013.006 | 0.1-200:0.01 | — | R1,LL (Polygon) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 10 |  |  |  | Distance Polygonal\Z1 | Rmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Polygonal\Z1 | Rmax | Real | SE | 40 | 5 | 0
200
x013_u002E_007 | Parametersatz 3->DIST | 013.007 | 0.1-200:0.01 | — | R2,LE (Polygon) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 20 |  |  |  | Distance Polygonal\Z2 | REmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Polygonal\Z2 | REmax | Real | SE | 40 | 5 | 0
200
x013_u002E_008 | Parametersatz 3->DIST | 013.008 | 0.1-200:0.01 | — | R2,LL (Polygon) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 20 |  |  |  | Distance Polygonal\Z2 | Rmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Polygonal\Z2 | Rmax | Real | SE | 40 | 5 | 0
200
x013_u002E_009 | Parametersatz 3->DIST | 013.009 | 0.1-200:0.01 | — | R3,LE (Polygon) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 30 |  |  |  | Distance Polygonal\Z3 | REmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Polygonal\Z3 | REmax | Real | SE | 40 | 5 | 0
200
x013_u002E_010 | Parametersatz 3->DIST | 013.010 | 0.1-200:0.01 | — | R3,LL (Polygon) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 30 |  |  |  | Distance Polygonal\Z3 | Rmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Polygonal\Z3 | Rmax | Real | SE | 40 | 5 | 0
200
x013_u002E_011 | Parametersatz 3->DIST | 013.011 | 0.1-200:0.01 | — | R4,LE (Polygon) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 40 |  |  |  | Distance Polygonal\Z4 | REmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Polygonal\Z4 | REmax | Real | SE | 40 | 5 | 0
200
x013_u002E_012 | Parametersatz 3->DIST | 013.012 | 0.1-200:0.01 | — | R4,LL (Polygon) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 40 |  |  |  | Distance Polygonal\Z4 | Rmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Polygonal\Z4 | Rmax | Real | SE | 40 | 5 | 0
200
x012_u002E_110 | Parametersatz 3->DIST | 012.110 | 0.1-200:0.01 | — | R5,LE (Polygon) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 50 |  |  |  | Distance Polygonal\Z5 | REmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Polygonal\Z5 | REmax | Real | SE | 40 | 5 | 0
200
x012_u002E_114 | Parametersatz 3->DIST | 012.114 | 0.1-200:0.01 | — | R5,LL (Polygon) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 50 |  |  |  | Distance Polygonal\Z5 | Rmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Polygonal\Z5 | Rmax | Real | SE | 40 | 5 | 0
200
x012_u002E_118 | Parametersatz 3->DIST | 012.118 | 0.1-200:0.01 | — | R6,LE (Polygon) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 60 |  |  |  | Distance Polygonal\Z6 | REmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Polygonal\Z6 | REmax | Real | SE | 40 | 5 | 0
200
x012_u002E_122 | Parametersatz 3->DIST | 012.122 | 0.1-200:0.01 | — | R6,LL (Polygon) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 60 |  |  |  | Distance Polygonal\Z6 | Rmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Polygonal\Z6 | Rmax | Real | SE | 40 | 5 | 0
200
x013_u002E_013 | Parametersatz 3->DIST | 013.013 | 40-90:1 | ° | €1 (Polygon) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 75 |  |  |  | Distance Polygonal\Z1 | phi | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Polygonal\Z1 | phi | Real | GE | 40 | 1 | 0
40
x013_u002E_014 | Parametersatz 3->DIST | 013.014 | 40-90:1 | ° | €2 (Polygon) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 75 |  |  |  | Distance Polygonal\Z2 | phi | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Polygonal\Z2 | phi | Real | GE | 40 | 1 | 0
40
x013_u002E_015 | Parametersatz 3->DIST | 013.015 | 40-90:1 | ° | €3 (Polygon) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 75 |  |  |  | Distance Polygonal\Z3 | phi | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Polygonal\Z3 | phi | Real | GE | 40 | 1 | 0
40
x013_u002E_016 | Parametersatz 3->DIST | 013.016 | 40-90:1 | ° | €4 (Polygon) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 75 |  |  |  | Distance Polygonal\Z4 | phi | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Polygonal\Z4 | phi | Real | GE | 40 | 1 | 0
40
x012_u002E_126 | Parametersatz 3->DIST | 012.126 | 40-90:1 | ° | €5 (Polygon) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 75 |  |  |  | Distance Polygonal\Z5 | phi | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Polygonal\Z5 | phi | Real | GE | 40 | 1 | 0
40
x012_u002E_130 | Parametersatz 3->DIST | 012.130 | 40-90:1 | ° | €6 (Polygon) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 75 |  |  |  | Distance Polygonal\Z6 | phi | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Polygonal\Z6 | phi | Real | GE | 40 | 1 | 0
40
x074_u002E_086 | Parametersatz 3->DIST | 074.086 | -20-20:1 | ° | ‹1 (Polygon) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 0 |  |  |  | Distance Polygonal\Z1 | beta | Real | -1 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\Z1 | beta | Real |  |  | -1 | 0
x074_u002E_087 | Parametersatz 3->DIST | 074.087 | -20-20:1 | ° | ‹2 (Polygon) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 0 |  |  |  | Distance Polygonal\Z2 | beta | Real | -1 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\Z2 | beta | Real |  |  | -1 | 0
x074_u002E_088 | Parametersatz 3->DIST | 074.088 | -20-20:1 | ° | ‹3 (Polygon) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 0 |  |  |  | Distance Polygonal\Z3 | beta | Real | -1 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\Z3 | beta | Real |  |  | -1 | 0
x074_u002E_089 | Parametersatz 3->DIST | 074.089 | -20-20:1 | ° | ‹4 (Polygon) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 0 |  |  |  | Distance Polygonal\Z4 | beta | Real | -1 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\Z4 | beta | Real |  |  | -1 | 0
x012_u002E_158 | Parametersatz 3->DIST | 012.158 | -20-20:1 | ° | ‹5 (Polygon) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 0 |  |  |  | Distance Polygonal\Z5 | beta | Real | -1 | 0 |  | Distance Polygonal;Distance Polygonal\Z5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\Z5 | beta | Real |  |  | -1 | 0
x012_u002E_162 | Parametersatz 3->DIST | 012.162 | -20-20:1 | ° | ‹6 (Polygon) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 0 |  |  |  | Distance Polygonal\Z6 | beta | Real | -1 | 0 |  | Distance Polygonal;Distance Polygonal\Z6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\Z6 | beta | Real |  |  | -1 | 0
x074_u002E_091 | Parametersatz 3->DIST | 074.091 | 0.05-200:0.01 | — | Z1 (Kreis) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 10 |  |  |  | Distance Circular\Z1 | Zm | Real | 0.2 | 0 |  | Distance Circular;Distance Circular\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Circular\Z1 | Zm | Real | SE | 40 | 5 | 0
200
x074_u002E_092 | Parametersatz 3->DIST | 074.092 | 0.05-200:0.01 | — | Z2 (Kreis) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 20 |  |  |  | Distance Circular\Z2 | Zm | Real | 0.2 | 0 |  | Distance Circular;Distance Circular\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Circular\Z2 | Zm | Real | SE | 40 | 5 | 0
200
x074_u002E_093 | Parametersatz 3->DIST | 074.093 | 0.05-200:0.01 | — | Z3 (Kreis) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 30 |  |  |  | Distance Circular\Z3 | Zm | Real | 0.2 | 0 |  | Distance Circular;Distance Circular\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Circular\Z3 | Zm | Real | SE | 40 | 5 | 0
200
x074_u002E_094 | Parametersatz 3->DIST | 074.094 | 0.05-200:0.01 | — | Z4 (Kreis) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 40 |  |  |  | Distance Circular\Z4 | Zm | Real | 0.2 | 0 |  | Distance Circular;Distance Circular\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Circular\Z4 | Zm | Real | SE | 40 | 5 | 0
200
x012_u002E_150 | Parametersatz 3->DIST | 012.150 | 0.05-200:0.01 | — | Z5 (Kreis) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 50 |  |  |  | Distance Circular\Z5 | Zm | Real | 0.2 | 0 |  | Distance Circular;Distance Circular\Z5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Circular\Z5 | Zm | Real | SE | 40 | 5 | 0
200
x012_u002E_154 | Parametersatz 3->DIST | 012.154 | 0.05-200:0.01 | — | Z6 (Kreis) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 60 |  |  |  | Distance Circular\Z6 | Zm | Real | 0.2 | 0 |  | Distance Circular;Distance Circular\Z6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Circular\Z6 | Zm | Real | SE | 40 | 5 | 0
200
x074_u002E_090 | Parametersatz 3->DIST | 074.090 | 10-90:1 | ° | €1 (Kreis) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 75 | 2 |  |  | Distance Circular\Z1 | arcalpha | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Circular\Z1 | arcalpha | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z1E | arcalpha | Real | 1 | 0
x074_u002E_095 | Parametersatz 3->DIST | 074.095 | 10-90:1 | ° | €2 (Kreis) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 75 |  |  |  | Distance Circular\Z2 | arcalpha | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Circular\Z2 | arcalpha | Real |  |  | 1 | 0
x074_u002E_096 | Parametersatz 3->DIST | 074.096 | 10-90:1 | ° | €3 (Kreis) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 75 |  |  |  | Distance Circular\Z3 | arcalpha | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Circular\Z3 | arcalpha | Real |  |  | 1 | 0
x074_u002E_099 | Parametersatz 3->DIST | 074.099 | 10-90:1 | ° | €4 (Kreis) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 75 |  |  |  | Distance Circular\Z4 | arcalpha | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Circular\Z4 | arcalpha | Real |  |  | 1 | 0
x012_u002E_166 | Parametersatz 3->DIST | 012.166 | 10-90:1 | ° | €5 (Kreis) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 75 |  |  |  | Distance Circular\Z5 | arcalpha | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Circular\Z5 | arcalpha | Real |  |  | 1 | 0
x012_u002E_170 | Parametersatz 3->DIST | 012.170 | 10-90:1 | ° | €6 (Kreis) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 75 |  |  |  | Distance Circular\Z6 | arcalpha | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Circular\Z6 | arcalpha | Real |  |  | 1 | 0
x012_u002E_091 | Parametersatz 3->DIST | 012.091 | nein¦0;ja¦1 |  | Li.bo.komp. Kr. PS3 | Enum | Parameter__Funktionsparameter | 0;1 | Real |  | x003_u002E_060 | E | 3 | 0 | 7 |  |  | Distance Circular\Z1 | arcen | Real | 1 | 0 | 6 | Distance Circular;Distance Circular\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Circular\Z1 | arcen | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z1E | arcen | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Circular\Z2 | arcen | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z2 | arcen | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Circular\Z3 | arcen | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z3 | arcen | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Circular\Z4 | arcen | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z4 | arcen | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Circular\Z5 | arcen | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z5 | arcen | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Circular\Z6 | arcen | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z6 | arcen | Real | 1 | 0
x013_u002E_023 | Parametersatz 3->DIST | 013.023 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung N1 PS3 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 3 | 0 | 4 | NE | 2 | Distance Circular\Z1 | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Circular\Z1 | idir | Real |  |  | 1 | 0
[16 empty] | NE | 2 | Distance Circular\Z1E | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\Z1 | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z1 | idir | Real | 1 | 0
[18 empty] | Distance Polygonal\Z1E | idir | Real | 1 | 0
x013_u002E_024 | Parametersatz 3->DIST | 013.024 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung N2 PS3 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 3 | 0 |  | NE | 2 | Distance Circular\Z2 | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Circular\Z2 | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z2 | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\Z2 | idir | Real |  |  | 1 | 0
x013_u002E_025 | Parametersatz 3->DIST | 013.025 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung N3 PS3 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 3 | 0 |  | NE | 2 | Distance Circular\Z3 | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Circular\Z3 | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z3 | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\Z3 | idir | Real |  |  | 1 | 0
x013_u002E_026 | Parametersatz 3->DIST | 013.026 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung N4 PS3 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 3 | 0 |  | NE | 2 | Distance Circular\Z4 | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Circular\Z4 | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z4 | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\Z4 | idir | Real |  |  | 1 | 0
x013_u002E_027 | Parametersatz 3->DIST | 013.027 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung N5 PS3 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 3 | 0 |  | NE | 2 | Distance Circular\Z5 | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Circular\Z5 | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z5 | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\Z5 | idir | Real |  |  | 1 | 0
x012_u002E_134 | Parametersatz 3->DIST | 012.134 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung N6 PS3 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 3 | 0 |  | NE | 2 | Distance Circular\Z6 | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Circular\Z6 | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z6 | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\Z6 | idir | Real |  |  | 1 | 0
x012_u002E_138 | Parametersatz 3->DIST | 012.138 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung N7 PS3 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 3 | 0 |  |  |  | Distance Circular\Directional | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Directional;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Circular\Directional | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Directional | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Directional;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\Directional | idir | Real |  |  | 1 | 0
x013_u002E_028 | Parametersatz 3->DIST | 013.028 | 0-60:0.001;blockiert=60.002 | s | t1 PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 0 | 4 | SE | 60 | Distance Circular\T1 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Circular\T1 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Circular\T1 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
[16 empty] | SE | 60 | Distance Polygonal\T1 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Polygonal\T1 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Polygonal\T1 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
x013_u002E_029 | Parametersatz 3->DIST | 013.029 | 0-60:0.001;blockiert=60.002 | s | t2 PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1 | 4 | SE | 60 | Distance Circular\T2 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Circular\T2 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Circular\T2 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
[16 empty] | SE | 60 | Distance Polygonal\T2 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Polygonal\T2 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Polygonal\T2 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
x013_u002E_030 | Parametersatz 3->DIST | 013.030 | 0-60:0.001;blockiert=60.002 | s | t3 PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 2 | 4 | SE | 60 | Distance Circular\T3 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Circular\T3 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Circular\T3 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
[16 empty] | SE | 60 | Distance Polygonal\T3 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Polygonal\T3 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Polygonal\T3 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
x013_u002E_031 | Parametersatz 3->DIST | 013.031 | 0-60:0.001;blockiert=60.002 | s | t4 PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 3 | 4 | SE | 60 | Distance Circular\T4 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Circular\T4 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Circular\T4 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
[16 empty] | SE | 60 | Distance Polygonal\T4 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Polygonal\T4 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Polygonal\T4 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
x013_u002E_032 | Parametersatz 3->DIST | 013.032 | 0-60:0.001;blockiert=60.002 | s | t5 PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 4 | 4 | SE | 60 | Distance Circular\T5 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Circular\T5 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Circular\T5 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
[16 empty] | SE | 60 | Distance Polygonal\T5 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Polygonal\T5 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Polygonal\T5 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
x013_u002E_033 | Parametersatz 3->DIST | 013.033 | 0-60:0.001;blockiert=60.002 | s | t6 PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 5 | 4 | SE | 60 | Distance Circular\T6 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Circular\T6 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Circular\T6 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
[16 empty] | SE | 60 | Distance Polygonal\T6 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Polygonal\T6 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Polygonal\T6 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
x012_u002E_142 | Parametersatz 3->DIST | 012.142 | 0-60:0.001;blockiert=60.002 | s | t7 PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 6 | 4 | SE | 60 | Distance Circular\T9 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T9;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Circular\T9 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Circular\T9 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
[16 empty] | SE | 60 | Distance Polygonal\T9 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T9;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Polygonal\T9 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Polygonal\T9 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
x012_u002E_146 | Parametersatz 3->DIST | 012.146 | 0-60:0.001;blockiert=60.002 | s | t8 PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 7 | 4 | SE | 60 | Distance Circular\T10 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T10;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Circular\T10 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Circular\T10 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
[16 empty] | SE | 60 | Distance Polygonal\T10 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T10;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Polygonal\T10 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Polygonal\T10 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
x013_u002E_035 | Parametersatz 3->DIST | 013.035 | 1-450:0.01 |  | kÜ,LL KU PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1.2 | 3 |  |  | Distance Circular\Z1E | kZ | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z1E;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Circular\Z1E | kZ | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z1E | kX | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z1E;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\Z1E | kX | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z1E | kR | Real | 1 | 0
x015_u002E_016 | Parametersatz 3->SV | 015.016 | nein¦0;ja¦1 |  | Freigabe PS3 | Enum | Parameter__Funktionsparameter | 0;1 | String |  | x003_u002E_060 | E | 3 | 0 | 2 |  |  | Distance Circular\PSIG Connect | aDipset | String |  |  | 2 | Distance Circular;Distance Circular\PSIG Connect;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Circular\PSIG Connect | aDipset | String
[18 empty] | Distance Polygonal\PSIG Connect | aDipset | String |  |  |  | Distance Polygonal;Distance Polygonal\PSIG Connect;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\PSIG Connect | aDipset | String
x024_u002E_060 | Parametersatz 3->SV | 024.060 | keine¦0;direkte Schaltermitn¦1;anregeabh. Mitnahme¦2;Meßbereichserweiter.¦3;Freigabeverfahren¦4;Sperrverfahren¦5;GS-Schleife¦6;rückwärtige Verrieg.¦7;Richtungsvergleich¦8 |  | Betriebsart PS3 | Enum | Parameter__Funktionsparameter | ;DIRECT = TRIP;PUTT = TRIP;POTT = TRIP;COMP_RELEASE = TRIP;COMP_BLOCK = TRIP;COMP_PILOT = TRIP; | String |  | x003_u002E_060 | E | 3 | PUTT = TRIP | 4 |  |  | Distance Circular\PSIG Receive | sLogic | String |  |  | 2 | Distance Circular;Distance Circular\PSIG Receive;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Circular\PSIG Receive | sLogic | String
[18 empty] | Distance Circular\PSIG Send | sLogic | String |  |  |  | Distance Polygonal;Distance Polygonal\PSIG Receive;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\PSIG Receive | sLogic | String
[18 empty] | Distance Polygonal\PSIG Receive | sLogic | String
[18 empty] | Distance Polygonal\PSIG Send | sLogic | String
x024_u002E_063 | Parametersatz 3->SV | 024.063 | 0-60:0.001;blockiert=60.002 | s | Startzeit PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 0.08 | 4 | SE | 60 | Distance Circular\PSIG T | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\PSIG T;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Circular\PSIG T | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Circular\PSIG T | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
[16 empty] | SE | 60 | Distance Polygonal\PSIG T | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\PSIG T;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Polygonal\PSIG T | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Polygonal\PSIG T | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
x024_u002E_061 | Parametersatz 3->SV | 024.061 | 0-10:0.001 | s | Rückf.zeit Send. PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 0.25 | 2 |  |  | Distance Circular\PSIG T Reset | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\PSIG T Reset;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Circular\PSIG T Reset | Tdelay | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\PSIG T Reset | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\PSIG T Reset;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\PSIG T Reset | Tdelay | Real |  |  | 1 | 0
x074_u002E_098 | Parametersatz 3->UMZ | 074.098 | nein¦0;ja¦1 |  | Freigabe PS3 | Enum | Parameter__Funktionsparameter | 1;0 | Real |  | x056_u002E_008;x003_u002E_060 | E;E | 0;3 | 1 | 12 |  |  | Overcurrent\I> | outserv | Real | 1 | 0 |  | x056_u002E_008;x003_u002E_060 |  |  | E;E | 0;3 | 12 | Overcurrent\I> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\I>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\I>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\I>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\I>>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\I>>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\I>>>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\IN> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\IN> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\IN>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\IN>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\IN>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\IN>>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\IN>>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\IN>>>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\Ineg> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\Ineg> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\Ineg>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\Ineg>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\Ineg>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\Ineg>>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\Ineg>>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\Ineg>>>> | outserv | Real |  |  | 1 | 0
x074_u002E_007 | Parametersatz 3->UMZ | 074.007 | 0.1-20:0.01 | Inom | I> PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 |  |  | Overcurrent\I> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 3 | Overcurrent\I> | Ipset | Real | G | 20 | 0 | 20
[18 empty] | Overcurrent\I> | idir | Real | 0 | 0 | [7 empty] | Overcurrent\I> | Ipset | Real | S | 0.1 | 0 | 0.1
[30 empty] | Overcurrent\I> | Ipset | Real |  |  | 1 | 0
x074_u002E_008 | Parametersatz 3->UMZ | 074.008 | 0.1-20:0.01 | Inom | I>> PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 |  |  | Overcurrent\I>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 3 | Overcurrent\I>> | Ipset | Real | G | 20 | 0 | 20
[18 empty] | Overcurrent\I>> | idir | Real | 0 | 0 | [7 empty] | Overcurrent\I>> | Ipset | Real | S | 0.1 | 0 | 0.1
[30 empty] | Overcurrent\I>> | Ipset | Real |  |  | 1 | 0
x074_u002E_009 | Parametersatz 3->UMZ | 074.009 | 0.1-20:0.01 | Inom | I>>> PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 |  |  | Overcurrent\I>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 3 | Overcurrent\I>>> | Ipset | Real | G | 20 | 0 | 20
[18 empty] | Overcurrent\I>>> | idir | Real | 0 | 0 | [7 empty] | Overcurrent\I>>> | Ipset | Real | S | 0.1 | 0 | 0.1
[30 empty] | Overcurrent\I>>> | Ipset | Real |  |  | 1 | 0
x074_u002E_010 | Parametersatz 3->UMZ | 074.010 | 0.1-20:0.01 | Inom | I>>>> PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 |  |  | Overcurrent\I>>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 3 | Overcurrent\I>>>> | Ipset | Real | G | 20 | 0 | 20
[18 empty] | Overcurrent\I>>>> | idir | Real | 0 | 0 | [7 empty] | Overcurrent\I>>>> | Ipset | Real | S | 0.1 | 0 | 0.1
[30 empty] | Overcurrent\I>>>> | Ipset | Real |  |  | 1 | 0
x074_u002E_019 | Parametersatz 3->UMZ | 074.019 | 0-30:0.001;blockiert=30.002 | s | tI> PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 | SE | 30 | Overcurrent\I> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Overcurrent\I> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\I> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x074_u002E_020 | Parametersatz 3->UMZ | 074.020 | 0-30:0.001;blockiert=30.002 | s | tI>> PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 | SE | 30 | Overcurrent\I>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Overcurrent\I>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\I>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x074_u002E_021 | Parametersatz 3->UMZ | 074.021 | 0-30:0.001;blockiert=30.002 | s | tI>>> PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 | SE | 30 | Overcurrent\I>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Overcurrent\I>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\I>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x074_u002E_022 | Parametersatz 3->UMZ | 074.022 | 0-30:0.001;blockiert=30.002 | s | tI>>>> PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 | SE | 30 | Overcurrent\I>>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Overcurrent\I>>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\I>>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x074_u002E_011 | Parametersatz 3->UMZ | 074.011 | 0.1-20:0.01 | Inom | Igegen> PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1 |  |  |  | Overcurrent\IN> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\IN> | Ipset | Real |  |  | 1 | 0
x074_u002E_012 | Parametersatz 3->UMZ | 074.012 | 0.1-20:0.01 | Inom | Igegen>> PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1 |  |  |  | Overcurrent\IN>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\IN>> | Ipset | Real |  |  | 1 | 0
x074_u002E_013 | Parametersatz 3->UMZ | 074.013 | 0.1-20:0.01 | Inom | Igegen>>> PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1 |  |  |  | Overcurrent\IN>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\IN>>> | Ipset | Real |  |  | 1 | 0
x074_u002E_014 | Parametersatz 3->UMZ | 074.014 | 0.1-20:0.01 | Inom | Igegen>>>> PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1 |  |  |  | Overcurrent\IN>>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\IN>>>> | Ipset | Real |  |  | 1 | 0
x074_u002E_023 | Parametersatz 3->UMZ | 074.023 | 0-30:0.001;blockiert=30.002 | s | tIgegen> PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 | SE | 30 | Overcurrent\IN> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Overcurrent\IN> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\IN> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x074_u002E_024 | Parametersatz 3->UMZ | 074.024 | 0-30:0.001;blockiert=30.002 | s | tIgegen>> PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 | SE | 30 | Overcurrent\IN>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Overcurrent\IN>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\IN>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x074_u002E_025 | Parametersatz 3->UMZ | 074.025 | 0-30:0.001;blockiert=30.002 | s | tIgegen>>> PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 | SE | 30 | Overcurrent\IN>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Overcurrent\IN>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\IN>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x074_u002E_026 | Parametersatz 3->UMZ | 074.026 | 0-30:0.001;blockiert=30.002 | s | tIgegen>>>> PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 | SE | 30 | Overcurrent\IN>>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Overcurrent\IN>>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\IN>>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x074_u002E_015 | Parametersatz 3->UMZ | 074.015 | 0.1-20:0.01 | Inom | IE> PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1 |  |  |  | Overcurrent\Ineg> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\Ineg> | Ipset | Real |  |  | 1 | 0
x074_u002E_016 | Parametersatz 3->UMZ | 074.016 | 0.1-20:0.01 | Inom | IE>> PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1 |  |  |  | Overcurrent\Ineg>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\Ineg>> | Ipset | Real |  |  | 1 | 0
x074_u002E_017 | Parametersatz 3->UMZ | 074.017 | 0.1-20:0.01 | Inom | IE>>> PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1 |  |  |  | Overcurrent\Ineg>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\Ineg>>> | Ipset | Real |  |  | 1 | 0
x074_u002E_018 | Parametersatz 3->UMZ | 074.018 | 0.1-20:0.01 | Inom | IE>>>> PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1 |  |  |  | Overcurrent\Ineg>>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\Ineg>>>> | Ipset | Real |  |  | 1 | 0
x074_u002E_027 | Parametersatz 3->UMZ | 074.027 | 0-30:0.001;blockiert=30.002 | s | tIE> PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 | SE | 30 | Overcurrent\Ineg> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Overcurrent\Ineg> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\Ineg> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x074_u002E_028 | Parametersatz 3->UMZ | 074.028 | 0-30:0.001;blockiert=30.002 | s | tIE>> PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 | SE | 30 | Overcurrent\Ineg>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Overcurrent\Ineg>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\Ineg>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x074_u002E_029 | Parametersatz 3->UMZ | 074.029 | 0-30:0.001;blockiert=30.002 | s | tIE>>> PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 | SE | 30 | Overcurrent\Ineg>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Overcurrent\Ineg>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\Ineg>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x074_u002E_030 | Parametersatz 3->UMZ | 074.030 | 0-30:0.001;blockiert=30.002 | s | tIE>>>> PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 | SE | 30 | Overcurrent\Ineg>>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Overcurrent\Ineg>>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\Ineg>>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x010_u002E_080 | Parametersatz 3->UMZ | 010.080 | 0.01-0.5:0.001 | Unom/©3 | UNE> PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 0.03 |  |  |  | Overcurrent\Directional N | upolu | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\Directional N | upolu | Real |  |  | 1 | 0
x004_u002E_248 | Parametersatz 3->UMZ | 004.248 | -90-90:1 | ° | Winkel phiE PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 0 |  |  |  | Overcurrent\Directional N | mtau | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\Directional N | mtau | Real |  |  | 1 | 0
x072_u002E_082 | Parametersatz 3->UMZ | 072.082 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung tIE> PS3 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real |  | x003_u002E_060 | E | 3 | 1 |  |  |  | Overcurrent\IN> | idir | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\IN> | idir | Real |  |  | 1 | 0
x072_u002E_083 | Parametersatz 3->UMZ | 072.083 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung tIE>> PS3 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real |  | x003_u002E_060 | E | 3 | 1 |  |  |  | Overcurrent\IN>> | idir | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\IN>> | idir | Real |  |  | 1 | 0
x072_u002E_084 | Parametersatz 3->UMZ | 072.084 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung tIE>>> PS3 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real |  | x003_u002E_060 | E | 3 | 1 |  |  |  | Overcurrent\IN>>> | idir | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\IN>>> | idir | Real |  |  | 1 | 0
x072_u002E_085 | Parametersatz 3->UMZ | 072.085 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung tIE>>>> PS3 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real |  | x003_u002E_060 | E | 3 | 1 |  |  |  | Overcurrent\IN>>>> | idir | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\IN>>>> | idir | Real |  |  | 1 | 0
x074_u002E_000 | Parametersatz 3->AMZ | 074.000 | nein¦0;ja¦1 |  | Freigabe PS3 | Enum | Parameter__Funktionsparameter | 1;0 | Real |  | x056_u002E_009;x003_u002E_060 | E;E | 0;3 | 1 |  |  |  | Overcurrent\IDMT P | outserv | Real | 1 | 0 |  | x056_u002E_009;x003_u002E_060 |  |  | E;E | 0;3 | 3 | Overcurrent\IDMT P | outserv | Real | E | 0 |  | 0
[18 empty] | Overcurrent\IDMT neg | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\IDMT neg | outserv | Real | E | 0 |  | 0
[18 empty] | Overcurrent\IDMT N | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\IDMT N | outserv | Real |  |  | 1 | 0
x074_u002E_050 | Parametersatz 3->AMZ | 074.050 | 0.1-4:0.01;blockiert=4.02 | Inom | IB,L PS3 | Real | Parameter__Funktionsparameter |  |  |  | x074_u002E_000;x003_u002E_060 | E;E | 0;3 | 1 | 4 | SE | 4 | Overcurrent\IDMT P | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Overcurrent\IDMT P | outserv | Real | E | 1 | 0 | 4.02
[16 empty] | SE | 4 | Overcurrent\IDMT P | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\IDMT P | Ipset | Real |  |  | 1 | 0
[16 empty] | G | 4 | Overcurrent\IDMT P | outserv | Real | 0 | 1
[18 empty] | Overcurrent\IDMT KI P | outserv | Real | 0 | 1
x074_u002E_056 | Parametersatz 3->AMZ | 074.056 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Kennlinientyp L PS3 | Enum | Parameter__Funktionsparameter | Definite Time;IEC 255-3 Standard Inverse;IEC 255-3 Very Inverse;IEC 255-3 Extremly Inverse;IEC 255-3 Long-Time Inverse;IEEE C37.112 Moderately Inverse;IEEE C37.112 Very Inverse;IEEE C37.112 Extremely Inverse;ANSI Normally Inverse;ANSI Short-Time Inverse;ANSI Long-Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | [8 empty] | Overcurrent\IDMT P | pcharac |  |  |  |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\IDMT P | pcharac
x074_u002E_053 | Parametersatz 3->AMZ | 074.053 | 0.01-10:0.01 |  | Kennl.fakt. kt,L PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 |  |  | Overcurrent\IDMT P | Tpset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\IDMT P | Tpset | Real |  |  | 1 | 0
[18 empty] | Overcurrent\IDMT P | udeftmin | Real | 0 | 0
x074_u002E_059 | Parametersatz 3->AMZ | 074.059 | unverzögert¦0;verzögert gem. Kennl¦1 |  | Rückfallen L PS3 | Enum | Parameter__Funktionsparameter | 0;1 | Real | 3 | x003_u002E_060;x074_u002E_056 | E;SW | 3;IEEE | 0 |  |  |  | Overcurrent\IDMT P | resetdis | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\IDMT P | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x074_u002E_056 | E;SW | 3;ANSI |  |  |  |  | Overcurrent\IDMT P | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | 3 |  |  |  |  | Overcurrent\IDMT P | resetdis | Real | 0 | 0
x074_u002E_051 | Parametersatz 3->AMZ | 074.051 | 0.1-4:0.01;blockiert=4.02 | Inom | IB,gegen PS3 | Real | Parameter__Funktionsparameter |  |  |  | x074_u002E_000;x003_u002E_060 | E;E | 0;3 | 1 | 4 | SE | 4 | Overcurrent\IDMT neg | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 3 | Overcurrent\IDMT neg | outserv | Real | E | 1 | 0 | 4.02
[16 empty] | SE | 4 | Overcurrent\IDMT neg | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\IDMT neg | Ipset | Real | GE | 0.1 | 1 | 0
[16 empty] | G | 4 | Overcurrent\IDMT neg | outserv | Real | 0 | 1 | [13 empty] | 0.1
[18 empty] | Overcurrent\IDMT KI neg | outserv | Real | 0 | 1
x074_u002E_057 | Parametersatz 3->AMZ | 074.057 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Kennl.typ gegen PS3 | Enum | Parameter__Funktionsparameter | Definite Time;IEC 255-3 Standard Inverse;IEC 255-3 Very Inverse;IEC 255-3 Extremly Inverse;IEC 255-3 Long-Time Inverse;IEEE C37.112 Moderately Inverse;IEEE C37.112 Very Inverse;IEEE C37.112 Extremely Inverse;ANSI Normally Inverse;ANSI Short-Time Inverse;ANSI Long-Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | [8 empty] | Overcurrent\IDMT neg | pcharac |  |  |  |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\IDMT neg | pcharac
x074_u002E_054 | Parametersatz 3->AMZ | 074.054 | 0.01-10:0.01 |  | Kennl.f. kt,gegn PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1 |  |  |  | Overcurrent\IDMT neg | Tpset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\IDMT neg | Tpset | Real |  |  | 1 | 0
[18 empty] | Overcurrent\IDMT neg | udeftmin | Real | 0 | 0
x074_u002E_060 | Parametersatz 3->AMZ | 074.060 | unverzögert¦0;verzögert gem. Kennl¦1 |  | Rückfallen gegen PS3 | Enum | Parameter__Funktionsparameter | 0;1 | Real | 3 | x003_u002E_060;x074_u002E_057 | E;SW | 3;IEEE | 0 |  |  |  | Overcurrent\IDMT neg | resetdis | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\IDMT neg | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x074_u002E_057 | E;SW | 3;ANSI |  |  |  |  | Overcurrent\IDMT neg | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | 3 |  |  |  |  | Overcurrent\IDMT neg | resetdis | Real | 0 | 0
x074_u002E_062 | Parametersatz 3->AMZ | 074.062 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung L PS3 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real |  | x003_u002E_060 | E | 3 |  |  |  |  | Overcurrent\IDMT neg | idir | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\IDMT neg | idir | Real |  |  | 1 | 0
x074_u002E_052 | Parametersatz 3->AMZ | 074.052 | 0.1-4:0.01;blockiert=4.02 | Inom | IB,E (gerechnet) PS3 | Real | Parameter__Funktionsparameter |  |  |  | x074_u002E_000;x003_u002E_060 | E;E | 0;3 | 1 | 4 | SE | 4 | Overcurrent\IDMT N | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 3 | Overcurrent\IDMT N | outserv | Real | E | 1 | 0 | 4.02
[16 empty] | SE | 4 | Overcurrent\IDMT N | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\IDMT N | Ipset | Real | GE | 0.1 | 1 | 0
[16 empty] | G | 4 | Overcurrent\IDMT N | outserv | Real | 0 | 1 | [13 empty] | 0.1
[18 empty] | Overcurrent\IDMT KI N | outserv | Real | 0 | 1
x074_u002E_058 | Parametersatz 3->AMZ | 074.058 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Kennlinientyp E PS3 | Enum | Parameter__Funktionsparameter | Definite Time;IEC 255-3 Standard Inverse;IEC 255-3 Very Inverse;IEC 255-3 Extremly Inverse;IEC 255-3 Long-Time Inverse;IEEE C37.112 Moderately Inverse;IEEE C37.112 Very Inverse;IEEE C37.112 Extremely Inverse;ANSI Normally Inverse;ANSI Short-Time Inverse;ANSI Long-Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | [8 empty] | Overcurrent\IDMT N | pcharac |  |  |  |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\IDMT N | pcharac
x074_u002E_055 | Parametersatz 3->AMZ | 074.055 | 0.01-10:0.01 |  | Kennl.f. kt,E PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 |  |  | Overcurrent\IDMT N | Tpset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\IDMT N | Tpset | Real |  |  | 1 | 0
[18 empty] | Overcurrent\IDMT N | udeftmin | Real | 0 | 0
x074_u002E_064 | Parametersatz 3->AMZ | 074.064 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung E PS3 | Enum | Parameter__Funktionsparameter | 0;1 | Real | 3 | x003_u002E_060;x074_u002E_058 | E;SW | 3;IEEE | 0 |  |  |  | Overcurrent\IDMT N | resetdis | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\IDMT N | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x074_u002E_058 | E;SW | 3;ANSI |  |  |  |  | Overcurrent\IDMT N | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | 3 |  |  |  |  | Overcurrent\IDMT N | resetdis | Real | 0 | 0
x074_u002E_062 | Parametersatz 3->AMZ | 074.062 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung L PS3 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real |  | x003_u002E_060 | E | 3 |  |  |  |  | Overcurrent\IDMT N | idir | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\IDMT N | idir | Real |  |  | 1 | 0
x078_u002E_000 | Parametersatz 3->U<> | 078.000 | nein¦0;ja¦1 |  | Freigabe PS3 | Enum | Parameter__Funktionsparameter | 1;0 | Real |  | x056_u002E_010;x003_u002E_060 | E;E | 0;3 | 1 |  |  |  | Voltage | outserv | Real | 1 | 0 |  | x056_u002E_010;x003_u002E_060 |  |  | E;E | 0;3 |  | Voltage | outserv | Real |  |  | 1 | 0
x078_u002E_001 | Parametersatz 3->U<> | 078.001 | Dreieck¦0;Stern¦1 |  | Betriebsart PS3 | Enum | Parameter__Funktionsparameter | 0;1 | Real |  | x078_u002E_000;x003_u002E_060 | E;E | 0;3 | 0 | 16 | E | 0 | Voltage\V< LE | outserv | Real | 0 | 1
[16 empty] | E | 0 | Voltage\V< LL | outserv | Real | 0 | 0
[16 empty] | E | 0 | Voltage\V<< LE | outserv | Real | 0 | 1
[16 empty] | E | 0 | Voltage\V<< LL | outserv | Real | 0 | 0
[16 empty] | E | 0 | Voltage\V> LE | outserv | Real | 0 | 1
[16 empty] | E | 0 | Voltage\V> LL | outserv | Real | 0 | 0
[16 empty] | E | 0 | Voltage\V>> LE | outserv | Real | 0 | 1
[16 empty] | E | 0 | Voltage\V>> LL | outserv | Real | 0 | 0
[16 empty] | E | 1 | Voltage\V< LE | outserv | Real | 0 | 0
[16 empty] | E | 1 | Voltage\V< LL | outserv | Real | 0 | 1
[16 empty] | E | 1 | Voltage\V<< LE | outserv | Real | 0 | 0
[16 empty] | E | 1 | Voltage\V<< LL | outserv | Real | 0 | 1
[16 empty] | E | 1 | Voltage\V> LE | outserv | Real | 0 | 0
[16 empty] | E | 1 | Voltage\V> LL | outserv | Real | 0 | 1
[16 empty] | E | 1 | Voltage\V>> LE | outserv | Real | 0 | 0
[16 empty] | E | 1 | Voltage\V>> LL | outserv | Real | 0 | 1
x078_u002E_003 | Parametersatz 3->U<> | 078.003 | 0.2-1.5:0.01;blockiert=1.52 | Unom(/©3) | U> PS3 | Real | Parameter__Funktionsparameter |  |  | 2 | x078_u002E_001;x003_u002E_060 | E;E | 0;3 | 1.1 | 3 | SE | 1.5 | Voltage\V> LL | Uset | Real | 1 | 0 | 2 | x078_u002E_001;x003_u002E_060 |  |  | E;E | 0;3 | 3 | Voltage\V> LL | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V> LL | outserv | Real | 0 | 0 | [7 empty] | Voltage\V> LL | Uset | Real | GE | 0.2 | 1 | 0
[16 empty] | G | 1.5 | Voltage\V> LL | outserv | Real | 0 | 1 | [13 empty] | 0.2
[11 empty] | x078_u002E_001;x003_u002E_060 | E;E | 1;3 |  | 3 | SE | 1.5 | Voltage\V> LE | Uset | Real | 1 | 0 |  | x078_u002E_001;x003_u002E_060 |  |  | E;E | 1;3 | 3 | Voltage\V> LE | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V> LE | outserv | Real | 0 | 0 | [7 empty] | Voltage\V> LE | Uset | Real | GE | 0.2 | 1 | 0
[16 empty] | G | 1.5 | Voltage\V> LE | outserv | Real | 0 | 1 | [13 empty] | 0.2
x078_u002E_004 | Parametersatz 3->U<> | 078.004 | 0.2-1.5:0.01;blockiert=1.52 | Unom(/©3) | U>> PS3 | Real | Parameter__Funktionsparameter |  |  | 2 | x078_u002E_001;x003_u002E_060 | E;E | 0;3 | 1.1 | 3 | SE | 1.5 | Voltage\V>> LL | Uset | Real | 1 | 0 | 2 | x078_u002E_001;x003_u002E_060 |  |  | E;E | 0;3 | 3 | Voltage\V>> LL | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V>> LL | outserv | Real | 0 | 0 | [7 empty] | Voltage\V>> LL | Uset | Real | GE | 0.2 | 1 | 0
[16 empty] | G | 1.5 | Voltage\V>> LL | outserv | Real | 0 | 1 | [13 empty] | 0.2
[11 empty] | x078_u002E_001;x003_u002E_060 | E;E | 1;3 |  | 3 | SE | 1.5 | Voltage\V>> LE | Uset | Real | 1 | 0 |  | x078_u002E_001;x003_u002E_060 |  |  | E;E | 1;3 | 3 | Voltage\V>> LE | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V>> LE | outserv | Real | 0 | 0 | [7 empty] | Voltage\V>> LE | Uset | Real | GE | 0.2 | 1 | 0
[16 empty] | G | 1.5 | Voltage\V>> LE | outserv | Real | 0 | 1 | [13 empty] | 0.2
x078_u002E_005 | Parametersatz 3->U<> | 078.005 | 0-100:0.01;blockiert=100.02 | s | tU> PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1 | 4 | SE | 100 | Voltage\V> LL | Tdel | Real | 1 | 0 | 2 | x078_u002E_001;x003_u002E_060 |  |  | E;E | 0;3 | 2 | Voltage\V> LL | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V> LL | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
[16 empty] | SE | 100 | Voltage\V> LE | Tdel | Real | 1 | 0 |  | x078_u002E_001;x003_u002E_060 |  |  | E;E | 1;3 | 2 | Voltage\V> LE | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V> LE | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x078_u002E_006 | Parametersatz 3->U<> | 078.006 | 0-100:0.01;blockiert=100.02 | s | tU>> PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1 | 4 | SE | 100 | Voltage\V>> LL | Tdel | Real | 1 | 0 |  | x078_u002E_001;x003_u002E_060 |  |  | E;E | 0;3 | 2 | Voltage\V>> LL | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V>> LL | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
[16 empty] | SE | 100 | Voltage\V>> LE | Tdel | Real | 1 | 0 |  | x078_u002E_001;x003_u002E_060 |  |  | E;E | 1;3 | 2 | Voltage\V>> LE | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V>> LE | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x078_u002E_007 | Parametersatz 3->U<> | 078.007 | 0.2-1.5:0.01;blockiert=1.52 | Unom(/©3) | U< PS3 | Real | Parameter__Funktionsparameter |  |  | 2 | x078_u002E_001;x003_u002E_060 | E;E | 0;3 | 0.8 | 3 | SE | 1.5 | Voltage\V< LL | Uset | Real | 1 | 0 | 2 | x078_u002E_001;x003_u002E_060 |  |  | E;E | 0;3 | 2 | Voltage\V< LL | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V< LL | outserv | Real | 0 | 0 | [7 empty] | Voltage\V< LL | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\V< LL | outserv | Real | 0 | 1 |  | x078_u002E_001;x003_u002E_060 |  |  | E;E | 1;3 | 2 | Voltage\V< LE | outserv | Real | E | 1 | 0 | 1.52
[11 empty] | x078_u002E_001;x003_u002E_060 | E;E | 1;3 | 0.8 |  | SE | 1.5 | Voltage\V< LE | Uset | Real | 1 | 0 | [7 empty] | Voltage\V< LE | Uset | Real |  |  | 1 | 0
[16 empty] | SE | 1.5 | Voltage\V< LE | outserv | Real | 0 | 0
[16 empty] | G | 1.5 | Voltage\V< LE | outserv | Real | 0 | 1
x078_u002E_008 | Parametersatz 3->U<> | 078.008 | 0.2-1.5:0.01;blockiert=1.52 | Unom(/©3) | U<< PS3 | Real | Parameter__Funktionsparameter |  |  | 2 | x078_u002E_001;x003_u002E_060 | E;E | 0;3 | 0.8 | 3 | SE | 1.5 | Voltage\V<< LL | Uset | Real | 1 | 0 | 2 | x078_u002E_001;x003_u002E_060 |  |  | E;E | 0;3 | 2 | Voltage\V<< LL | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V<< LL | outserv | Real | 0 | 0 | [7 empty] | Voltage\V<< LL | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\V<< LL | outserv | Real | 0 | 1 |  | x078_u002E_001;x003_u002E_060 |  |  | E;E | 1;3 | 2 | Voltage\V<< LE | outserv | Real | E | 1 | 0 | 1.52
[11 empty] | x078_u002E_001;x003_u002E_060 | E;E | 1;3 | 0.8 |  | SE | 1.5 | Voltage\V<< LE | Uset | Real | 1 | 0 | [7 empty] | Voltage\V<< LE | Uset | Real |  |  | 1 | 0
[16 empty] | SE | 1.5 | Voltage\V<< LE | outserv | Real | 0 | 0
[16 empty] | G | 1.5 | Voltage\V<< LE | outserv | Real | 0 | 1
x078_u002E_009 | Parametersatz 3->U<> | 078.009 | 0-100:0.01;blockiert=100.02 | s | tU< PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1 | 4 | SE | 100 | Voltage\V< LL | Tdel | Real | 1 | 0 |  | x078_u002E_001;x003_u002E_060 |  |  | E;E | 0;3 | 2 | Voltage\V< LL | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V< LL | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
[16 empty] | SE | 100 | Voltage\V< LE | Tdel | Real | 1 | 0 |  | x078_u002E_001;x003_u002E_060 |  |  | E;E | 1;3 | 2 | Voltage\V< LE | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V< LE | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x078_u002E_010 | Parametersatz 3->U<> | 078.010 | 0-100:0.01;blockiert=100.02 | s | tU<< PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1 | 4 | SE | 100 | Voltage\V<< LL | Tdel | Real | 1 | 0 |  | x078_u002E_001;x003_u002E_060 |  |  | E;E | 0;3 | 2 | Voltage\V<< LL | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V<< LL | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
[16 empty] | SE | 100 | Voltage\V<< LE | Tdel | Real | 1 | 0 |  | x078_u002E_001;x003_u002E_060 |  |  | E;E | 1;3 | 2 | Voltage\V<< LE | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V<< LE | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x078_u002E_015 | Parametersatz 3->U<> | 078.015 | 0.2-1.5:0.01;blockiert=1.52 | Unom/©3 | Umit> PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1.1 | 3 | SE | 1.5 | Voltage\Vpos> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 3 | Voltage\Vpos> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos> | Uset | Real | GE | 0.2 | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vpos> | outserv | Real | 0 | 1 | [13 empty] | 0.2
x078_u002E_016 | Parametersatz 3->U<> | 078.016 | 0.2-1.5:0.01;blockiert=1.52 | Unom/©3 | Umit>> PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1.1 | 3 | SE | 1.5 | Voltage\Vpos>> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 3 | Voltage\Vpos>> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos>> | Uset | Real | GE | 0.2 | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vpos>> | outserv | Real | 0 | 1 | [13 empty] | 0.2
x078_u002E_017 | Parametersatz 3->U<> | 078.017 | 0-100:0.01;blockiert=100.02 | s | tUmit> PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 | SE | 100 | Voltage\Vpos> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Voltage\Vpos> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vpos> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x078_u002E_018 | Parametersatz 3->U<> | 078.018 | 0-100:0.01;blockiert=100.02 | s | tUmit>> PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 | SE | 100 | Voltage\Vpos>> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Voltage\Vpos>> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vpos>> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x078_u002E_019 | Parametersatz 3->U<> | 078.019 | 0.2-1.5:0.01;blockiert=1.52 | Unom/©3 | Umit< PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 0.8 | 3 | SE | 1.5 | Voltage\Vpos< | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 3 | Voltage\Vpos< | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos< | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos< | Uset | Real | GE | 0.2 | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vpos< | outserv | Real | 0 | 1 | [13 empty] | 0.2
x078_u002E_020 | Parametersatz 3->U<> | 078.020 | 0.2-1.5:0.01;blockiert=1.52 | Unom/©3 | Umit<< PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 0.8 | 3 | SE | 1.5 | Voltage\Vpos<< | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 3 | Voltage\Vpos<< | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos<< | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos<< | Uset | Real | GE | 0.2 | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vpos<< | outserv | Real | 0 | 1 | [13 empty] | 0.2
x078_u002E_021 | Parametersatz 3->U<> | 078.021 | 0-100:0.01;blockiert=100.02 | s | tUmit< PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 | SE | 100 | Voltage\Vpos< | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Voltage\Vpos< | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vpos< | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x078_u002E_022 | Parametersatz 3->U<> | 078.022 | 0-100:0.01;blockiert=100.02 | s | tUmit<< PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 | SE | 100 | Voltage\Vpos<< | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Voltage\Vpos<< | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vpos<< | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x078_u002E_023 | Parametersatz 3->U<> | 078.023 | 0.2-1.5:0.01;blockiert=1.52 | Unom/©3 | Ugegen> PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1.52 | 3 | SE | 1.5 | Voltage\Vneg> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 3 | Voltage\Vneg> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vneg> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vneg> | Uset | Real | GE | 0.2 | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vneg> | outserv | Real | 0 | 1 | [13 empty] | 0.2
x078_u002E_024 | Parametersatz 3->U<> | 078.024 | 0.2-1.5:0.01;blockiert=1.52 | Unom/©3 | Ugegen>> PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1.52 | 3 | SE | 1.5 | Voltage\Vneg>> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 3 | Voltage\Vneg>> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vneg>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vneg>> | Uset | Real | GE | 0.2 | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vneg>> | outserv | Real | 0 | 1 | [13 empty] | 0.2
x078_u002E_025 | Parametersatz 3->U<> | 078.025 | 0-100:0.01;blockiert=100.02 | s | tUgegen> PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 | SE | 100 | Voltage\Vneg> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Voltage\Vneg> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vneg> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x078_u002E_026 | Parametersatz 3->U<> | 078.026 | 0-100:0.01;blockiert=100.02 | s | tUgegen>> PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 | SE | 100 | Voltage\Vneg>> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Voltage\Vneg>> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vneg>> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x078_u002E_011 | Parametersatz 3->U<> | 078.011 | 0.02-1:0.01;blockiert=1.02 | Unom(/©3) | UNE> PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1.02 | 3 | SE | 1 | Voltage\VNG> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Voltage\VNG> | outserv | Real | E | 1 | 0 | 1.02
[16 empty] | SE | 1 | Voltage\VNG> | outserv | Real | 0 | 0 | [7 empty] | Voltage\VNG> | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1 | Voltage\VNG> | outserv | Real | 0 | 1
x078_u002E_012 | Parametersatz 3->U<> | 078.012 | 0.02-1:0.01;blockiert=1.02 | Unom(/©3) | UNE>> PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1.02 | 3 | SE | 1 | Voltage\VNG>> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Voltage\VNG>> | outserv | Real | E | 1 | 0 | 1.02
[16 empty] | SE | 1 | Voltage\VNG>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\VNG>> | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1 | Voltage\VNG>> | outserv | Real | 0 | 1
x078_u002E_013 | Parametersatz 3->U<> | 078.013 | 0-100:0.01;blockiert=100.02 | s | tUNE> PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 | SE | 100 | Voltage\VNG> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Voltage\VNG> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\VNG> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x078_u002E_014 | Parametersatz 3->U<> | 078.014 | 0-100:0.01;blockiert=100.02 | s | tUNE>> PS3 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 | SE | 100 | Voltage\VNG>> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Voltage\VNG>> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\VNG>> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x018_u002E_198 | Parametersatz 3->f<> | 018.198 | nein¦0;ja¦1 |  | Freigabe PS3 | Enum | Parameter__Funktionsparameter | 1;0 | Real |  | x056_u002E_033;x003_u002E_060 | E;E | 0;3 | 1 |  |  |  | Frequency | outserv | Real | 1 | 0 |  | x056_u002E_033;x003_u002E_060 |  |  | E;E | 0;3 |  | Frequency | outserv | Real |  |  | 1 | 0
x018_u002E_122 | Parametersatz 3->f<> | 018.122 | f¦0;f mit df/dt¦1;f m. Delta f/Delta t¦2 |  | Betriebsart f1 PS3 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 3 | 0 |  | NE | 0 | Frequency\f1 | outserv | Real | 0 | 1
x018_u002E_102 | Parametersatz 3->f<> | 018.102 | 40-70:0.01;blockiert=70.02 | Hz | f1 PS3 | Real | Parameter__Funktionsparameter |  |  |  | x018_u002E_122;x003_u002E_060 | E;E | 0;3 | 49.8 | 3 | SE | 70 | Frequency\f1 | Fset | Real | 1 | 0 |  | x018_u002E_122;x003_u002E_060 |  |  | E;E | 0;3 | 2 | Frequency\f1 | outserv | Real | E | 1 | 0 | 70.02
[16 empty] | SE | 70 | Frequency\f1 | outserv | Real | 0 | 0 | [7 empty] | Frequency\f1 | Uset | Real |  |  | 1 | 0
[16 empty] | G | 70 | Frequency\f1 | outserv | Real | 0 | 1
x018_u002E_106 | Parametersatz 3->f<> | 018.106 | 0-10:0.001;blockiert=10.002 | s | tf1 PS3 | Real | Parameter__Funktionsparameter |  |  |  | x018_u002E_122;x003_u002E_060 | E;E | 0;3 | 0 | 2 | SE | 10 | Frequency\f1 | Tdel | Real | 1 | 0 |  | x018_u002E_122;x003_u002E_060 |  |  | E;E | 0;3 | 2 | Frequency\f1 | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Frequency\f1 | Tdel | Real | 0 | 9999999 | [13 empty] | 10.002
x018_u002E_146 | Parametersatz 3->f<> | 018.146 | f¦0;f mit df/dt¦1;f m. Delta f/Delta t¦2 |  | Betriebsart f2 PS3 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 3 | 0 |  | NE | 0 | Frequency\f2 | outserv | Real | 0 | 1
x018_u002E_126 | Parametersatz 3->f<> | 018.126 | 40-70:0.01;blockiert=70.02 | Hz | f2 PS3 | Real | Parameter__Funktionsparameter |  |  |  | x018_u002E_146;x003_u002E_060 | E;E | 0;3 | 49.8 | 3 | SE | 70 | Frequency\f2 | Fset | Real | 1 | 0 |  | x018_u002E_146;x003_u002E_060 |  |  | E;E | 0;3 | 2 | Frequency\f2 | outserv | Real | E | 1 | 0 | 70.02
[16 empty] | SE | 70 | Frequency\f2 | outserv | Real | 0 | 0 | [7 empty] | Frequency\f2 | Uset | Real |  |  | 1 | 0
[16 empty] | G | 70 | Frequency\f2 | outserv | Real | 0 | 1
x018_u002E_130 | Parametersatz 3->f<> | 018.130 | 0-10:0.001;blockiert=10.002 | s | tf2 PS3 | Real | Parameter__Funktionsparameter |  |  |  | x018_u002E_146;x003_u002E_060 | E;E | 0;3 | 0 | 2 | SE | 10 | Frequency\f2 | Tdel | Real | 1 | 0 |  | x018_u002E_146;x003_u002E_060 |  |  | E;E | 0;3 | 2 | Frequency\f2 | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Frequency\f2 | Tdel | Real | 0 | 9999999 | [13 empty] | 10.002
x018_u002E_170 | Parametersatz 3->f<> | 018.170 | f¦0;f mit df/dt¦1;f m. Delta f/Delta t¦2 |  | Betriebsart f3 PS3 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 3 | 0 |  | NE | 0 | Frequency\f3 | outserv | Real | 0 | 1
x018_u002E_150 | Parametersatz 3->f<> | 018.150 | 40-70:0.01;blockiert=70.02 | Hz | f3 PS3 | Real | Parameter__Funktionsparameter |  |  |  | x018_u002E_170;x003_u002E_060 | E;E | 0;3 | 49.8 | 3 | SE | 70 | Frequency\f3 | Fset | Real | 1 | 0 |  | x018_u002E_170;x003_u002E_060 |  |  | E;E | 0;3 | 2 | Frequency\f3 | outserv | Real | E | 1 | 0 | 70.02
[16 empty] | SE | 70 | Frequency\f3 | outserv | Real | 0 | 0 | [7 empty] | Frequency\f3 | Uset | Real |  |  | 1 | 0
[16 empty] | G | 70 | Frequency\f3 | outserv | Real | 0 | 1
x018_u002E_154 | Parametersatz 3->f<> | 018.154 | 0-10:0.001;blockiert=10.002 | s | tf3 PS3 | Real | Parameter__Funktionsparameter |  |  |  | x018_u002E_170;x003_u002E_060 | E;E | 0;3 | 0 | 2 | SE | 10 | Frequency\f3 | Tdel | Real | 1 | 0 |  | x018_u002E_170;x003_u002E_060 |  |  | E;E | 0;3 | 2 | Frequency\f3 | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Frequency\f3 | Tdel | Real | 0 | 9999999 | [13 empty] | 10.002
x018_u002E_194 | Parametersatz 3->f<> | 018.194 | f¦0;f mit df/dt¦1;f m. Delta f/Delta t¦2 |  | Betriebsart f4 PS3 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 3 | 0 |  | NE | 0 | Frequency\f4 | outserv | Real | 0 | 1
x018_u002E_174 | Parametersatz 3->f<> | 018.174 | 40-70:0.01;blockiert=70.02 | Hz | f4 PS3 | Real | Parameter__Funktionsparameter |  |  |  | x018_u002E_194;x003_u002E_060 | E;E | 0;3 | 49.8 | 3 | SE | 70 | Frequency\f4 | Fset | Real | 1 | 0 |  | x018_u002E_194;x003_u002E_060 |  |  | E;E | 0;3 | 2 | Frequency\f4 | outserv | Real | E | 1 | 0 | 70.02
[16 empty] | SE | 70 | Frequency\f4 | outserv | Real | 0 | 0 | [7 empty] | Frequency\f4 | Uset | Real |  |  | 1 | 0
[16 empty] | G | 70 | Frequency\f4 | outserv | Real | 0 | 1
x018_u002E_178 | Parametersatz 3->f<> | 018.178 | 0-10:0.001;blockiert=10.002 | s | tf4 PS3 | Real | Parameter__Funktionsparameter |  |  |  | x018_u002E_194;x003_u002E_060 | E;E | 0;3 | 0 | 2 | SE | 10 | Frequency\f4 | Tdel | Real | 1 | 0 |  | x018_u002E_194;x003_u002E_060 |  |  | E;E | 0;3 | 2 | Frequency\f4 | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Frequency\f4 | Tdel | Real | 0 | 9999999 | [13 empty] | 10.002
x001_u002E_078 | Parametersatz 4->GRUND | 001.078 | niederohmig geerdet¦0;isol/komp m.Anreg.LE¦1;isol/komp o.Anreg.LE¦2;Kurzzeiterdung¦3 |  | Sternpunktbeh. PS4 | Enum | Parameter__Funktionsparameter | 0;1;2;3;4 | Real |  | x003_u002E_060 | E | 4 | 0 | 4 | E | 0 | Distance Circular\Starting | isysstar | Real | 0 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Circular\Starting | isysstar | Real | E | 0 | 1 | 0
[16 empty] | E | 0 | Distance Polygonal\Starting | isysstar | Real | 0 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Polygonal\Starting | isysstar | Real | E | 0 | 1 | 0
[16 empty] | NE | 0 | Distance Circular\Starting | isysstar | Real | 0 | 1
[16 empty] | NE | 0 | Distance Polygonal\Starting | isysstar | Real | 0 | 1
x001_u002E_081 | Parametersatz 4->GRUND | 001.081 | Erde¦0;LvE=f(Imittel,Imax)¦1 |  | Mitnahme bei 1p PS4 | Enum | Parameter__Funktionsparameter | 0;1 | Real |  | x003_u002E_060 | E | 4 | 0 | 2 |  |  | Distance Circular\Starting | itransf1p | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Circular\Starting | itransf1p | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | itransf1p | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Polygonal\Starting | itransf1p | Real |  |  | 1 | 0
x011_u002E_014 | Parametersatz 4->DIST | 011.014 | 0.1-20:0.01 | Inom | I>> PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 |  |  | Distance Circular\Starting | IMM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Circular\Starting | IMM | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | IMM | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Polygonal\Starting | IMM | Real |  |  | 1 | 0
x011_u002E_028 | Parametersatz 4->DIST | 011.028 | 0.1-1:0.01 | Inom | I> (IF)(max.Ber.)PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 0.2 | 2 |  |  | Distance Circular\Starting | IM1 | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;4 | 2 | Distance Circular\Starting | IM1 | Real | GE | 0.1 | 1 | 0
[18 empty] | Distance Polygonal\Starting | IM1 | Real | 1 | 0 | [13 empty] | 0.1
[24 empty] | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;4 | 2 | Distance Polygonal\Starting | IM1 | Real | GE | 0.1 | 1 | 0
0.1
x010_u002E_122 | Parametersatz 4->DIST | 010.122 | 0.05-1:0.01 | Inom | I> (IF)(emp.Ber.)PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 0.2 | 2 |  |  | Distance Circular\Starting | IM2 | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Circular\Starting | IM2 | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | IM2 | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Polygonal\Starting | IM2 | Real |  |  | 1 | 0
x011_u002E_027 | Parametersatz 4->DIST | 011.027 | ohne U<-Anregung¦0;mit U<-Anreg. nur LE¦1;mit U<-Anreg. LE, LL¦2 |  | Betriebsart U< PS4 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 4 | 2 | 8 | E | 0 | Distance Circular\Starting | iopt_u | Real | 0 | 0 | 4 | Distance Circular;Distance Circular\Starting;x003_u002E_060 | outserv;iopt_u | Real | E;E;E | 0;0;4 | [7 empty] | 0
[16 empty] | E | 0 | Distance Polygonal\Starting | iopt_u | Real | 0 | 0 |  | Distance Circular;Distance Circular\Starting;x003_u002E_060 | outserv;iopt_u | Real | E;E;E | 0;1;4 | 2 | Distance Circular\Starting | iVOpMode | Real | E | 0 | 0 | 1
[16 empty] | NE | 0 | Distance Circular\Starting | iopt_u | Real | 0 | 1 | [7 empty] | Distance Circular\Starting | iVOpMode | Real | E | 1 | 0 | 2
[16 empty] | NE | 0 | Distance Polygonal\Starting | iopt_u | Real | 0 | 1 |  | Distance Polygonal;Distance Polygonal\Starting;x003_u002E_060 | outserv;iopt_u | Real | E;E;E | 0;0;4 | [7 empty] | 0
[16 empty] | E | 1 | Distance Circular\Starting | iVOpMode | Real | 0 | 0 |  | Distance Polygonal;Distance Polygonal\Starting;x003_u002E_060 | outserv;iopt_u | Real | E;E;E | 0;1;4 | 2 | Distance Polygonal\Starting | iVOpMode | Real | E | 0 | 0 | 1
[16 empty] | E | 1 | Distance Polygonal\Starting | iVOpMode | Real | 0 | 0 | [7 empty] | Distance Polygonal\Starting | iVOpMode | Real | E | 1 | 0 | 2
[16 empty] | E | 2 | Distance Circular\Starting | iVOpMode | Real | 0 | 1
[16 empty] | E | 2 | Distance Polygonal\Starting | iVOpMode | Real | 0 | 1
x011_u002E_029 | Parametersatz 4->DIST | 011.029 | 0.1-0.9:0.01 | Unom(/©3) | U< PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 0.7 | 2 |  |  | Distance Circular\Starting | Um | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Circular\Starting | Um | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | Um | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Polygonal\Starting | Um | Real |  |  | 1 | 0
x011_u002E_026 | Parametersatz 4->DIST | 011.026 | ohne Z<-Anregung¦0;mit Z<-Anreg. nur LE¦1;mit Z<-Anreg. LE, LL¦2 |  | Betriebsart Z< PS4 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 4 | 2 | 8 | E | 0 | Distance Circular\Starting | iopt_z | Real | 0 | 0 | 4 | Distance Circular;Distance Circular\Starting;x003_u002E_060 | outserv;iopt_z | Real | E;E;E | 0;0;4 | [7 empty] | 0
[16 empty] | E | 0 | Distance Polygonal\Starting | iopt_z | Real | 0 | 0 |  | Distance Circular;Distance Circular\Starting;x003_u002E_060 | outserv;iopt_z | Real | E;E;E | 0;1;4 | 2 | Distance Circular\Starting | iZOpMode | Real | E | 0 | 0 | 1
[16 empty] | NE | 0 | Distance Circular\Starting | iopt_z | Real | 0 | 1 | [7 empty] | Distance Circular\Starting | iZOpMode | Real | E | 1 | 0 | 2
[16 empty] | NE | 0 | Distance Polygonal\Starting | iopt_z | Real | 0 | 1 |  | Distance Polygonal;Distance Polygonal\Starting;x003_u002E_060 | outserv;iopt_z | Real | E;E;E | 0;0;4 | [7 empty] | 0
[16 empty] | E | 1 | Distance Circular\Starting | iZOpMode | Real | 0 | 0 |  | Distance Polygonal;Distance Polygonal\Starting;x003_u002E_060 | outserv;iopt_z | Real | E;E;E | 0;1;4 | 2 | Distance Polygonal\Starting | iZOpMode | Real | E | 0 | 0 | 1
[16 empty] | E | 1 | Distance Polygonal\Starting | iZOpMode | Real | 0 | 0 | [7 empty] | Distance Polygonal\Starting | iZOpMode | Real | E | 1 | 0 | 2
[16 empty] | E | 2 | Distance Circular\Starting | iZOpMode | Real | 0 | 1
[16 empty] | E | 2 | Distance Polygonal\Starting | iZOpMode | Real | 0 | 1
x011_u002E_010 | Parametersatz 4->DIST | 011.010 | 0.1-300:0.01 | — | Xv PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 10 | 2 |  |  | Distance Circular\Starting | Xfw | Real | 0.2 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;4 | 2 | Distance Circular\Starting | Xfw | Real | SE | 60 | 5 | 0
[18 empty] | Distance Polygonal\Starting | Xfw | Real | 0.2 | 0 | [13 empty] | 300
[24 empty] | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;4 | 2 | Distance Polygonal\Starting | Xfw | Real | SE | 60 | 5 | 0
300
x011_u002E_011 | Parametersatz 4->DIST | 011.011 | 0.1-300:0.01 | — | Rv,LE PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 10 | 2 |  |  | Distance Circular\Starting | RfPG | Real | 0.2 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;4 | 2 | Distance Circular\Starting | RfPG | Real | SE | 60 | 5 | 0
[18 empty] | Distance Polygonal\Starting | RfPG | Real | 0.2 | 0 | [13 empty] | 300
[24 empty] | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;4 | 2 | Distance Polygonal\Starting | RfPG | Real | SE | 60 | 5 | 0
300
x011_u002E_012 | Parametersatz 4->DIST | 011.012 | 0.1-300:0.01 | — | Rv,LL PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 10 | 2 |  |  | Distance Circular\Starting | RfPP | Real | 0.2 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;4 | 2 | Distance Circular\Starting | RfPP | Real | SE | 60 | 5 | 0
[18 empty] | Distance Polygonal\Starting | RfPP | Real | 0.2 | 0 | [13 empty] | 300
[24 empty] | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;4 | 2 | Distance Polygonal\Starting | RfPP | Real | SE | 60 | 5 | 0
300
x011_u002E_023 | Parametersatz 4->DIST | 011.023 | 15-65:1 | ° | ß PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 30 | 2 |  |  | Distance Circular\Starting | Beta | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Circular\Starting | Beta | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | Beta | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Polygonal\Starting | Beta | Real |  |  | 1 | 0
x010_u002E_104 | Parametersatz 4->DIST | 010.104 | 0-300:0.01 | — | Zv,LE PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 0 | 2 |  |  | Distance Circular\Starting | ZfPG | Real | 0.2 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;4 | 2 | Distance Circular\Starting | ZfPG | Real | SE | 60 | 5 | 0
[18 empty] | Distance Polygonal\Starting | ZfPG | Real | 0.2 | 0 | [13 empty] | 300
[24 empty] | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;4 | 2 | Distance Polygonal\Starting | ZfPG | Real | SE | 60 | 5 | 0
300
x010_u002E_108 | Parametersatz 4->DIST | 010.108 | 0-300:0.01 | — | Zv,LL PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 0 | 2 |  |  | Distance Circular\Starting | ZfPP | Real | 0.2 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;4 | 2 | Distance Circular\Starting | ZfPP | Real | SE | 60 | 5 | 0
[18 empty] | Distance Polygonal\Starting | ZfPP | Real | 0.2 | 0 | [13 empty] | 300
[24 empty] | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;4 | 2 | Distance Polygonal\Starting | ZfPP | Real | SE | 60 | 5 | 0
300
x011_u002E_013 | Parametersatz 4->DIST | 011.013 | 0.1-4:0.01 |  | Zr/Zv PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 0.5 | 2 |  |  | Distance Circular\Starting | ZbwZfw | Real | 0.2 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;4 | 2 | Distance Circular\Starting | ZbwZfw | Real | GE | 0.1 | 1 | 0
[18 empty] | Distance Polygonal\Starting | ZbwZfw | Real | 0.2 | 0 | [13 empty] | 0.1
[24 empty] | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;4 | 2 | Distance Polygonal\Starting | ZbwZfw | Real | GE | 0.1 | 1 | 0
0.1
x011_u002E_015 | Parametersatz 4->DIST | 011.015 | 0.1-2:0.01 | Inom | IE> (max.Ber.) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 0.2 | 2 |  |  | Distance Circular\Starting | INMM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;4 | 2 | Distance Circular\Starting | INMM | Real | GE | 0.1 | 1 | 0
[18 empty] | Distance Polygonal\Starting | INMM | Real | 1 | 0 | [13 empty] | 0.1
[24 empty] | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;4 | 2 | Distance Polygonal\Starting | INMM | Real | GE | 0.1 | 1 | 0
0.1
x010_u002E_126 | Parametersatz 4->DIST | 010.126 | 0.05-2:0.01 | Inom | IE> (emp.Ber.) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 0.2 | 2 |  |  | Distance Circular\Starting | INM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Circular\Starting | INM | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | INM | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Polygonal\Starting | INM | Real |  |  | 1 | 0
x011_u002E_017 | Parametersatz 4->DIST | 011.017 | 0-0.5:0.001 | s | tIE> PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 0.1 | 2 |  |  | Distance Circular\Starting | tINM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Circular\Starting | tINM | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | tINM | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Polygonal\Starting | tINM | Real |  |  | 1 | 0
x011_u002E_016 | Parametersatz 4->DIST | 011.016 | 0.02-1:0.01 | Unom/©3 | UNE> PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 0.1 | 2 |  |  | Distance Circular\Starting | VNGM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;4 | 2 | Distance Circular\Starting | VNGM | Real | GE | 0.02 | 1 | 0
[18 empty] | Distance Polygonal\Starting | VNGM | Real | 1 | 0 | [13 empty] | 0.02
[24 empty] | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;4 | 2 | Distance Polygonal\Starting | VNGM | Real | GE | 0.02 | 1 | 0
0.02
x011_u002E_022 | Parametersatz 4->DIST | 011.022 | 0.2-1:0.01 | Unom/©3 | UNE>> PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 0.5 | 2 |  |  | Distance Circular\Starting | VNGMM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Circular\Starting | VNGMM | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | VNGMM | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Polygonal\Starting | VNGMM | Real |  |  | 1 | 0
x011_u002E_021 | Parametersatz 4->DIST | 011.021 | 0-60:0.001 | s | tUNE>> PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 |  |  | Distance Circular\Starting | tVNGMM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Circular\Starting | tVNGMM | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | tVNGMM | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Polygonal\Starting | tVNGMM | Real |  |  | 1 | 0
x013_u002E_087 | Parametersatz 4->DIST | 013.087 | 0-8:0.01 |  | Betrag kE PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 |  |  | Distance Circular\Polarisation | k0 | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Circular\Polarisation | k0 | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Polarisation | k0 | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Polygonal\Polarisation | k0 | Real |  |  | 1 | 0
x013_u002E_086 | Parametersatz 4->DIST | 013.086 | -180-180:1 | ° | Winkel kE PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 0 | 2 |  |  | Distance Circular\Polarisation | phik0 | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Circular\Polarisation | phik0 | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Polarisation | phik0 | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Polygonal\Polarisation | phik0 | Real |  |  | 1 | 0
x075_u002E_097 | Parametersatz 4->DIST | 075.097 | Kreis¦0;Polygon¦1 |  | Kennlinientyp PS4 | Enum | Parameter__Funktionsparameter | 0;1 | Real |  | x056_u002E_014;x031_u002E_073;x003_u002E_060 | E;E;E | 0;0;4 | 1 | 4 | E | 0 | Distance Circular | outserv | Real | 0 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Distance Circular | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 0 | Distance Polygonal | outserv | Real | 0 | 1 | [13 empty] | 1
[16 empty] | E | 1 | Distance Circular | outserv | Real | 0 | 1
[16 empty] | E | 1 | Distance Polygonal | outserv | Real | 0 | 0
x013_u002E_051 | Parametersatz 4->DIST | 013.051 | 0.1-200:0.01 | — | X1 (Polygon) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 10 |  |  |  | Distance Polygonal\Z1 | Xmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Polygonal\Z1 | Xmax | Real | SE | 40 | 5 | 0
200
x013_u002E_052 | Parametersatz 4->DIST | 013.052 | 0.1-200:0.01 | — | X2 (Polygon) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 20 |  |  |  | Distance Polygonal\Z2 | Xmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Polygonal\Z2 | Xmax | Real | SE | 40 | 5 | 0
200
x013_u002E_053 | Parametersatz 4->DIST | 013.053 | 0.1-200:0.01 | — | X3 (Polygon) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 30 |  |  |  | Distance Polygonal\Z3 | Xmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Polygonal\Z3 | Xmax | Real | SE | 40 | 5 | 0
200
x013_u002E_054 | Parametersatz 4->DIST | 013.054 | 0.1-200:0.01 | — | X4 (Polygon) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 40 |  |  |  | Distance Polygonal\Z4 | Xmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Polygonal\Z4 | Xmax | Real | SE | 40 | 5 | 0
200
x012_u002E_103 | Parametersatz 4->DIST | 012.103 | 0.1-200:0.01 | — | X5 (Polygon) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 50 |  |  |  | Distance Polygonal\Z5 | Xmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Polygonal\Z5 | Xmax | Real | SE | 40 | 5 | 0
200
x012_u002E_107 | Parametersatz 4->DIST | 012.107 | 0.1-200:0.01 | — | X6 (Polygon) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 60 |  |  |  | Distance Polygonal\Z6 | Xmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Polygonal\Z6 | Xmax | Real | SE | 40 | 5 | 0
200
x013_u002E_055 | Parametersatz 4->DIST | 013.055 | 0.1-200:0.01 | — | R1,LE (Polygon) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 10 |  |  |  | Distance Polygonal\Z1 | REmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Polygonal\Z1 | REmax | Real | SE | 40 | 5 | 0
200
x013_u002E_056 | Parametersatz 4->DIST | 013.056 | 0.1-200:0.01 | — | R1,LL (Polygon) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 10 |  |  |  | Distance Polygonal\Z1 | Rmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Polygonal\Z1 | Rmax | Real | SE | 40 | 5 | 0
200
x013_u002E_057 | Parametersatz 4->DIST | 013.057 | 0.1-200:0.01 | — | R2,LE (Polygon) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 20 |  |  |  | Distance Polygonal\Z2 | REmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Polygonal\Z2 | REmax | Real | SE | 40 | 5 | 0
200
x013_u002E_058 | Parametersatz 4->DIST | 013.058 | 0.1-200:0.01 | — | R2,LL (Polygon) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 20 |  |  |  | Distance Polygonal\Z2 | Rmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Polygonal\Z2 | Rmax | Real | SE | 40 | 5 | 0
200
x013_u002E_059 | Parametersatz 4->DIST | 013.059 | 0.1-200:0.01 | — | R3,LE (Polygon) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 30 |  |  |  | Distance Polygonal\Z3 | REmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Polygonal\Z3 | REmax | Real | SE | 40 | 5 | 0
200
x013_u002E_060 | Parametersatz 4->DIST | 013.060 | 0.1-200:0.01 | — | R3,LL (Polygon) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 30 |  |  |  | Distance Polygonal\Z3 | Rmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Polygonal\Z3 | Rmax | Real | SE | 40 | 5 | 0
200
x013_u002E_061 | Parametersatz 4->DIST | 013.061 | 0.1-200:0.01 | — | R4,LE (Polygon) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 40 |  |  |  | Distance Polygonal\Z4 | REmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Polygonal\Z4 | REmax | Real | SE | 40 | 5 | 0
200
x013_u002E_062 | Parametersatz 4->DIST | 013.062 | 0.1-200:0.01 | — | R4,LL (Polygon) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 40 |  |  |  | Distance Polygonal\Z4 | Rmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Polygonal\Z4 | Rmax | Real | SE | 40 | 5 | 0
200
x012_u002E_111 | Parametersatz 4->DIST | 012.111 | 0.1-200:0.01 | — | R5,LE (Polygon) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 50 |  |  |  | Distance Polygonal\Z5 | REmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Polygonal\Z5 | REmax | Real | SE | 40 | 5 | 0
200
x012_u002E_115 | Parametersatz 4->DIST | 012.115 | 0.1-200:0.01 | — | R5,LL (Polygon) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 50 |  |  |  | Distance Polygonal\Z5 | Rmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Polygonal\Z5 | Rmax | Real | SE | 40 | 5 | 0
200
x012_u002E_119 | Parametersatz 4->DIST | 012.119 | 0.1-200:0.01 | — | R6,LE (Polygon) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 60 |  |  |  | Distance Polygonal\Z6 | REmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Polygonal\Z6 | REmax | Real | SE | 40 | 5 | 0
200
x012_u002E_123 | Parametersatz 4->DIST | 012.123 | 0.1-200:0.01 | — | R6,LL (Polygon) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 60 |  |  |  | Distance Polygonal\Z6 | Rmax | Real | 0.2 | 0 |  | Distance Polygonal;Distance Polygonal\Z6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Polygonal\Z6 | Rmax | Real | SE | 40 | 5 | 0
200
x013_u002E_063 | Parametersatz 4->DIST | 013.063 | 40-90:1 | ° | €1 (Polygon) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 75 |  |  |  | Distance Polygonal\Z1 | phi | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Polygonal\Z1 | phi | Real | GE | 40 | 1 | 0
40
x013_u002E_064 | Parametersatz 4->DIST | 013.064 | 40-90:1 | ° | €2 (Polygon) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 75 |  |  |  | Distance Polygonal\Z2 | phi | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Polygonal\Z2 | phi | Real | GE | 40 | 1 | 0
40
x013_u002E_065 | Parametersatz 4->DIST | 013.065 | 40-90:1 | ° | €3 (Polygon) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 75 |  |  |  | Distance Polygonal\Z3 | phi | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Polygonal\Z3 | phi | Real | GE | 40 | 1 | 0
40
x013_u002E_066 | Parametersatz 4->DIST | 013.066 | 40-90:1 | ° | €4 (Polygon) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 75 |  |  |  | Distance Polygonal\Z4 | phi | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Polygonal\Z4 | phi | Real | GE | 40 | 1 | 0
40
x012_u002E_127 | Parametersatz 4->DIST | 012.127 | 40-90:1 | ° | €5 (Polygon) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 75 |  |  |  | Distance Polygonal\Z5 | phi | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Polygonal\Z5 | phi | Real | GE | 40 | 1 | 0
40
x012_u002E_131 | Parametersatz 4->DIST | 012.131 | 40-90:1 | ° | €6 (Polygon) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 75 |  |  |  | Distance Polygonal\Z6 | phi | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Polygonal\Z6 | phi | Real | GE | 40 | 1 | 0
40
x075_u002E_086 | Parametersatz 4->DIST | 075.086 | -20-20:1 | ° | ‹1 (Polygon) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 0 |  |  |  | Distance Polygonal\Z1 | beta | Real | -1 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\Z1 | beta | Real |  |  | -1 | 0
x075_u002E_087 | Parametersatz 4->DIST | 075.087 | -20-20:1 | ° | ‹2 (Polygon) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 0 |  |  |  | Distance Polygonal\Z2 | beta | Real | -1 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\Z2 | beta | Real |  |  | -1 | 0
x075_u002E_088 | Parametersatz 4->DIST | 075.088 | -20-20:1 | ° | ‹3 (Polygon) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 0 |  |  |  | Distance Polygonal\Z3 | beta | Real | -1 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\Z3 | beta | Real |  |  | -1 | 0
x075_u002E_089 | Parametersatz 4->DIST | 075.089 | -20-20:1 | ° | ‹4 (Polygon) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 0 |  |  |  | Distance Polygonal\Z4 | beta | Real | -1 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\Z4 | beta | Real |  |  | -1 | 0
x012_u002E_159 | Parametersatz 4->DIST | 012.159 | -20-20:1 | ° | ‹5 (Polygon) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 0 |  |  |  | Distance Polygonal\Z5 | beta | Real | -1 | 0 |  | Distance Polygonal;Distance Polygonal\Z5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\Z5 | beta | Real |  |  | -1 | 0
x012_u002E_163 | Parametersatz 4->DIST | 012.163 | -20-20:1 | ° | ‹6 (Polygon) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 0 |  |  |  | Distance Polygonal\Z6 | beta | Real | -1 | 0 |  | Distance Polygonal;Distance Polygonal\Z6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\Z6 | beta | Real |  |  | -1 | 0
x075_u002E_091 | Parametersatz 4->DIST | 075.091 | 0.05-200:0.01 | — | Z1 (Kreis) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 10 |  |  |  | Distance Circular\Z1 | Zm | Real | 0.2 | 0 |  | Distance Circular;Distance Circular\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Circular\Z1 | Zm | Real | SE | 40 | 5 | 0
200
x075_u002E_092 | Parametersatz 4->DIST | 075.092 | 0.05-200:0.01 | — | Z2 (Kreis) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 20 |  |  |  | Distance Circular\Z2 | Zm | Real | 0.2 | 0 |  | Distance Circular;Distance Circular\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Circular\Z2 | Zm | Real | SE | 40 | 5 | 0
200
x075_u002E_093 | Parametersatz 4->DIST | 075.093 | 0.05-200:0.01 | — | Z3 (Kreis) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 30 |  |  |  | Distance Circular\Z3 | Zm | Real | 0.2 | 0 |  | Distance Circular;Distance Circular\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Circular\Z3 | Zm | Real | SE | 40 | 5 | 0
200
x075_u002E_094 | Parametersatz 4->DIST | 075.094 | 0.05-200:0.01 | — | Z4 (Kreis) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 40 |  |  |  | Distance Circular\Z4 | Zm | Real | 0.2 | 0 |  | Distance Circular;Distance Circular\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Circular\Z4 | Zm | Real | SE | 40 | 5 | 0
200
x012_u002E_151 | Parametersatz 4->DIST | 012.151 | 0.05-200:0.01 | — | Z5 (Kreis) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 50 |  |  |  | Distance Circular\Z5 | Zm | Real | 0.2 | 0 |  | Distance Circular;Distance Circular\Z5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Circular\Z5 | Zm | Real | SE | 40 | 5 | 0
200
x012_u002E_155 | Parametersatz 4->DIST | 012.155 | 0.05-200:0.01 | — | Z6 (Kreis) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 60 |  |  |  | Distance Circular\Z6 | Zm | Real | 0.2 | 0 |  | Distance Circular;Distance Circular\Z6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Circular\Z6 | Zm | Real | SE | 40 | 5 | 0
200
x075_u002E_090 | Parametersatz 4->DIST | 075.090 | 10-90:1 | ° | €1 (Kreis) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 75 | 2 |  |  | Distance Circular\Z1 | arcalpha | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Circular\Z1 | arcalpha | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z1E | arcalpha | Real | 1 | 0
x075_u002E_095 | Parametersatz 4->DIST | 075.095 | 10-90:1 | ° | €2 (Kreis) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 75 |  |  |  | Distance Circular\Z2 | arcalpha | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Circular\Z2 | arcalpha | Real |  |  | 1 | 0
x075_u002E_096 | Parametersatz 4->DIST | 075.096 | 10-90:1 | ° | €3 (Kreis) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 75 |  |  |  | Distance Circular\Z3 | arcalpha | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Circular\Z3 | arcalpha | Real |  |  | 1 | 0
x075_u002E_099 | Parametersatz 4->DIST | 075.099 | 10-90:1 | ° | €4 (Kreis) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 75 |  |  |  | Distance Circular\Z4 | arcalpha | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Circular\Z4 | arcalpha | Real |  |  | 1 | 0
x012_u002E_167 | Parametersatz 4->DIST | 012.167 | 10-90:1 | ° | €5 (Kreis) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 75 |  |  |  | Distance Circular\Z5 | arcalpha | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Circular\Z5 | arcalpha | Real |  |  | 1 | 0
x012_u002E_171 | Parametersatz 4->DIST | 012.171 | 10-90:1 | ° | €6 (Kreis) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 75 |  |  |  | Distance Circular\Z6 | arcalpha | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Circular\Z6 | arcalpha | Real |  |  | 1 | 0
x012_u002E_092 | Parametersatz 4->DIST | 012.092 | nein¦0;ja¦1 |  | Li.bo.komp. Kr. PS4 | Enum | Parameter__Funktionsparameter | 0;1 | Real |  | x003_u002E_060 | E | 4 | 0 | 7 |  |  | Distance Circular\Z1 | arcen | Real | 1 | 0 | 6 | Distance Circular;Distance Circular\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Circular\Z1 | arcen | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z1E | arcen | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Circular\Z2 | arcen | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z2 | arcen | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Circular\Z3 | arcen | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z3 | arcen | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Circular\Z4 | arcen | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z4 | arcen | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Circular\Z5 | arcen | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z5 | arcen | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Circular\Z6 | arcen | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z6 | arcen | Real | 1 | 0
x013_u002E_073 | Parametersatz 4->DIST | 013.073 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung N1 PS4 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 4 | 0 | 4 | NE | 2 | Distance Circular\Z1 | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Circular\Z1 | idir | Real |  |  | 1 | 0
[16 empty] | NE | 2 | Distance Circular\Z1E | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\Z1 | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z1 | idir | Real | 1 | 0
[18 empty] | Distance Polygonal\Z1E | idir | Real | 1 | 0
x013_u002E_074 | Parametersatz 4->DIST | 013.074 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung N2 PS4 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 4 | 0 |  | NE | 2 | Distance Circular\Z2 | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Circular\Z2 | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z2 | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\Z2 | idir | Real |  |  | 1 | 0
x013_u002E_075 | Parametersatz 4->DIST | 013.075 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung N3 PS4 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 4 | 0 |  | NE | 2 | Distance Circular\Z3 | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Circular\Z3 | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z3 | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\Z3 | idir | Real |  |  | 1 | 0
x013_u002E_076 | Parametersatz 4->DIST | 013.076 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung N4 PS4 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 4 | 0 |  | NE | 2 | Distance Circular\Z4 | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Circular\Z4 | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z4 | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\Z4 | idir | Real |  |  | 1 | 0
x013_u002E_077 | Parametersatz 4->DIST | 013.077 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung N5 PS4 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 4 | 0 |  | NE | 2 | Distance Circular\Z5 | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Circular\Z5 | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z5 | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\Z5 | idir | Real |  |  | 1 | 0
x012_u002E_135 | Parametersatz 4->DIST | 012.135 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung N6 PS4 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 4 | 0 |  | NE | 2 | Distance Circular\Z6 | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Circular\Z6 | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z6 | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\Z6 | idir | Real |  |  | 1 | 0
x012_u002E_139 | Parametersatz 4->DIST | 012.139 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung N7 PS4 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 4 | 0 |  |  |  | Distance Circular\Directional | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Directional;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Circular\Directional | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Directional | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Directional;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\Directional | idir | Real |  |  | 1 | 0
x013_u002E_078 | Parametersatz 4->DIST | 013.078 | 0-60:0.001;blockiert=60.002 | s | t1 PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 0 | 4 | SE | 60 | Distance Circular\T1 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Circular\T1 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Circular\T1 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
[16 empty] | SE | 60 | Distance Polygonal\T1 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Polygonal\T1 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Polygonal\T1 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
x013_u002E_079 | Parametersatz 4->DIST | 013.079 | 0-60:0.001;blockiert=60.002 | s | t2 PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1 | 4 | SE | 60 | Distance Circular\T2 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Circular\T2 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Circular\T2 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
[16 empty] | SE | 60 | Distance Polygonal\T2 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Polygonal\T2 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Polygonal\T2 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
x013_u002E_080 | Parametersatz 4->DIST | 013.080 | 0-60:0.001;blockiert=60.002 | s | t3 PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 2 | 4 | SE | 60 | Distance Circular\T3 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Circular\T3 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Circular\T3 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
[16 empty] | SE | 60 | Distance Polygonal\T3 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Polygonal\T3 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Polygonal\T3 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
x013_u002E_081 | Parametersatz 4->DIST | 013.081 | 0-60:0.001;blockiert=60.002 | s | t4 PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 3 | 4 | SE | 60 | Distance Circular\T4 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Circular\T4 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Circular\T4 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
[16 empty] | SE | 60 | Distance Polygonal\T4 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Polygonal\T4 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Polygonal\T4 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
x013_u002E_082 | Parametersatz 4->DIST | 013.082 | 0-60:0.001;blockiert=60.002 | s | t5 PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 4 | 4 | SE | 60 | Distance Circular\T5 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Circular\T5 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Circular\T5 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
[16 empty] | SE | 60 | Distance Polygonal\T5 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Polygonal\T5 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Polygonal\T5 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
x013_u002E_083 | Parametersatz 4->DIST | 013.083 | 0-60:0.001;blockiert=60.002 | s | t6 PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 5 | 4 | SE | 60 | Distance Circular\T6 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Circular\T6 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Circular\T6 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
[16 empty] | SE | 60 | Distance Polygonal\T6 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Polygonal\T6 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Polygonal\T6 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
x012_u002E_143 | Parametersatz 4->DIST | 012.143 | 0-60:0.001;blockiert=60.002 | s | t7 PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 6 | 4 | SE | 60 | Distance Circular\T9 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T9;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Circular\T9 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Circular\T9 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
[16 empty] | SE | 60 | Distance Polygonal\T9 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T9;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Polygonal\T9 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Polygonal\T9 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
x012_u002E_147 | Parametersatz 4->DIST | 012.147 | 0-60:0.001;blockiert=60.002 | s | t8 PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 7 | 4 | SE | 60 | Distance Circular\T10 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T10;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Circular\T10 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Circular\T10 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
[16 empty] | SE | 60 | Distance Polygonal\T10 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T10;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Polygonal\T10 | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Polygonal\T10 | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
x013_u002E_085 | Parametersatz 4->DIST | 013.085 | 1-450:0.01 |  | kÜ,LL KU PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1.2 | 3 |  |  | Distance Circular\Z1E | kZ | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z1E;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Circular\Z1E | kZ | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z1E | kX | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z1E;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\Z1E | kX | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z1E | kR | Real | 1 | 0
x015_u002E_017 | Parametersatz 4->SV | 015.017 | nein¦0;ja¦1 |  | Freigabe PS4 | Enum | Parameter__Funktionsparameter | 0;1 | String |  | x003_u002E_060 | E | 4 | 0 | 2 |  |  | Distance Circular\PSIG Connect | aDipset | String |  |  | 2 | Distance Circular;Distance Circular\PSIG Connect;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Circular\PSIG Connect | aDipset | String
[18 empty] | Distance Polygonal\PSIG Connect | aDipset | String |  |  |  | Distance Polygonal;Distance Polygonal\PSIG Connect;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\PSIG Connect | aDipset | String
x025_u002E_020 | Parametersatz 4->SV | 025.020 | keine¦0;direkte Schaltermitn¦1;anregeabh. Mitnahme¦2;Meßbereichserweiter.¦3;Freigabeverfahren¦4;Sperrverfahren¦5;GS-Schleife¦6;rückwärtige Verrieg.¦7;Richtungsvergleich¦8 |  | Betriebsart PS4 | Enum | Parameter__Funktionsparameter | ;DIRECT = TRIP;PUTT = TRIP;POTT = TRIP;COMP_RELEASE = TRIP;COMP_BLOCK = TRIP;COMP_PILOT = TRIP; | String |  | x003_u002E_060 | E | 4 | PUTT = TRIP | 4 |  |  | Distance Circular\PSIG Receive | sLogic | String |  |  | 2 | Distance Circular;Distance Circular\PSIG Receive;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Circular\PSIG Receive | sLogic | String
[18 empty] | Distance Circular\PSIG Send | sLogic | String |  |  |  | Distance Polygonal;Distance Polygonal\PSIG Receive;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\PSIG Receive | sLogic | String
[18 empty] | Distance Polygonal\PSIG Receive | sLogic | String
[18 empty] | Distance Polygonal\PSIG Send | sLogic | String
x025_u002E_023 | Parametersatz 4->SV | 025.023 | 0-60:0.001;blockiert=60.002 | s | Startzeit PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 0.08 | 4 | SE | 60 | Distance Circular\PSIG T | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\PSIG T;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Circular\PSIG T | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Circular\PSIG T | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
[16 empty] | SE | 60 | Distance Polygonal\PSIG T | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\PSIG T;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Polygonal\PSIG T | Tdelay | Real | SE | 60 | 1 | 0
[16 empty] | G | 60 | Distance Polygonal\PSIG T | Tdelay | Real | 0 | 9999999 | [13 empty] | 60.002
x025_u002E_021 | Parametersatz 4->SV | 025.021 | 0-10:0.001 | s | Rückf.zeit Send. PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 0.25 | 2 |  |  | Distance Circular\PSIG T Reset | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\PSIG T Reset;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Circular\PSIG T Reset | Tdelay | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\PSIG T Reset | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\PSIG T Reset;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\PSIG T Reset | Tdelay | Real |  |  | 1 | 0
x075_u002E_098 | Parametersatz 4->UMZ | 075.098 | nein¦0;ja¦1 |  | Freigabe PS4 | Enum | Parameter__Funktionsparameter | 1;0 | Real |  | x056_u002E_008;x003_u002E_060 | E;E | 0;3 | 1 | 12 |  |  | Overcurrent\I> | outserv | Real | 1 | 0 |  | x056_u002E_008;x003_u002E_060 |  |  | E;E | 0;4 | 12 | Overcurrent\I> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\I>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\I>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\I>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\I>>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\I>>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\I>>>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\IN> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\IN> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\IN>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\IN>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\IN>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\IN>>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\IN>>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\IN>>>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\Ineg> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\Ineg> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\Ineg>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\Ineg>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\Ineg>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\Ineg>>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\Ineg>>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\Ineg>>>> | outserv | Real |  |  | 1 | 0
x075_u002E_007 | Parametersatz 4->UMZ | 075.007 | 0.1-20:0.01 | Inom | I> PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 |  |  | Overcurrent\I> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 3 | Overcurrent\I> | Ipset | Real | G | 20 | 0 | 20
[18 empty] | Overcurrent\I> | idir | Real | 0 | 0 | [7 empty] | Overcurrent\I> | Ipset | Real | S | 0.1 | 0 | 0.1
[30 empty] | Overcurrent\I> | Ipset | Real |  |  | 1 | 0
x075_u002E_008 | Parametersatz 4->UMZ | 075.008 | 0.1-20:0.01 | Inom | I>> PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 |  |  | Overcurrent\I>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 3 | Overcurrent\I>> | Ipset | Real | G | 20 | 0 | 20
[18 empty] | Overcurrent\I>> | idir | Real | 0 | 0 | [7 empty] | Overcurrent\I>> | Ipset | Real | S | 0.1 | 0 | 0.1
[30 empty] | Overcurrent\I>> | Ipset | Real |  |  | 1 | 0
x075_u002E_009 | Parametersatz 4->UMZ | 075.009 | 0.1-20:0.01 | Inom | I>>> PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 |  |  | Overcurrent\I>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 3 | Overcurrent\I>>> | Ipset | Real | G | 20 | 0 | 20
[18 empty] | Overcurrent\I>>> | idir | Real | 0 | 0 | [7 empty] | Overcurrent\I>>> | Ipset | Real | S | 0.1 | 0 | 0.1
[30 empty] | Overcurrent\I>>> | Ipset | Real |  |  | 1 | 0
x075_u002E_010 | Parametersatz 4->UMZ | 075.010 | 0.1-20:0.01 | Inom | I>>>> PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 |  |  | Overcurrent\I>>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 3 | Overcurrent\I>>>> | Ipset | Real | G | 20 | 0 | 20
[18 empty] | Overcurrent\I>>>> | idir | Real | 0 | 0 | [7 empty] | Overcurrent\I>>>> | Ipset | Real | S | 0.1 | 0 | 0.1
[30 empty] | Overcurrent\I>>>> | Ipset | Real |  |  | 1 | 0
x075_u002E_019 | Parametersatz 4->UMZ | 075.019 | 0-30:0.001;blockiert=30.002 | s | tI> PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 | SE | 30 | Overcurrent\I> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Overcurrent\I> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\I> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x075_u002E_020 | Parametersatz 4->UMZ | 075.020 | 0-30:0.001;blockiert=30.002 | s | tI>> PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 | SE | 30 | Overcurrent\I>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Overcurrent\I>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\I>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x075_u002E_021 | Parametersatz 4->UMZ | 075.021 | 0-30:0.001;blockiert=30.002 | s | tI>>> PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 | SE | 30 | Overcurrent\I>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Overcurrent\I>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\I>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x075_u002E_022 | Parametersatz 4->UMZ | 075.022 | 0-30:0.001;blockiert=30.002 | s | tI>>>> PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 | SE | 30 | Overcurrent\I>>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Overcurrent\I>>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\I>>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x075_u002E_011 | Parametersatz 4->UMZ | 075.011 | 0.1-20:0.01 | Inom | Igegen> PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1 |  |  |  | Overcurrent\IN> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\IN> | Ipset | Real |  |  | 1 | 0
x075_u002E_012 | Parametersatz 4->UMZ | 075.012 | 0.1-20:0.01 | Inom | Igegen>> PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1 |  |  |  | Overcurrent\IN>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\IN>> | Ipset | Real |  |  | 1 | 0
x075_u002E_013 | Parametersatz 4->UMZ | 075.013 | 0.1-20:0.01 | Inom | Igegen>>> PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1 |  |  |  | Overcurrent\IN>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\IN>>> | Ipset | Real |  |  | 1 | 0
x075_u002E_014 | Parametersatz 4->UMZ | 075.014 | 0.1-20:0.01 | Inom | Igegen>>>> PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1 |  |  |  | Overcurrent\IN>>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\IN>>>> | Ipset | Real |  |  | 1 | 0
x075_u002E_023 | Parametersatz 4->UMZ | 075.023 | 0-30:0.001;blockiert=30.002 | s | tIgegen> PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 | SE | 30 | Overcurrent\IN> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Overcurrent\IN> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\IN> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x075_u002E_024 | Parametersatz 4->UMZ | 075.024 | 0-30:0.001;blockiert=30.002 | s | tIgegen>> PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 | SE | 30 | Overcurrent\IN>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Overcurrent\IN>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\IN>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x075_u002E_025 | Parametersatz 4->UMZ | 075.025 | 0-30:0.001;blockiert=30.002 | s | tIgegen>>> PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 | SE | 30 | Overcurrent\IN>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Overcurrent\IN>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\IN>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x075_u002E_026 | Parametersatz 4->UMZ | 075.026 | 0-30:0.001;blockiert=30.002 | s | tIgegen>>>> PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 | SE | 30 | Overcurrent\IN>>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Overcurrent\IN>>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\IN>>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x075_u002E_015 | Parametersatz 4->UMZ | 075.015 | 0.1-20:0.01 | Inom | IE> PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1 |  |  |  | Overcurrent\Ineg> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\Ineg> | Ipset | Real |  |  | 1 | 0
x075_u002E_016 | Parametersatz 4->UMZ | 075.016 | 0.1-20:0.01 | Inom | IE>> PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1 |  |  |  | Overcurrent\Ineg>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\Ineg>> | Ipset | Real |  |  | 1 | 0
x075_u002E_017 | Parametersatz 4->UMZ | 075.017 | 0.1-20:0.01 | Inom | IE>>> PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1 |  |  |  | Overcurrent\Ineg>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\Ineg>>> | Ipset | Real |  |  | 1 | 0
x075_u002E_018 | Parametersatz 4->UMZ | 075.018 | 0.1-20:0.01 | Inom | IE>>>> PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1 |  |  |  | Overcurrent\Ineg>>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\Ineg>>>> | Ipset | Real |  |  | 1 | 0
x075_u002E_027 | Parametersatz 4->UMZ | 075.027 | 0-30:0.001;blockiert=30.002 | s | tIE> PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 | SE | 30 | Overcurrent\Ineg> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Overcurrent\Ineg> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\Ineg> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x075_u002E_028 | Parametersatz 4->UMZ | 075.028 | 0-30:0.001;blockiert=30.002 | s | tIE>> PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 | SE | 30 | Overcurrent\Ineg>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Overcurrent\Ineg>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\Ineg>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x075_u002E_029 | Parametersatz 4->UMZ | 075.029 | 0-30:0.001;blockiert=30.002 | s | tIE>>> PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 | SE | 30 | Overcurrent\Ineg>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Overcurrent\Ineg>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\Ineg>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x075_u002E_030 | Parametersatz 4->UMZ | 075.030 | 0-30:0.001;blockiert=30.002 | s | tIE>>>> PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 | SE | 30 | Overcurrent\Ineg>>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Overcurrent\Ineg>>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\Ineg>>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x010_u002E_139 | Parametersatz 4->UMZ | 010.139 | 0.01-0.5:0.001 | Unom/©3 | UNE> PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 0.03 |  |  |  | Overcurrent\Directional N | upolu | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\Directional N | upolu | Real |  |  | 1 | 0
x004_u002E_249 | Parametersatz 4->UMZ | 004.249 | -90-90:1 | ° | Winkel phiE PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 0 |  |  |  | Overcurrent\Directional N | mtau | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\Directional N | mtau | Real |  |  | 1 | 0
x072_u002E_091 | Parametersatz 4->UMZ | 072.091 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung tIE> PS4 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real |  | x003_u002E_060 | E | 4 | 1 |  |  |  | Overcurrent\IN> | idir | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\IN> | idir | Real |  |  | 1 | 0
x072_u002E_092 | Parametersatz 4->UMZ | 072.092 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung tIE>> PS4 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real |  | x003_u002E_060 | E | 4 | 1 |  |  |  | Overcurrent\IN>> | idir | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\IN>> | idir | Real |  |  | 1 | 0
x072_u002E_093 | Parametersatz 4->UMZ | 072.093 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung tIE>>> PS4 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real |  | x003_u002E_060 | E | 4 | 1 |  |  |  | Overcurrent\IN>>> | idir | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\IN>>> | idir | Real |  |  | 1 | 0
x072_u002E_094 | Parametersatz 4->UMZ | 072.094 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung tIE>>>> PS4 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real |  | x003_u002E_060 | E | 4 | 1 |  |  |  | Overcurrent\IN>>>> | idir | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\IN>>>> | idir | Real |  |  | 1 | 0
x075_u002E_000 | Parametersatz 4->AMZ | 075.000 | nein¦0;ja¦1 |  | Freigabe PS4 | Enum | Parameter__Funktionsparameter | 1;0 | Real |  | x056_u002E_009;x003_u002E_060 | E;E | 0;4 | 1 |  |  |  | Overcurrent\IDMT P | outserv | Real | 1 | 0 |  | x056_u002E_009;x003_u002E_060 |  |  | E;E | 0;4 | 3 | Overcurrent\IDMT P | outserv | Real | E | 0 |  | 0
[18 empty] | Overcurrent\IDMT neg | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\IDMT neg | outserv | Real | E | 0 |  | 0
[18 empty] | Overcurrent\IDMT N | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\IDMT N | outserv | Real |  |  | 1 | 0
x075_u002E_050 | Parametersatz 4->AMZ | 075.050 | 0.1-4:0.01;blockiert=4.02 | Inom | IB,L PS4 | Real | Parameter__Funktionsparameter |  |  |  | x075_u002E_000;x003_u002E_060 | E;E | 0;4 | 1 | 4 | SE | 4 | Overcurrent\IDMT P | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Overcurrent\IDMT P | outserv | Real | E | 1 | 0 | 4.02
[16 empty] | SE | 4 | Overcurrent\IDMT P | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\IDMT P | Ipset | Real |  |  | 1 | 0
[16 empty] | G | 4 | Overcurrent\IDMT P | outserv | Real | 0 | 1
[18 empty] | Overcurrent\IDMT KI P | outserv | Real | 0 | 1
x075_u002E_056 | Parametersatz 4->AMZ | 075.056 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Kennlinientyp L PS4 | Enum | Parameter__Funktionsparameter | Definite Time;IEC 255-3 Standard Inverse;IEC 255-3 Very Inverse;IEC 255-3 Extremly Inverse;IEC 255-3 Long-Time Inverse;IEEE C37.112 Moderately Inverse;IEEE C37.112 Very Inverse;IEEE C37.112 Extremely Inverse;ANSI Normally Inverse;ANSI Short-Time Inverse;ANSI Long-Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | [8 empty] | Overcurrent\IDMT P | pcharac |  |  |  |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\IDMT P | pcharac
x075_u002E_053 | Parametersatz 4->AMZ | 075.053 | 0.01-10:0.01 |  | Kennl.fakt. kt,L PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 |  |  | Overcurrent\IDMT P | Tpset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\IDMT P | Tpset | Real |  |  | 1 | 0
[18 empty] | Overcurrent\IDMT P | udeftmin | Real | 0 | 0
x075_u002E_059 | Parametersatz 4->AMZ | 075.059 | unverzögert¦0;verzögert gem. Kennl¦1 |  | Rückfallen L PS4 | Enum | Parameter__Funktionsparameter | 0;1 | Real | 3 | x003_u002E_060;x075_u002E_056 | E;SW | 4;IEEE | 0 |  |  |  | Overcurrent\IDMT P | resetdis | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\IDMT P | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x075_u002E_056 | E;SW | 4;ANSI |  |  |  |  | Overcurrent\IDMT P | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | 4 |  |  |  |  | Overcurrent\IDMT P | resetdis | Real | 0 | 0
x075_u002E_062 | Parametersatz 4->AMZ | 075.062 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung L PS4 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real |  | x003_u002E_060 | E | 4 |  |  |  |  | Overcurrent\IDMT P | idir | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\IDMT P | idir | Real |  |  | 1 | 0
x075_u002E_051 | Parametersatz 4->AMZ | 075.051 | 0.1-4:0.01;blockiert=4.02 | Inom | IB,gegen PS4 | Real | Parameter__Funktionsparameter |  |  |  | x075_u002E_000;x003_u002E_060 | E;E | 0;4 | 1 | 4 | SE | 4 | Overcurrent\IDMT neg | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 3 | Overcurrent\IDMT neg | outserv | Real | E | 1 | 0 | 4.02
[16 empty] | SE | 4 | Overcurrent\IDMT neg | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\IDMT neg | Ipset | Real | GE | 0.1 | 1 | 0
[16 empty] | G | 4 | Overcurrent\IDMT neg | outserv | Real | 0 | 1 | [13 empty] | 0.1
[18 empty] | Overcurrent\IDMT KI neg | outserv | Real | 0 | 1
x075_u002E_057 | Parametersatz 4->AMZ | 075.057 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Kennl.typ gegen PS4 | Enum | Parameter__Funktionsparameter | Definite Time;IEC 255-3 Standard Inverse;IEC 255-3 Very Inverse;IEC 255-3 Extremly Inverse;IEC 255-3 Long-Time Inverse;IEEE C37.112 Moderately Inverse;IEEE C37.112 Very Inverse;IEEE C37.112 Extremely Inverse;ANSI Normally Inverse;ANSI Short-Time Inverse;ANSI Long-Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | [8 empty] | Overcurrent\IDMT neg | pcharac |  |  |  |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\IDMT neg | pcharac
x075_u002E_054 | Parametersatz 4->AMZ | 075.054 | 0.01-10:0.01 |  | Kennl.f. kt,gegn PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 |  |  | Overcurrent\IDMT neg | Tpset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\IDMT neg | Tpset | Real |  |  | 1 | 0
[18 empty] | Overcurrent\IDMT neg | udeftmin | Real | 0 | 0
x075_u002E_060 | Parametersatz 4->AMZ | 075.060 | unverzögert¦0;verzögert gem. Kennl¦1 |  | Rückfallen gegen PS4 | Enum | Parameter__Funktionsparameter | 0;1 | Real | 3 | x003_u002E_060;x075_u002E_057 | E;SW | 4;IEEE | 0 |  |  |  | Overcurrent\IDMT neg | resetdis | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\IDMT neg | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x075_u002E_057 | E;SW | 4;ANSI |  |  |  |  | Overcurrent\IDMT neg | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | 4 |  |  |  |  | Overcurrent\IDMT neg | resetdis | Real | 0 | 0
x075_u002E_052 | Parametersatz 4->AMZ | 075.052 | 0.1-4:0.01;blockiert=4.02 | Inom | IB,E (gerechnet) PS4 | Real | Parameter__Funktionsparameter |  |  |  | x075_u002E_000;x003_u002E_060 | E;E | 0;4 | 1 | 4 | SE | 4 | Overcurrent\IDMT N | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 3 | Overcurrent\IDMT N | outserv | Real | E | 1 | 0 | 4.02
[16 empty] | SE | 4 | Overcurrent\IDMT N | outserv | Real | 0 | 0 | [7 empty] | Overcurrent\IDMT N | Ipset | Real | GE | 0.1 | 1 | 0
[16 empty] | G | 4 | Overcurrent\IDMT N | outserv | Real | 0 | 1 | [13 empty] | 0.1
[18 empty] | Overcurrent\IDMT KI N | outserv | Real | 0 | 1
x075_u002E_058 | Parametersatz 4->AMZ | 075.058 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Kennlinientyp E PS4 | Enum | Parameter__Funktionsparameter | Definite Time;IEC 255-3 Standard Inverse;IEC 255-3 Very Inverse;IEC 255-3 Extremly Inverse;IEC 255-3 Long-Time Inverse;IEEE C37.112 Moderately Inverse;IEEE C37.112 Very Inverse;IEEE C37.112 Extremely Inverse;ANSI Normally Inverse;ANSI Short-Time Inverse;ANSI Long-Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | [8 empty] | Overcurrent\IDMT N | pcharac |  |  |  |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\IDMT N | pcharac
x075_u002E_055 | Parametersatz 4->AMZ | 075.055 | 0.01-10:0.01 |  | Kennl.f. kt,E PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 |  |  | Overcurrent\IDMT N | Tpset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\IDMT N | Tpset | Real |  |  | 1 | 0
[18 empty] | Overcurrent\IDMT N | udeftmin | Real | 0 | 0
x075_u002E_061 | Parametersatz 4->AMZ | 075.061 | unverzögert¦0;verzögert gem. Kennl¦1 |  | Rückfallen E PS4 | Enum | Parameter__Funktionsparameter | 0;1 | Real | 3 | x003_u002E_060;x075_u002E_058 | E;SW | 4;IEEE | 0 |  |  |  | Overcurrent\IDMT N | resetdis | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\IDMT N | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x075_u002E_058 | E;SW | 4;ANSI |  |  |  |  | Overcurrent\IDMT N | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | 4 |  |  |  |  | Overcurrent\IDMT N | resetdis | Real | 0 | 0
x075_u002E_064 | Parametersatz 4->AMZ | 075.064 | vorwärts gerichtet¦0;rückwärts gerichtet¦1;ungerichtet¦2 |  | Richtung E PS4 | Enum | Parameter__Funktionsparameter | 1;2;0 | Real |  | x003_u002E_060 | E | 4 |  |  |  |  | Overcurrent\IDMT N | idir | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\IDMT N | idir | Real |  |  | 1 | 0
x079_u002E_000 | Parametersatz 4->U<> | 079.000 | nein¦0;ja¦1 |  | Freigabe PS4 | Enum | Parameter__Funktionsparameter | 1;0 | Real |  | x056_u002E_010;x003_u002E_060 | E;E | 0;4 | 1 |  |  |  | Voltage | outserv | Real | 1 | 0 |  | x056_u002E_010;x003_u002E_060 |  |  | E;E | 0;4 |  | Voltage | outserv | Real |  |  | 1 | 0
x079_u002E_001 | Parametersatz 4->U<> | 079.001 | Dreieck¦0;Stern¦1 |  | Betriebsart PS4 | Enum | Parameter__Funktionsparameter | 0;1 | Real |  | x079_u002E_000;x003_u002E_060 | E;E | 0;4 | 0 | 16 | E | 0 | Voltage\V< LE | outserv | Real | 0 | 1
[16 empty] | E | 0 | Voltage\V< LL | outserv | Real | 0 | 0
[16 empty] | E | 0 | Voltage\V<< LE | outserv | Real | 0 | 1
[16 empty] | E | 0 | Voltage\V<< LL | outserv | Real | 0 | 0
[16 empty] | E | 0 | Voltage\V> LE | outserv | Real | 0 | 1
[16 empty] | E | 0 | Voltage\V> LL | outserv | Real | 0 | 0
[16 empty] | E | 0 | Voltage\V>> LE | outserv | Real | 0 | 1
[16 empty] | E | 0 | Voltage\V>> LL | outserv | Real | 0 | 0
[16 empty] | E | 1 | Voltage\V< LE | outserv | Real | 0 | 0
[16 empty] | E | 1 | Voltage\V< LL | outserv | Real | 0 | 1
[16 empty] | E | 1 | Voltage\V<< LE | outserv | Real | 0 | 0
[16 empty] | E | 1 | Voltage\V<< LL | outserv | Real | 0 | 1
[16 empty] | E | 1 | Voltage\V> LE | outserv | Real | 0 | 0
[16 empty] | E | 1 | Voltage\V> LL | outserv | Real | 0 | 1
[16 empty] | E | 1 | Voltage\V>> LE | outserv | Real | 0 | 0
[16 empty] | E | 1 | Voltage\V>> LL | outserv | Real | 0 | 1
x079_u002E_003 | Parametersatz 4->U<> | 079.003 | 0.2-1.5:0.01;blockiert=1.52 | Unom(/©3) | U> PS4 | Real | Parameter__Funktionsparameter |  |  | 2 | x079_u002E_001;x003_u002E_060 | E;E | 0;4 | 1.1 | 3 | SE | 1.5 | Voltage\V> LL | Uset | Real | 1 | 0 | 2 | x079_u002E_001;x003_u002E_060 |  |  | E;E | 0;4 | 3 | Voltage\V> LL | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V> LL | outserv | Real | 0 | 0 | [7 empty] | Voltage\V> LL | Uset | Real | GE | 0.2 | 1 | 0
[16 empty] | G | 1.5 | Voltage\V> LL | outserv | Real | 0 | 1 | [13 empty] | 0.2
[11 empty] | x079_u002E_001;x003_u002E_060 | E;E | 1;4 |  | 3 | SE | 1.5 | Voltage\V> LE | Uset | Real | 1 | 0 |  | x079_u002E_001;x003_u002E_060 |  |  | E;E | 1;4 | 3 | Voltage\V> LE | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V> LE | outserv | Real | 0 | 0 | [7 empty] | Voltage\V> LE | Uset | Real | GE | 0.2 | 1 | 0
[16 empty] | G | 1.5 | Voltage\V> LE | outserv | Real | 0 | 1 | [13 empty] | 0.2
x079_u002E_004 | Parametersatz 4->U<> | 079.004 | 0.2-1.5:0.01;blockiert=1.52 | Unom(/©3) | U>> PS4 | Real | Parameter__Funktionsparameter |  |  | 2 | x079_u002E_001;x003_u002E_060 | E;E | 0;4 | 1.1 | 3 | SE | 1.5 | Voltage\V>> LL | Uset | Real | 1 | 0 | 2 | x079_u002E_001;x003_u002E_060 |  |  | E;E | 0;4 | 3 | Voltage\V>> LL | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V>> LL | outserv | Real | 0 | 0 | [7 empty] | Voltage\V>> LL | Uset | Real | GE | 0.2 | 1 | 0
[16 empty] | G | 1.5 | Voltage\V>> LL | outserv | Real | 0 | 1 | [13 empty] | 0.2
[11 empty] | x079_u002E_001;x003_u002E_060 | E;E | 1;4 |  | 3 | SE | 1.5 | Voltage\V>> LE | Uset | Real | 1 | 0 |  | x079_u002E_001;x003_u002E_060 |  |  | E;E | 1;4 | 3 | Voltage\V>> LE | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V>> LE | outserv | Real | 0 | 0 | [7 empty] | Voltage\V>> LE | Uset | Real | GE | 0.2 | 1 | 0
[16 empty] | G | 1.5 | Voltage\V>> LE | outserv | Real | 0 | 1 | [13 empty] | 0.2
x079_u002E_005 | Parametersatz 4->U<> | 079.005 | 0-100:0.01;blockiert=100.02 | s | tU> PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1 | 4 | SE | 100 | Voltage\V> LL | Tdel | Real | 1 | 0 | 2 | x079_u002E_001;x003_u002E_060 |  |  | E;E | 0;4 | 2 | Voltage\V> LL | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V> LL | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
[16 empty] | SE | 100 | Voltage\V> LE | Tdel | Real | 1 | 0 |  | x079_u002E_001;x003_u002E_060 |  |  | E;E | 1;4 | 2 | Voltage\V> LE | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V> LE | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x079_u002E_006 | Parametersatz 4->U<> | 079.006 | 0-100:0.01;blockiert=100.02 | s | tU>> PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1 | 4 | SE | 100 | Voltage\V>> LL | Tdel | Real | 1 | 0 |  | x079_u002E_001;x003_u002E_060 |  |  | E;E | 0;4 | 2 | Voltage\V>> LL | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V>> LL | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
[16 empty] | SE | 100 | Voltage\V>> LE | Tdel | Real | 1 | 0 |  | x079_u002E_001;x003_u002E_060 |  |  | E;E | 1;4 | 2 | Voltage\V>> LE | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V>> LE | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x079_u002E_007 | Parametersatz 4->U<> | 079.007 | 0.2-1.5:0.01;blockiert=1.52 | Unom(/©3) | U< PS4 | Real | Parameter__Funktionsparameter |  |  | 2 | x079_u002E_001;x003_u002E_060 | E;E | 0;4 | 0.8 | 3 | SE | 1.5 | Voltage\V< LL | Uset | Real | 1 | 0 | 2 | x079_u002E_001;x003_u002E_060 |  |  | E;E | 0;4 | 2 | Voltage\V< LL | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V< LL | outserv | Real | 0 | 0 | [7 empty] | Voltage\V< LL | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\V< LL | outserv | Real | 0 | 1 |  | x079_u002E_001;x003_u002E_060 |  |  | E;E | 1;4 | 2 | Voltage\V< LE | outserv | Real | E | 1 | 0 | 1.52
[11 empty] | x079_u002E_001;x003_u002E_060 | E;E | 1;4 | 0.8 |  | SE | 1.5 | Voltage\V< LE | Uset | Real | 1 | 0 | [7 empty] | Voltage\V< LE | Uset | Real |  |  | 1 | 0
[16 empty] | SE | 1.5 | Voltage\V< LE | outserv | Real | 0 | 0
[16 empty] | G | 1.5 | Voltage\V< LE | outserv | Real | 0 | 1
x079_u002E_008 | Parametersatz 4->U<> | 079.008 | 0.2-1.5:0.01;blockiert=1.52 | Unom(/©3) | U<< PS4 | Real | Parameter__Funktionsparameter |  |  | 2 | x079_u002E_001;x003_u002E_060 | E;E | 0;4 | 0.8 | 3 | SE | 1.5 | Voltage\V<< LL | Uset | Real | 1 | 0 | 2 | x079_u002E_001;x003_u002E_060 |  |  | E;E | 0;4 | 2 | Voltage\V<< LL | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V<< LL | outserv | Real | 0 | 0 | [7 empty] | Voltage\V<< LL | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\V<< LL | outserv | Real | 0 | 1 |  | x079_u002E_001;x003_u002E_060 |  |  | E;E | 1;4 | 2 | Voltage\V<< LE | outserv | Real | E | 1 | 0 | 1.52
[11 empty] | x079_u002E_001;x003_u002E_060 | E;E | 1;4 | 0.8 |  | SE | 1.5 | Voltage\V<< LE | Uset | Real | 1 | 0 | [7 empty] | Voltage\V<< LE | Uset | Real |  |  | 1 | 0
[16 empty] | SE | 1.5 | Voltage\V<< LE | outserv | Real | 0 | 0
[16 empty] | G | 1.5 | Voltage\V<< LE | outserv | Real | 0 | 1
x079_u002E_009 | Parametersatz 4->U<> | 079.009 | 0-100:0.01;blockiert=100.02 | s | tU< PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1 | 4 | SE | 100 | Voltage\V< LL | Tdel | Real | 1 | 0 |  | x079_u002E_001;x003_u002E_060 |  |  | E;E | 0;4 | 2 | Voltage\V< LL | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V< LL | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
[16 empty] | SE | 100 | Voltage\V< LE | Tdel | Real | 1 | 0 |  | x079_u002E_001;x003_u002E_060 |  |  | E;E | 1;4 | 2 | Voltage\V< LE | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V< LE | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x079_u002E_010 | Parametersatz 4->U<> | 079.010 | 0-100:0.01;blockiert=100.02 | s | tU<< PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1 | 4 | SE | 100 | Voltage\V<< LL | Tdel | Real | 1 | 0 |  | x079_u002E_001;x003_u002E_060 |  |  | E;E | 0;4 | 2 | Voltage\V<< LL | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V<< LL | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
[16 empty] | SE | 100 | Voltage\V<< LE | Tdel | Real | 1 | 0 |  | x079_u002E_001;x003_u002E_060 |  |  | E;E | 1;4 | 2 | Voltage\V<< LE | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V<< LE | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x079_u002E_015 | Parametersatz 4->U<> | 079.015 | 0.2-1.5:0.01;blockiert=1.52 | Unom/©3 | Umit> PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1.1 | 3 | SE | 1.5 | Voltage\Vpos> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 3 | Voltage\Vpos> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos> | Uset | Real | GE | 0.2 | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vpos> | outserv | Real | 0 | 1 | [13 empty] | 0.2
x079_u002E_016 | Parametersatz 4->U<> | 079.016 | 0.2-1.5:0.01;blockiert=1.52 | Unom/©3 | Umit>> PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1.1 | 3 | SE | 1.5 | Voltage\Vpos>> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 3 | Voltage\Vpos>> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos>> | Uset | Real | GE | 0.2 | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vpos>> | outserv | Real | 0 | 1 | [13 empty] | 0.2
x079_u002E_017 | Parametersatz 4->U<> | 079.017 | 0-100:0.01;blockiert=100.02 | s | tUmit> PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 | SE | 100 | Voltage\Vpos> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Voltage\Vpos> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vpos> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x079_u002E_018 | Parametersatz 4->U<> | 079.018 | 0-100:0.01;blockiert=100.02 | s | tUmit>> PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 | SE | 100 | Voltage\Vpos>> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Voltage\Vpos>> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vpos>> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x079_u002E_019 | Parametersatz 4->U<> | 079.019 | 0.2-1.5:0.01;blockiert=1.52 | Unom/©3 | Umit< PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 0.8 | 3 | SE | 1.5 | Voltage\Vpos< | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 3 | Voltage\Vpos< | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos< | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos< | Uset | Real | GE | 0.2 | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vpos< | outserv | Real | 0 | 1 | [13 empty] | 0.2
x079_u002E_020 | Parametersatz 4->U<> | 079.020 | 0.2-1.5:0.01;blockiert=1.52 | Unom/©3 | Umit<< PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 0.8 | 3 | SE | 1.5 | Voltage\Vpos<< | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 3 | Voltage\Vpos<< | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos<< | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos<< | Uset | Real | GE | 0.2 | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vpos<< | outserv | Real | 0 | 1 | [13 empty] | 0.2
x079_u002E_021 | Parametersatz 4->U<> | 079.021 | 0-100:0.01;blockiert=100.02 | s | tUmit< PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 | SE | 100 | Voltage\Vpos< | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Voltage\Vpos< | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vpos< | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x079_u002E_022 | Parametersatz 4->U<> | 079.022 | 0-100:0.01;blockiert=100.02 | s | tUmit<< PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 | SE | 100 | Voltage\Vpos<< | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Voltage\Vpos<< | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vpos<< | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x079_u002E_023 | Parametersatz 4->U<> | 079.023 | 0.2-1.5:0.01;blockiert=1.52 | Unom/©3 | Ugegen> PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1.52 | 3 | SE | 1.5 | Voltage\Vneg> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 3 | Voltage\Vneg> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vneg> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vneg> | Uset | Real | GE | 0.2 | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vneg> | outserv | Real | 0 | 1 | [13 empty] | 0.2
x079_u002E_024 | Parametersatz 4->U<> | 079.024 | 0.2-1.5:0.01;blockiert=1.52 | Unom/©3 | Ugegen>> PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1.52 | 3 | SE | 1.5 | Voltage\Vneg>> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 3 | Voltage\Vneg>> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vneg>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vneg>> | Uset | Real | GE | 0.2 | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vneg>> | outserv | Real | 0 | 1 | [13 empty] | 0.2
x079_u002E_025 | Parametersatz 4->U<> | 079.025 | 0-100:0.01;blockiert=100.02 | s | tUgegen> PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 | SE | 100 | Voltage\Vneg> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Voltage\Vneg> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vneg> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x079_u002E_026 | Parametersatz 4->U<> | 079.026 | 0-100:0.01;blockiert=100.02 | s | tUgegen>> PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 | SE | 100 | Voltage\Vneg>> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Voltage\Vneg>> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vneg>> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x079_u002E_011 | Parametersatz 4->U<> | 079.011 | 0.02-1:0.01;blockiert=1.02 | Unom(/©3) | UNE> PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1.02 | 3 | SE | 1 | Voltage\VNG> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Voltage\VNG> | outserv | Real | E | 1 | 0 | 1.02
[16 empty] | SE | 1 | Voltage\VNG> | outserv | Real | 0 | 0 | [7 empty] | Voltage\VNG> | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1 | Voltage\VNG> | outserv | Real | 0 | 1
x079_u002E_012 | Parametersatz 4->U<> | 079.012 | 0.02-1:0.01;blockiert=1.02 | Unom(/©3) | UNE>> PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1.02 | 3 | SE | 1 | Voltage\VNG>> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Voltage\VNG>> | outserv | Real | E | 1 | 0 | 1.02
[16 empty] | SE | 1 | Voltage\VNG>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\VNG>> | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1 | Voltage\VNG>> | outserv | Real | 0 | 1
x079_u002E_013 | Parametersatz 4->U<> | 079.013 | 0-100:0.01;blockiert=100.02 | s | tUNE> PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 | SE | 100 | Voltage\VNG> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Voltage\VNG> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\VNG> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x079_u002E_014 | Parametersatz 4->U<> | 079.014 | 0-100:0.01;blockiert=100.02 | s | tUNE>> PS4 | Real | Parameter__Funktionsparameter |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 | SE | 100 | Voltage\VNG>> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Voltage\VNG>> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\VNG>> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x018_u002E_199 | Parametersatz 4->f<> | 018.199 | nein¦0;ja¦1 |  | Freigabe PS4 | Enum | Parameter__Funktionsparameter | 1;0 | Real |  | x056_u002E_033;x003_u002E_060 | E;E | 0;4 | 1 |  |  |  | Frequency | outserv | Real | 1 | 0 |  | x056_u002E_033;x003_u002E_060 |  |  | E;E | 0;4 |  | Frequency | outserv | Real |  |  | 1 | 0
x018_u002E_123 | Parametersatz 4->f<> | 018.123 | f¦0;f mit df/dt¦1;f m. Delta f/Delta t¦2 |  | Betriebsart f1 PS4 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 4 | 0 |  | NE | 0 | Frequency\f1 | outserv | Real | 0 | 1
x018_u002E_103 | Parametersatz 4->f<> | 018.103 | 40-70:0.01;blockiert=70.02 | Hz | f1 PS4 | Real | Parameter__Funktionsparameter |  |  |  | x018_u002E_123;x003_u002E_060 | E;E | 0;4 | 49.8 | 3 | SE | 70 | Frequency\f1 | Fset | Real | 1 | 0 |  | x018_u002E_123;x003_u002E_060 |  |  | E;E | 0;4 | 2 | Frequency\f1 | outserv | Real | E | 1 | 0 | 70.02
[16 empty] | SE | 70 | Frequency\f1 | outserv | Real | 0 | 0 | [7 empty] | Frequency\f1 | Uset | Real |  |  | 1 | 0
[16 empty] | G | 70 | Frequency\f1 | outserv | Real | 0 | 1
x018_u002E_107 | Parametersatz 4->f<> | 018.107 | 0-10:0.001;blockiert=10.002 | s | tf1 PS4 | Real | Parameter__Funktionsparameter |  |  |  | x018_u002E_123;x003_u002E_060 | E;E | 0;4 | 0 | 2 | SE | 10 | Frequency\f1 | Tdel | Real | 1 | 0 |  | x018_u002E_123;x003_u002E_060 |  |  | E;E | 0;4 | 2 | Frequency\f1 | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Frequency\f1 | Tdel | Real | 0 | 9999999 | [13 empty] | 10.002
x018_u002E_147 | Parametersatz 4->f<> | 018.147 | f¦0;f mit df/dt¦1;f m. Delta f/Delta t¦2 |  | Betriebsart f2 PS4 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 4 | 0 |  | NE | 0 | Frequency\f2 | outserv | Real | 0 | 1
x018_u002E_127 | Parametersatz 4->f<> | 018.127 | 40-70:0.01;blockiert=70.02 | Hz | f2 PS4 | Real | Parameter__Funktionsparameter |  |  |  | x018_u002E_147;x003_u002E_060 | E;E | 0;4 | 49.8 | 3 | SE | 70 | Frequency\f2 | Fset | Real | 1 | 0 |  | x018_u002E_147;x003_u002E_060 |  |  | E;E | 0;4 | 2 | Frequency\f2 | outserv | Real | E | 1 | 0 | 70.02
[16 empty] | SE | 70 | Frequency\f2 | outserv | Real | 0 | 0 | [7 empty] | Frequency\f2 | Uset | Real |  |  | 1 | 0
[16 empty] | G | 70 | Frequency\f2 | outserv | Real | 0 | 1
x018_u002E_131 | Parametersatz 4->f<> | 018.131 | 0-10:0.001;blockiert=10.002 | s | tf2 PS4 | Real | Parameter__Funktionsparameter |  |  |  | x018_u002E_147;x003_u002E_060 | E;E | 0;4 | 0 | 2 | SE | 10 | Frequency\f2 | Tdel | Real | 1 | 0 |  | x018_u002E_147;x003_u002E_060 |  |  | E;E | 0;4 | 2 | Frequency\f2 | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Frequency\f2 | Tdel | Real | 0 | 9999999 | [13 empty] | 10.002
x018_u002E_171 | Parametersatz 4->f<> | 018.171 | f¦0;f mit df/dt¦1;f m. Delta f/Delta t¦2 |  | Betriebsart f3 PS4 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 4 | 0 |  | NE | 0 | Frequency\f3 | outserv | Real | 0 | 1
x018_u002E_151 | Parametersatz 4->f<> | 018.151 | 40-70:0.01;blockiert=70.02 | Hz | f3 PS4 | Real | Parameter__Funktionsparameter |  |  |  | x018_u002E_171;x003_u002E_060 | E;E | 0;4 | 49.8 | 3 | SE | 70 | Frequency\f3 | Fset | Real | 1 | 0 |  | x018_u002E_171;x003_u002E_060 |  |  | E;E | 0;4 | 2 | Frequency\f3 | outserv | Real | E | 1 | 0 | 70.02
[16 empty] | SE | 70 | Frequency\f3 | outserv | Real | 0 | 0 | [7 empty] | Frequency\f3 | Uset | Real |  |  | 1 | 0
[16 empty] | G | 70 | Frequency\f3 | outserv | Real | 0 | 1
x018_u002E_155 | Parametersatz 4->f<> | 018.155 | 0-10:0.001;blockiert=10.002 | s | tf3 PS4 | Real | Parameter__Funktionsparameter |  |  |  | x018_u002E_171;x003_u002E_060 | E;E | 0;4 | 0 | 2 | SE | 10 | Frequency\f3 | Tdel | Real | 1 | 0 |  | x018_u002E_171;x003_u002E_060 |  |  | E;E | 0;4 | 2 | Frequency\f3 | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Frequency\f3 | Tdel | Real | 0 | 9999999 | [13 empty] | 10.002
x018_u002E_195 | Parametersatz 4->f<> | 018.195 | f¦0;f mit df/dt¦1;f m. Delta f/Delta t¦2 |  | Betriebsart f4 PS4 | Enum | Parameter__Funktionsparameter | 0;1;2 | Real |  | x003_u002E_060 | E | 4 | 0 |  | NE | 0 | Frequency\f4 | outserv | Real | 0 | 1
x018_u002E_175 | Parametersatz 4->f<> | 018.175 | 40-70:0.01;blockiert=70.02 | Hz | f4 PS4 | Real | Parameter__Funktionsparameter |  |  |  | x018_u002E_195;x003_u002E_060 | E;E | 0;4 | 49.8 | 3 | SE | 70 | Frequency\f4 | Fset | Real | 1 | 0 |  | x018_u002E_195;x003_u002E_060 |  |  | E;E | 0;4 | 2 | Frequency\f4 | outserv | Real | E | 1 | 0 | 70.02
[16 empty] | SE | 70 | Frequency\f4 | outserv | Real | 0 | 0 | [7 empty] | Frequency\f4 | Uset | Real |  |  | 1 | 0
[16 empty] | G | 70 | Frequency\f4 | outserv | Real | 0 | 1
x018_u002E_179 | Parametersatz 4->f<> | 018.179 | 0-10:0.001;blockiert=10.002 | s | tf4 PS4 | Real | Parameter__Funktionsparameter |  |  |  | x018_u002E_195;x003_u002E_060 | E;E | 0;4 | 0 | 2 | SE | 10 | Frequency\f4 | Tdel | Real | 1 | 0 |  | x018_u002E_195;x003_u002E_060 |  |  | E;E | 0;4 | 2 | Frequency\f4 | Tdel | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Frequency\f4 | Tdel | Real | 0 | 9999999 | [13 empty] | 10.002
_END_