## Mapping
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37
StationWare | [6 empty] | Common |  |  | Import | [12 empty] | Export
[8 empty] | Enumeration |  | Pre-Condition |  |  |  |  | Instruction | [7 empty] | Pre-Condition | [5 empty] | Instruction
Key | Chapter | Display name | Range | Unit | Description | Type | Group | Mapping | Type |  | Setting | Operator | Value | Default |  | Operator | Value | Target | Parameter | Type | Scale | Offset |  | Source | Parameter | Type | Operator | Value |  | Source | Parameter | Type | Operator | Value | Scale | Offset
x056_u002E_014 | DIST | 056.014 | Without¦0;With¦1 |  | Function group DIST | Enum | Parameters__Config__parameters | 1;0 | Real |  |  |  |  | 1 | 2 | E | 1 | Distance Circular | outserv | Real | 0 | 1
[16 empty] | E | 1 | Distance Polygonal | outserv | Real | 0 | 1
x056_u002E_004 | PSIG | 056.004 | Without¦0;With¦1 |  | Function group PSIG | Enum | Parameters__Config__parameters | 1;0 | Real |  |  |  |  | 1 | 4 | E | 1 | Distance Circular\PSIG Receive | outserv | Real | 0 | 1
[16 empty] | E | 1 | Distance Circular\PSIG Send | outserv | Real | 0 | 1
[16 empty] | E | 1 | Distance Polygonal\PSIG Receive | outserv | Real | 0 | 1
[16 empty] | E | 1 | Distance Polygonal\PSIG Send | outserv | Real | 0 | 1
x056_u002E_008 | DTOC | 056.008 | Without¦0;With¦1 |  | Function group DTOC | Enum | Parameters__Config__parameters | 1;0 | Real |  |  |  |  | 1 | 12 | E | 1 | Overcurrent\I> | outserv | Real | 0 | 1
[16 empty] | E | 1 | Overcurrent\I>> | outserv | Real | 0 | 1
[16 empty] | E | 1 | Overcurrent\I>>> | outserv | Real | 0 | 1
[16 empty] | E | 1 | Overcurrent\I>>>> | outserv | Real | 0 | 1
[16 empty] | E | 1 | Overcurrent\IN> | outserv | Real | 0 | 1
[16 empty] | E | 1 | Overcurrent\IN>> | outserv | Real | 0 | 1
[16 empty] | E | 1 | Overcurrent\IN>>> | outserv | Real | 0 | 1
[16 empty] | E | 1 | Overcurrent\IN>>>> | outserv | Real | 0 | 1
[16 empty] | E | 1 | Overcurrent\Ineg> | outserv | Real | 0 | 1
[16 empty] | E | 1 | Overcurrent\Ineg>> | outserv | Real | 0 | 1
[16 empty] | E | 1 | Overcurrent\Ineg>>> | outserv | Real | 0 | 1
[16 empty] | E | 1 | Overcurrent\Ineg>>>> | outserv | Real | 0 | 1
x056_u002E_009 | IDMT | 056.009 | Without¦0;With¦1 |  | Function group IDMT | Enum | Parameters__Config__parameters | 1;0 | Real |  |  |  |  | 1 | 3 | E | 1 | Overcurrent\IDMT P | outserv | Real | 0 | 1
[16 empty] | E | 1 | Overcurrent\IDMT N | outserv | Real | 0 | 1
[16 empty] | E | 1 | Overcurrent\IDMT neg | outserv | Real | 0 | 1
x056_u002E_010 | V<> | 056.010 | Without¦0;With¦1 |  | Function group V<> | Enum | Parameters__Config__parameters | 1;0 | Real |  |  |  |  | 1 |  | E | 1 | Voltage | outserv | Real | 0 | 1
x010_u002E_009 | Global->MAIN | 010.009 | 50-130:1 | V | Vnom V.T. sec. | Real | Parameters__Function_parameters | [6 empty] | 100 | 3 |  |  | Measurement | Unom | Real | 1 | 0 | [7 empty] | Measurement | Unom | Real |  |  | 1 | 0
[18 empty] | Measurement Delta | Unom | Real | 1 | 0
[18 empty] | Measurement Sequence | Unom | Real | 1 | 0
x010_u002E_048 | Main functions->MAIN | 010.048 | Low-imped. grounding¦0;Isol./res.w.start.PG¦1;Isol./res.w/o st. PG¦2;Short-durat. ground.¦3 |  | Neutral-point treat. | Enum | Parameters__Function_parameters | 0;1;2;3;4 | Real |  |  |  |  | 0 | 4 | E | 0 | Distance Circular\Starting | isysstar | Real | 0 | 0 | 2 | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Starting | isysstar | Real | E | 0 | 1 | 0
[16 empty] | E | 0 | Distance Polygonal\Starting | isysstar | Real | 0 | 0 |  | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Starting | isysstar | Real | E | 0 | 1 | 0
[16 empty] | NE | 0 | Distance Circular\Starting | isysstar | Real | 0 | 1
[16 empty] | NE | 0 | Distance Polygonal\Starting | isysstar | Real | 0 | 1
x010_u002E_040 | Main functions->MAIN | 010.040 | Ground¦0;P or G =f(Imed,Imax)¦1 |  | Transfer for 1p | Enum | Parameters__Function_parameters | 0;1 | Real |  |  |  |  | 0 | 2 |  |  | Distance Circular\Starting | itransf1p | Real | 1 | 0 | 2 | Distance Circular | outserv | Real | E | 0 |  | Distance Circular\Starting | itransf1p | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | itransf1p | Real | 1 | 0 |  | Distance Polygonal | outserv | Real | E | 0 |  | Distance Polygonal\Starting | itransf1p | Real |  |  | 1 | 0
x031_u002E_073 | Main functions->DIST | 031.073 | No¦0;Yes¦1 |  | General enable USER | Enum | Parameters__Function_parameters | 1;0 | Real |  | x056_u002E_014 | E | 0 | 0 | 2 | E | 1 | Distance Circular | outserv | Real | 0 | 1 |  | x056_u002E_014 |  |  | E | 0 | 2 | Distance Circular\Starting | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 1 | Distance Polygonal | outserv | Real | 0 | 1 | [7 empty] | Distance Polygonal\Starting | outserv | Real |  |  | 1 | 0
x003_u002E_060 | Global->PSS | 003.060 | Parameter subset 1¦0;Parameter subset 2¦1;Parameter subset 3¦2;Parameter subset 4¦3 |  | Param.subs.sel. USER | Enum | Parameters__Function_parameters | 1;2;3;4 | Real |  |  |  |  | 1
x010_u002E_054 | Parameter subset 1->DIST | 010.054 | 0.1-20:0.01 | Inom | I>> PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 |  |  | Distance Circular\Starting | IMM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Circular\Starting | IMM | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | IMM | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Polygonal\Starting | IMM | Real |  |  | 1 | 0
x010_u002E_068 | Parameter subset 1->DIST | 010.068 | 0.1-1:0.01 | Inom | I> (Ibl) high r. PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 0.2 | 2 |  |  | Distance Circular\Starting | IM1 | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Circular\Starting | IM1 | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | IM1 | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Polygonal\Starting | IM1 | Real |  |  | 1 | 0
x010_u002E_067 | Parameter subset 1->DIST | 010.067 | W/o V< starting¦0;With V< start. PG¦1;With V< start.PG,PP¦2 |  | Operat. mode V< PS1 | Enum | Parameters__Function_parameters | 0;1;2 | Real |  | x003_u002E_060 | E | 1 | 2 | 8 | E | 0 | Distance Circular\Starting | iopt_u | Real | 0 | 0 | 4 | Distance Circular;Distance Circular\Starting;x003_u002E_060 | outserv;iopt_u | Real | E;E;E | 0;0;1 | [7 empty] | 0
[16 empty] | E | 0 | Distance Polygonal\Starting | iopt_u | Real | 0 | 0 |  | Distance Circular;Distance Circular\Starting;x003_u002E_060 | outserv;iopt_u | Real | E;E;E | 0;1;1 | 2 | Distance Circular\Starting | iVOpMode | Real | 0 | 0 | 0 | 1
[16 empty] | NE | 0 | Distance Circular\Starting | iopt_u | Real | 0 | 1 | [7 empty] | Distance Circular\Starting | iVOpMode | Real | 0 | 1 | 0 | 2
[16 empty] | NE | 0 | Distance Polygonal\Starting | iopt_u | Real | 0 | 1 |  | Distance Polygonal;Distance Polygonal\Starting;x003_u002E_060 | outserv;iopt_u | Real | E;E;E | 0;0;1 | [7 empty] | 0
[16 empty] | E | 1 | Distance Circular\Starting | iVOpMode | Real | 0 | 0 |  | Distance Polygonal;Distance Polygonal\Starting;x003_u002E_060 | outserv;iopt_u | Real | E;E;E | 0;1;1 | 2 | Distance Polygonal\Starting | iVOpMode | Real | 0 | 0 | 0 | 1
[16 empty] | E | 1 | Distance Polygonal\Starting | iVOpMode | Real | 0 | 0 | [7 empty] | Distance Polygonal\Starting | iVOpMode | Real | 0 | 1 | 0 | 2
[16 empty] | E | 2 | Distance Circular\Starting | iVOpMode | Real | 0 | 1
[16 empty] | E | 2 | Distance Polygonal\Starting | iVOpMode | Real | 0 | 1
x010_u002E_069 | Parameter subset 1->DIST | 010.069 | 0.1-0.9:0.01 | Vnom(/©3) | V< PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 0.7 | 2 |  |  | Distance Circular\Starting | Um | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Circular\Starting | Um | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | Um | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Polygonal\Starting | Um | Real |  |  | 1 | 0
x010_u002E_066 | Parameter subset 1->DIST | 010.066 | W/o Z< starting¦0;With Z< starting P-G¦1;With Z< start.PG,PP¦2 |  | Operat. mode Z< PS1 | Enum | Parameters__Function_parameters | 0;1;2 | Real |  | x003_u002E_060 | E | 1 | 2 | 8 | E | 0 | Distance Circular\Starting | iopt_z | Real | 0 | 0 | 4 | Distance Circular;Distance Circular\Starting;x003_u002E_060 | outserv;iopt_z | Real | E;E;E | 0;0;1 | [7 empty] | 0
[16 empty] | E | 0 | Distance Polygonal\Starting | iopt_z | Real | 0 | 0 |  | Distance Circular;Distance Circular\Starting;x003_u002E_060 | outserv;iopt_z | Real | E;E;E | 0;1;1 | 2 | Distance Circular\Starting | iZOpMode | Real | 0 | 0 | 0 | 1
[16 empty] | NE | 0 | Distance Circular\Starting | iopt_z | Real | 0 | 1 | [7 empty] | Distance Circular\Starting | iZOpMode | Real | 0 | 1 | 0 | 2
[16 empty] | NE | 0 | Distance Polygonal\Starting | iopt_z | Real | 0 | 1 |  | Distance Polygonal;Distance Polygonal\Starting;x003_u002E_060 | outserv;iopt_z | Real | E;E;E | 0;0;1 | [7 empty] | 0
[16 empty] | E | 1 | Distance Circular\Starting | iZOpMode | Real | 0 | 0 |  | Distance Polygonal;Distance Polygonal\Starting;x003_u002E_060 | outserv;iopt_z | Real | E;E;E | 0;1;1 | 2 | Distance Polygonal\Starting | iZOpMode | Real | 0 | 0 | 0 | 1
[16 empty] | E | 1 | Distance Polygonal\Starting | iZOpMode | Real | 0 | 0 | [7 empty] | Distance Polygonal\Starting | iZOpMode | Real | 0 | 1 | 0 | 2
[16 empty] | E | 2 | Distance Circular\Starting | iZOpMode | Real | 0 | 1
[16 empty] | E | 2 | Distance Polygonal\Starting | iZOpMode | Real | 0 | 1
x010_u002E_050 | Parameter subset 1->DIST | 010.050 | 0.1-300:0.01 | — | Xfw PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 10 | 2 |  |  | Distance Circular\Starting | Xfw | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Circular\Starting | Xfw | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | Xfw | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Polygonal\Starting | Xfw | Real |  |  | 1 | 0
x010_u002E_051 | Parameter subset 1->DIST | 010.051 | 0.1-300:0.01 | — | Rfw,PG PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 10 | 2 |  |  | Distance Circular\Starting | RfPG | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Circular\Starting | RfPG | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | RfPG | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Polygonal\Starting | RfPG | Real |  |  | 1 | 0
x010_u002E_052 | Parameter subset 1->DIST | 010.052 | 0.1-300:0.01 | — | Rfw,PP PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 10 | 2 |  |  | Distance Circular\Starting | RfPP | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Circular\Starting | RfPP | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | RfPP | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Polygonal\Starting | RfPP | Real |  |  | 1 | 0
x010_u002E_063 | Parameter subset 1->DIST | 010.063 | 15-65:1 | ° | ß PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 30 | 2 |  |  | Distance Circular\Starting | Beta | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Circular\Starting | Beta | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | Beta | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Polygonal\Starting | Beta | Real |  |  | 1 | 0
x010_u002E_101 | Parameter subset 1->DIST | 010.101 | 0-300:0.01 | — | Zfw,PG PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 10 | 2 |  |  | Distance Circular\Starting | ZfPG | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Circular\Starting | ZfPG | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | ZfPG | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Polygonal\Starting | ZfPG | Real |  |  | 1 | 0
x010_u002E_105 | Parameter subset 1->DIST | 010.105 | 0-300:0.01 | — | Zfw,PP PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 10 | 2 |  |  | Distance Circular\Starting | ZfPP | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Circular\Starting | ZfPP | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | ZfPP | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Polygonal\Starting | ZfPP | Real |  |  | 1 | 0
x010_u002E_053 | Parameter subset 1->DIST | 010.053 | 0.1-4:0.01 |  | Zbw/Zfw PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 0.5 | 2 |  |  | Distance Circular\Starting | ZbwZfw | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Circular\Starting | ZbwZfw | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | ZbwZfw | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Polygonal\Starting | ZbwZfw | Real |  |  | 1 | 0
x010_u002E_055 | Parameter subset 1->DIST | 010.055 | 0.1-2:0.01 | Inom | IN> high range PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 0.2 | 2 |  |  | Distance Circular\Starting | INM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Circular\Starting | INM | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | INM | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Polygonal\Starting | INM | Real |  |  | 1 | 0
x010_u002E_057 | Parameter subset 1->DIST | 010.057 | 0-0.5:0.001 | s | tIN> PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 0.1 | 2 |  |  | Distance Circular\Starting | tINM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Circular\Starting | tINM | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | tINM | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Polygonal\Starting | tINM | Real |  |  | 1 | 0
x010_u002E_056 | Parameter subset 1->DIST | 010.056 | 0.02-1:0.01 | Vnom | VNG> PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 0.1 | 2 |  |  | Distance Circular\Starting | VNGM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Circular\Starting | VNGM | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | VNGM | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Polygonal\Starting | VNGM | Real |  |  | 1 | 0
x010_u002E_062 | Parameter subset 1->DIST | 010.062 | 0.2-1:0.01 | Vnom | VNG>> PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 0.5 | 2 |  |  | Distance Circular\Starting | VNGMM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Circular\Starting | VNGMM | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | VNGMM | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Polygonal\Starting | VNGMM | Real |  |  | 1 | 0
x010_u002E_061 | Parameter subset 1->DIST | 010.061 | 0-60:0.001 | s | tVNG>> PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 |  |  | Distance Circular\Starting | tVNGMM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Circular\Starting | tVNGMM | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | tVNGMM | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Polygonal\Starting | tVNGMM | Real |  |  | 1 | 0
x012_u002E_037 | Parameter subset 1->DIST | 012.037 | 0-8:0.01 |  | Abs. value kG PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 |  |  | Distance Circular\Polarisation | k0 | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Circular\Polarisation | k0 | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Polarisation | k0 | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Polygonal\Polarisation | k0 | Real |  |  | 1 | 0
x012_u002E_036 | Parameter subset 1->DIST | 012.036 | -180-180:1 | ° | Angle kG PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 0 | 2 |  |  | Distance Circular\Polarisation | phik0 | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Circular\Polarisation | phik0 | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Polarisation | phik0 | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;1 |  | Distance Polygonal\Polarisation | phik0 | Real |  |  | 1 | 0
x012_u002E_040 | Parameter subset 1->DIST | 012.040 | Circle¦0;Polygon¦1 |  | Characteristic PS1 | Enum | Parameters__Function_parameters | 0;1 | Real |  | x056_u002E_014;x031_u002E_073;x003_u002E_060 | E;E;E | 0;0;1 | 1 | 4 | E | 0 | Distance Circular | outserv | Real | 0 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Distance Circular | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 0 | Distance Polygonal | outserv | Real | 0 | 1 | [13 empty] | 1
[16 empty] | E | 1 | Distance Circular | outserv | Real | 0 | 1
[16 empty] | E | 1 | Distance Polygonal | outserv | Real | 0 | 0
x012_u002E_001 | Parameter subset 1->DIST | 012.001 | 0.1-200:0.01 | — | X1 (polygon) PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 10 |  |  |  | Distance Polygonal\Z1 | Xmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\Z1 | Xmax | Real |  |  | 1 | 0
x012_u002E_002 | Parameter subset 1->DIST | 012.002 | 0.1-200:0.01 | — | X2 (polygon) PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 20 |  |  |  | Distance Polygonal\Z2 | Xmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\Z2 | Xmax | Real |  |  | 1 | 0
x012_u002E_003 | Parameter subset 1->DIST | 012.003 | 0.1-200:0.01 | — | X3 (polygon) PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 30 |  |  |  | Distance Polygonal\Z3 | Xmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\Z3 | Xmax | Real |  |  | 1 | 0
x012_u002E_004 | Parameter subset 1->DIST | 012.004 | 0.1-200:0.01 | — | X4 (polygon) PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 40 |  |  |  | Distance Polygonal\Z4 | Xmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\Z4 | Xmax | Real |  |  | 1 | 0
x012_u002E_005 | Parameter subset 1->DIST | 012.005 | 0.1-200:0.01 | — | R1,PG (polygon) PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 10 |  |  |  | Distance Polygonal\Z1 | REmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\Z1 | REmax | Real |  |  | 1 | 0
x012_u002E_006 | Parameter subset 1->DIST | 012.006 | 0.1-200:0.01 | — | R1,PP (polygon) PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 10 |  |  |  | Distance Polygonal\Z1 | Rmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\Z1 | Rmax | Real |  |  | 1 | 0
x012_u002E_007 | Parameter subset 1->DIST | 012.007 | 0.1-200:0.01 | — | R2,PG (polygon) PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 20 |  |  |  | Distance Polygonal\Z2 | REmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\Z2 | REmax | Real |  |  | 1 | 0
x012_u002E_008 | Parameter subset 1->DIST | 012.008 | 0.1-200:0.01 | — | R2,PP (polygon) PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 20 |  |  |  | Distance Polygonal\Z2 | Rmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\Z2 | Rmax | Real |  |  | 1 | 0
x012_u002E_009 | Parameter subset 1->DIST | 012.009 | 0.1-200:0.01 | — | R3,PG (polygon) PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 30 |  |  |  | Distance Polygonal\Z3 | REmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\Z3 | REmax | Real |  |  | 1 | 0
x012_u002E_010 | Parameter subset 1->DIST | 012.010 | 0.1-200:0.01 | — | R3,PP (polygon) PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 30 |  |  |  | Distance Polygonal\Z3 | Rmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\Z3 | Rmax | Real |  |  | 1 | 0
x012_u002E_011 | Parameter subset 1->DIST | 012.011 | 0.1-200:0.01 | — | R4,PG (polygon) PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 40 |  |  |  | Distance Polygonal\Z4 | REmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\Z4 | REmax | Real |  |  | 1 | 0
x012_u002E_012 | Parameter subset 1->DIST | 012.012 | 0.1-200:0.01 | — | R4,PP (polygon) PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 40 |  |  |  | Distance Polygonal\Z4 | Rmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\Z4 | Rmax | Real |  |  | 1 | 0
x012_u002E_013 | Parameter subset 1->DIST | 012.013 | 40-90:1 | ° | €1 (polygon) PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 75 |  |  |  | Distance Polygonal\Z1 | phi | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\Z1 | phi | Real |  |  | 1 | 0
x012_u002E_014 | Parameter subset 1->DIST | 012.014 | 40-90:1 | ° | €2 (polygon) PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 75 |  |  |  | Distance Polygonal\Z2 | phi | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\Z2 | phi | Real |  |  | 1 | 0
x012_u002E_015 | Parameter subset 1->DIST | 012.015 | 40-90:1 | ° | €3 (polygon) PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 75 |  |  |  | Distance Polygonal\Z3 | phi | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\Z3 | phi | Real |  |  | 1 | 0
x012_u002E_016 | Parameter subset 1->DIST | 012.016 | 40-90:1 | ° | €4 (polygon) PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 75 |  |  |  | Distance Polygonal\Z4 | phi | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\Z4 | phi | Real |  |  | 1 | 0
x072_u002E_086 | Parameter subset 1->DIST | 072.086 | -20-20:1 | ° | ‹1 (polygon) PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 0 |  |  |  | Distance Polygonal\Z1 | beta | Real | -1 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\Z1 | beta | Real |  |  | -1 | 0
x072_u002E_087 | Parameter subset 1->DIST | 072.087 | -20-20:1 | ° | ‹2 (polygon) PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 0 |  |  |  | Distance Polygonal\Z2 | beta | Real | -1 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\Z2 | beta | Real |  |  | -1 | 0
x072_u002E_088 | Parameter subset 1->DIST | 072.088 | -20-20:1 | ° | ‹3 (polygon) PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 0 |  |  |  | Distance Polygonal\Z3 | beta | Real | -1 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\Z3 | beta | Real |  |  | -1 | 0
x072_u002E_089 | Parameter subset 1->DIST | 072.089 | -20-20:1 | ° | ‹4 (polygon) PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 0 |  |  |  | Distance Polygonal\Z4 | beta | Real | -1 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\Z4 | beta | Real |  |  | -1 | 0
x012_u002E_042 | Parameter subset 1->DIST | 012.042 | 0.05-200:0.01 | — | Z1 (circle) PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 10 |  |  |  | Distance Circular\Z1 | Zm | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Circular\Z1 | Zm | Real |  |  | 1 | 0
x012_u002E_043 | Parameter subset 1->DIST | 012.043 | 0.05-200:0.01 | — | Z2 (circle) PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 20 |  |  |  | Distance Circular\Z2 | Zm | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Circular\Z2 | Zm | Real |  |  | 1 | 0
x012_u002E_044 | Parameter subset 1->DIST | 012.044 | 0.05-200:0.01 | — | Z3 (circle) PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 30 |  |  |  | Distance Circular\Z3 | Zm | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Circular\Z3 | Zm | Real |  |  | 1 | 0
x012_u002E_045 | Parameter subset 1->DIST | 012.045 | 0.05-200:0.01 | — | Z4 (circle) PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 40 |  |  |  | Distance Circular\Z4 | Zm | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Circular\Z4 | Zm | Real |  |  | 1 | 0
x072_u002E_090 | Parameter subset 1->DIST | 072.090 | 10-90:1 | ° | €1 (circle) PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 75 | 2 |  |  | Distance Circular\Z1 | arcalpha | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Circular\Z1 | arcalpha | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z1E | arcalpha | Real | 1 | 0
x072_u002E_095 | Parameter subset 1->DIST | 072.095 | 10-90:1 | ° | €2 (circle) PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 75 |  |  |  | Distance Circular\Z2 | arcalpha | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Circular\Z2 | arcalpha | Real |  |  | 1 | 0
x072_u002E_096 | Parameter subset 1->DIST | 072.096 | 10-90:1 | ° | €3 (circle) PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 75 |  |  |  | Distance Circular\Z3 | arcalpha | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Circular\Z3 | arcalpha | Real |  |  | 1 | 0
x072_u002E_099 | Parameter subset 1->DIST | 072.099 | 10-90:1 | ° | €4 (circle) PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 75 |  |  |  | Distance Circular\Z4 | arcalpha | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Circular\Z4 | arcalpha | Real |  |  | 1 | 0
x012_u002E_038 | Parameter subset 1->DIST | 012.038 | No¦0;Yes¦1 |  | Arc comp. circle PS1 | Enum | Parameters__Function_parameters | 0;1 | Real |  | x003_u002E_060 | E | 1 | 0 | 5 |  |  | Distance Circular\Z1 | arcen | Real | 1 | 0 | 4 | Distance Circular;Distance Circular\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Circular\Z1 | arcen | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z1E | arcen | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Circular\Z2 | arcen | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z2 | arcen | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Circular\Z3 | arcen | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z3 | arcen | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Circular\Z4 | arcen | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z4 | arcen | Real | 1 | 0
x012_u002E_023 | Parameter subset 1->DIST | 012.023 | Forward directional¦0;Backward directional¦1;Non-directional¦2 |  | Direction N1 PS1 | Enum | Parameters__Function_parameters | 0;1;2 | Real |  | x003_u002E_060 | E | 1 | 0 | 4 | NE | 2 | Distance Circular\Z1 | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Circular\Z1 | idir | Real |  |  | 1 | 0
[16 empty] | NE | 2 | Distance Circular\Z1E | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\Z1 | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z1 | idir | Real | 1 | 0
[18 empty] | Distance Polygonal\Z1E | idir | Real | 1 | 0
x012_u002E_024 | Parameter subset 1->DIST | 012.024 | Forward directional¦0;Backward directional¦1;Non-directional¦2 |  | Direction N2 PS1 | Enum | Parameters__Function_parameters | 0;1;2 | Real |  | x003_u002E_060 | E | 1 | 0 |  | NE | 2 | Distance Circular\Z2 | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Circular\Z2 | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z2 | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\Z2 | idir | Real |  |  | 1 | 0
x012_u002E_025 | Parameter subset 1->DIST | 012.025 | Forward directional¦0;Backward directional¦1;Non-directional¦2 |  | Direction N3 PS1 | Enum | Parameters__Function_parameters | 0;1;2 | Real |  | x003_u002E_060 | E | 1 | 0 |  | NE | 2 | Distance Circular\Z3 | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Circular\Z3 | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z3 | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\Z3 | idir | Real |  |  | 1 | 0
x012_u002E_026 | Parameter subset 1->DIST | 012.026 | Forward directional¦0;Backward directional¦1;Non-directional¦2 |  | Direction N4 PS1 | Enum | Parameters__Function_parameters | 0;1;2 | Real |  | x003_u002E_060 | E | 1 | 0 |  | NE | 2 | Distance Circular\Z4 | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Circular\Z4 | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z4 | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\Z4 | idir | Real |  |  | 1 | 0
x012_u002E_027 | Parameter subset 1->DIST | 012.027 | Forward directional¦0;Backward directional¦1;Non-directional¦2 |  | Direction N5 PS1 | Enum | Parameters__Function_parameters | 0;1;2 | Real |  | x003_u002E_060 | E | 1 | 0 |  |  |  | Distance Circular\Directional | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Directional;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Circular\Directional | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Directional | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Directional;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\Directional | idir | Real |  |  | 1 | 0
x012_u002E_028 | Parameter subset 1->DIST | 012.028 | 0-10:0.001;Blocked=10.002 | s | t1 PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 0 | 4 | SE | 10 | Distance Circular\T1 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Circular\T1 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Circular\T1 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
[16 empty] | SE | 10 | Distance Polygonal\T1 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Polygonal\T1 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Polygonal\T1 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
x012_u002E_029 | Parameter subset 1->DIST | 012.029 | 0-10:0.001;Blocked=10.002 | s | t2 PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 | 4 | SE | 10 | Distance Circular\T2 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Circular\T2 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Circular\T2 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
[16 empty] | SE | 10 | Distance Polygonal\T2 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Polygonal\T2 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Polygonal\T2 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
x012_u002E_030 | Parameter subset 1->DIST | 012.030 | 0-10:0.001;Blocked=10.002 | s | t3 PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 2 | 4 | SE | 10 | Distance Circular\T3 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Circular\T3 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Circular\T3 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
[16 empty] | SE | 10 | Distance Polygonal\T3 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Polygonal\T3 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Polygonal\T3 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
x012_u002E_031 | Parameter subset 1->DIST | 012.031 | 0-10:0.001;Blocked=10.002 | s | t4 PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 3 | 4 | SE | 10 | Distance Circular\T4 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Circular\T4 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Circular\T4 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
[16 empty] | SE | 10 | Distance Polygonal\T4 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Polygonal\T4 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Polygonal\T4 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
x012_u002E_032 | Parameter subset 1->DIST | 012.032 | 0-10:0.001;Blocked=10.002 | s | t5 PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 4 | 4 | SE | 10 | Distance Circular\T5 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Circular\T5 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Circular\T5 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
[16 empty] | SE | 10 | Distance Polygonal\T5 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Polygonal\T5 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Polygonal\T5 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
x012_u002E_033 | Parameter subset 1->DIST | 012.033 | 0-10:0.001;Blocked=10.002 | s | t6 PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 5 | 4 | SE | 10 | Distance Circular\T6 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Circular\T6 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Circular\T6 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
[16 empty] | SE | 10 | Distance Polygonal\T6 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Polygonal\T6 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Polygonal\T6 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
x012_u002E_035 | Parameter subset 1->DIST | 012.035 | 1-450:0.01 |  | kze,PP HSR PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1.2 | 3 |  |  | Distance Circular\Z1E | kZ | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z1E;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Circular\Z1E | kZ | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z1E | kX | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z1E;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\Z1E | kX | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z1E | kR | Real | 1 | 0
x015_u002E_014 | Parameter subset 1->PSIG | 015.014 | No¦0;Yes¦1 |  | Enable PS1 | Enum | Parameters__Function_parameters | 0;1 | String |  | x003_u002E_060 | E | 1 | 0 | 2 |  |  | Distance Circular\PSIG Connect | aDipset | String |  |  | 2 | Distance Circular;Distance Circular\PSIG Connect;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Circular\PSIG Connect | aDipset | String
[18 empty] | Distance Polygonal\PSIG Connect | aDipset | String |  |  |  | Distance Polygonal;Distance Polygonal\PSIG Connect;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\PSIG Connect | aDipset | String
x015_u002E_000 | Parameter subset 1->PSIG | 015.000 | Without¦0;Dir.trans.trip.under¦1;PUTT¦2;Zone extension¦3;Release scheme¦4;Blocking scheme¦5;DC loop operat. mode¦6;Reverse interlocking¦7;Direction comparison¦8 |  | Operating mode PS1 | Enum | Parameters__Function_parameters | ;DIRECT = TRIP;PUTT = TRIP;POTT = TRIP;COMP_RELEASE = TRIP;COMP_BLOCK = TRIP;COMP_PILOT = TRIP; | String |  | x003_u002E_060 | E | 1 | PUTT = TRIP | 4 |  |  | Distance Circular\PSIG Receive | sLogic | String |  |  | 2 | Distance Circular;Distance Circular\PSIG Receive;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Circular\PSIG Receive | sLogic | String
[18 empty] | Distance Circular\PSIG Send | sLogic | String |  |  |  | Distance Polygonal;Distance Polygonal\PSIG Receive;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\PSIG Receive | sLogic | String
[18 empty] | Distance Polygonal\PSIG Receive | sLogic | String
[18 empty] | Distance Polygonal\PSIG Send | sLogic | String
x015_u002E_011 | Parameter subset 1->PSIG | 015.011 | 0-10:0.001;Blocked=10.002 | s | Tripping time PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 0.08 | 4 | SE | 10 | Distance Circular\PSIG T | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\PSIG T;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Circular\PSIG T | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Circular\PSIG T | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
[16 empty] | SE | 10 | Distance Polygonal\PSIG T | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\PSIG T;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 | 2 | Distance Polygonal\PSIG T | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Polygonal\PSIG T | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
x015_u002E_002 | Parameter subset 1->PSIG | 015.002 | 0-10:0.001 | s | Release t. send PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 0.25 | 2 |  |  | Distance Circular\PSIG T Reset | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\PSIG T Reset;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Circular\PSIG T Reset | Tdelay | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\PSIG T Reset | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\PSIG T Reset;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;1 |  | Distance Polygonal\PSIG T Reset | Tdelay | Real |  |  | 1 | 0
x072_u002E_098 | Parameter subset 1->DTOC | 072.098 | No¦0;Yes¦1 |  | Enable PS1 | Enum | Parameters__Function_parameters | 1;0 | Real |  | x056_u002E_008;x003_u002E_060 | E;E | 0;1 | 1 | 12 |  |  | Overcurrent\I> | outserv | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 12 | Overcurrent\I> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\I>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\I>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\I>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\I>>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\I>>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\I>>>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\IN> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\IN> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\IN>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\IN>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\IN>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\IN>>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\IN>>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\IN>>>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\Ineg> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\Ineg> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\Ineg>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\Ineg>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\Ineg>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\Ineg>>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\Ineg>>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\Ineg>>>> | outserv | Real |  |  | 1 | 0
x072_u002E_007 | Parameter subset 1->DTOC | 072.007 | 0.1-20:0.01 | Inom | I> PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 |  |  |  | Overcurrent\I> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\I> | Ipset | Real |  |  | 1 | 0
x072_u002E_008 | Parameter subset 1->DTOC | 072.008 | 0.1-20:0.01 | Inom | I>> PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 |  |  |  | Overcurrent\I>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\I>> | Ipset | Real |  |  | 1 | 0
x072_u002E_009 | Parameter subset 1->DTOC | 072.009 | 0.1-20:0.01 | Inom | I>>> PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 |  |  |  | Overcurrent\I>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\I>>> | Ipset | Real |  |  | 1 | 0
x072_u002E_010 | Parameter subset 1->DTOC | 072.010 | 0.1-20:0.01 | Inom | I>>>> PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 |  |  |  | Overcurrent\I>>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\I>>>> | Ipset | Real |  |  | 1 | 0
x072_u002E_019 | Parameter subset 1->DTOC | 072.019 | 0-30:0.001;Blocked=30.002 | s | tI> PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 | SE | 30 | Overcurrent\I> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Overcurrent\I> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\I> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x072_u002E_020 | Parameter subset 1->DTOC | 072.020 | 0-30:0.001;Blocked=30.002 | s | tI>> PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 | SE | 30 | Overcurrent\I>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Overcurrent\I>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\I>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x072_u002E_021 | Parameter subset 1->DTOC | 072.021 | 0-30:0.001;Blocked=30.002 | s | tI>>> PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 | SE | 30 | Overcurrent\I>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Overcurrent\I>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\I>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x072_u002E_022 | Parameter subset 1->DTOC | 072.022 | 0-30:0.001;Blocked=30.002 | s | tI>>>> PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 | SE | 30 | Overcurrent\I>>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Overcurrent\I>>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\I>>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x072_u002E_011 | Parameter subset 1->DTOC | 072.011 | 0.1-20:0.01 | Inom | Ineg> PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 |  |  |  | Overcurrent\IN> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\IN> | Ipset | Real |  |  | 1 | 0
x072_u002E_012 | Parameter subset 1->DTOC | 072.012 | 0.1-20:0.01 | Inom | Ineg>> PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 |  |  |  | Overcurrent\IN>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\IN>> | Ipset | Real |  |  | 1 | 0
x072_u002E_013 | Parameter subset 1->DTOC | 072.013 | 0.1-20:0.01 | Inom | Ineg>>> PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 |  |  |  | Overcurrent\IN>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\IN>>> | Ipset | Real |  |  | 1 | 0
x072_u002E_014 | Parameter subset 1->DTOC | 072.014 | 0.1-20:0.01 | Inom | Ineg>>>> PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 |  |  |  | Overcurrent\IN>>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\IN>>>> | Ipset | Real |  |  | 1 | 0
x072_u002E_023 | Parameter subset 1->DTOC | 072.023 | 0-30:0.001;Blocked=30.002 | s | tIneg> PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 | SE | 30 | Overcurrent\IN> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Overcurrent\IN> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\IN> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x072_u002E_024 | Parameter subset 1->DTOC | 072.024 | 0-30:0.001;Blocked=30.002 | s | tIneg>> PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 | SE | 30 | Overcurrent\IN>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Overcurrent\IN>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\IN>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x072_u002E_025 | Parameter subset 1->DTOC | 072.025 | 0-30:0.001;Blocked=30.002 | s | tIneg>>> PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 | SE | 30 | Overcurrent\IN>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Overcurrent\IN>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\IN>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x072_u002E_026 | Parameter subset 1->DTOC | 072.026 | 0-30:0.001;Blocked=30.002 | s | tIneg>>>> PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 | SE | 30 | Overcurrent\IN>>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Overcurrent\IN>>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\IN>>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x072_u002E_015 | Parameter subset 1->DTOC | 072.015 | 0.1-20:0.01 | Inom | IN> PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 |  |  |  | Overcurrent\Ineg> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\Ineg> | Ipset | Real |  |  | 1 | 0
x072_u002E_016 | Parameter subset 1->DTOC | 072.016 | 0.1-20:0.01 | Inom | IN>> PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 |  |  |  | Overcurrent\Ineg>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\Ineg>> | Ipset | Real |  |  | 1 | 0
x072_u002E_017 | Parameter subset 1->DTOC | 072.017 | 0.1-20:0.01 | Inom | IN>>> PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 |  |  |  | Overcurrent\Ineg>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\Ineg>>> | Ipset | Real |  |  | 1 | 0
x072_u002E_018 | Parameter subset 1->DTOC | 072.018 | 0.1-20:0.01 | Inom | IN>>>> PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 |  |  |  | Overcurrent\Ineg>>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\Ineg>>>> | Ipset | Real |  |  | 1 | 0
x072_u002E_027 | Parameter subset 1->DTOC | 072.027 | 0-30:0.001;Blocked=30.002 | s | tIN> PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 | SE | 30 | Overcurrent\Ineg> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Overcurrent\Ineg> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\Ineg> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x072_u002E_028 | Parameter subset 1->DTOC | 072.028 | 0-30:0.001;Blocked=30.002 | s | tIN>> PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 | SE | 30 | Overcurrent\Ineg>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Overcurrent\Ineg>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\Ineg>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x072_u002E_029 | Parameter subset 1->DTOC | 072.029 | 0-30:0.001;Blocked=30.002 | s | tIN>>> PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 | SE | 30 | Overcurrent\Ineg>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Overcurrent\Ineg>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\Ineg>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x072_u002E_030 | Parameter subset 1->DTOC | 072.030 | 0-30:0.001;Blocked=30.002 | s | tIN>>>> PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 | SE | 30 | Overcurrent\Ineg>>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Overcurrent\Ineg>>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\Ineg>>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x072_u002E_000 | Parameter subset 1->IDMT | 072.000 | No¦0;Yes¦1 |  | Enable P PS1 | Enum | Parameters__Function_parameters | 1;0 | Real |  | x056_u002E_009;x003_u002E_060 | E;E | 0;1 | 1 |  |  |  | Overcurrent\IDMT P | outserv | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\IDMT P | outserv | Real |  |  | 1 | 0
x072_u002E_050 | Parameter subset 1->IDMT | 072.050 | 0.1-4:0.01 | Inom | Iref,P PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 |  |  |  | Overcurrent\IDMT P | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\IDMT P | Ipset | Real |  |  | 1 | 0
x072_u002E_056 | Parameter subset 1->IDMT | 072.056 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Characterist. P PS1 | Enum | Parameters__Function_parameters | Definite Time;IEC 255-3 Standard Inverse;IEC 255-3 Very Inverse;IEC 255-3 Extremly Inverse;IEC 255-3 Long-Time Inverse;IEEE C37.112 Moderately Inverse;IEEE C37.112 Very Inverse;IEEE C37.112 Extremely Inverse;ANSI Normally Inverse;ANSI Short-Time Inverse;ANSI Long-Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | [8 empty] | Overcurrent\IDMT P | pcharac |  |  |  |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\IDMT P | pcharac
x072_u002E_053 | Parameter subset 1->IDMT | 072.053 | 0.01-10:0.01 |  | Ch. factor kt,P PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 |  |  |  | Overcurrent\IDMT P | Tpset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\IDMT P | Tpset | Real |  |  | 1 | 0
x072_u002E_059 | Parameter subset 1->IDMT | 072.059 | Without delay¦0;Delayed as per char.¦1 |  | Reset P PS1 | Enum | Parameters__Function_parameters | 0;1 | Real | 3 | x003_u002E_060;x072_u002E_056 | E;SW | 1;IEEE | 0 |  |  |  | Overcurrent\IDMT P | resetdis | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\IDMT P | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x072_u002E_056 | E;SW | 1;ANSI |  |  |  |  | Overcurrent\IDMT P | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | 1 |  |  |  |  | Overcurrent\IDMT P | resetdis | Real | 0 | 0
x072_u002E_062 | Parameter subset 1->IDMT | 072.062 | Forward directional¦0;Backward directional¦1;Non-directional¦2 |  | Direction P PS1 | Enum | Parameters__Function_parameters | 1;2;0 | Real |  | x003_u002E_060 | E | 1 | 1 |  |  |  | Overcurrent\IDMT P | idir | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\IDMT P | idir | Real |  |  | 1 | 0
x072_u002E_001 | Parameter subset 1->IDMT | 072.001 | No¦0;Yes¦1 |  | Enable neg. PS1 | Enum | Parameters__Function_parameters | 1;0 | Real |  | x056_u002E_009;x003_u002E_060 | E;E | 0;1 | 1 |  |  |  | Overcurrent\IDMT neg | outserv | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\IDMT neg | outserv | Real |  |  | 1 | 0
x072_u002E_051 | Parameter subset 1->IDMT | 072.051 | 0.1-4:0.01 | Inom | Iref,neg PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 |  |  |  | Overcurrent\IDMT neg | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\IDMT neg | Ipset | Real |  |  | 1 | 0
x072_u002E_057 | Parameter subset 1->IDMT | 072.057 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Character. neg. PS1 | Enum | Parameters__Function_parameters | Definite Time;IEC 255-3 Standard Inverse;IEC 255-3 Very Inverse;IEC 255-3 Extremly Inverse;IEC 255-3 Long-Time Inverse;IEEE C37.112 Moderately Inverse;IEEE C37.112 Very Inverse;IEEE C37.112 Extremely Inverse;ANSI Normally Inverse;ANSI Short-Time Inverse;ANSI Long-Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | [8 empty] | Overcurrent\IDMT neg | pcharac |  |  |  |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\IDMT neg | pcharac
x072_u002E_054 | Parameter subset 1->IDMT | 072.054 | 0.01-10:0.01 |  | Factor kt,neg PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 |  |  |  | Overcurrent\IDMT neg | Tpset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\IDMT neg | Tpset | Real |  |  | 1 | 0
x072_u002E_060 | Parameter subset 1->IDMT | 072.060 | Without delay¦0;Delayed as per char.¦1 |  | Reset neg. PS1 | Enum | Parameters__Function_parameters | 0;1 | Real | 3 | x003_u002E_060;x072_u002E_057 | E;SW | 1;IEEE | 0 |  |  |  | Overcurrent\IDMT neg | resetdis | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\IDMT neg | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x072_u002E_057 | E;SW | 1;ANSI |  |  |  |  | Overcurrent\IDMT neg | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | 1 |  |  |  |  | Overcurrent\IDMT neg | resetdis | Real | 0 | 0
x072_u002E_063 | Parameter subset 1->IDMT | 072.063 | Forward directional¦0;Backward directional¦1;Non-directional¦2 |  | Direction neg. PS1 | Enum | Parameters__Function_parameters | 1;2;0 | Real |  | x003_u002E_060 | E | 1 | 1 |  |  |  | Overcurrent\IDMT neg | idir | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\IDMT neg | idir | Real |  |  | 1 | 0
x072_u002E_002 | Parameter subset 1->IDMT | 072.002 | No¦0;Yes¦1 |  | Enable N PS1 | Enum | Parameters__Function_parameters | 1;0 | Real |  | x056_u002E_009;x003_u002E_060 | E;E | 0;1 | 1 |  |  |  | Overcurrent\IDMT N | outserv | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\IDMT N | outserv | Real |  |  | 1 | 0
x072_u002E_052 | Parameter subset 1->IDMT | 072.052 | 0.1-4:0.01 | Inom | Iref,N PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 |  |  |  | Overcurrent\IDMT N | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\IDMT N | Ipset | Real |  |  | 1 | 0
x072_u002E_058 | Parameter subset 1->IDMT | 072.058 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Characterist. N PS1 | Enum | Parameters__Function_parameters | Definite Time;IEC 255-3 Standard Inverse;IEC 255-3 Very Inverse;IEC 255-3 Extremly Inverse;IEC 255-3 Long-Time Inverse;IEEE C37.112 Moderately Inverse;IEEE C37.112 Very Inverse;IEEE C37.112 Extremely Inverse;ANSI Normally Inverse;ANSI Short-Time Inverse;ANSI Long-Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | [8 empty] | Overcurrent\IDMT N | pcharac |  |  |  |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\IDMT N | pcharac
x072_u002E_055 | Parameter subset 1->IDMT | 072.055 | 0.01-10:0.01 |  | Factor kt,N PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 |  |  |  | Overcurrent\IDMT N | Tpset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\IDMT N | Tpset | Real |  |  | 1 | 0
x072_u002E_061 | Parameter subset 1->IDMT | 072.061 | Without delay¦0;Delayed as per char.¦1 |  | Reset N PS1 | Enum | Parameters__Function_parameters | 0;1 | Real | 3 | x003_u002E_060;x072_u002E_058 | E;SW | 1;IEEE | 0 |  |  |  | Overcurrent\IDMT neg | resetdis | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\IDMT neg | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x072_u002E_058 | E;SW | 1;ANSI |  |  |  |  | Overcurrent\IDMT neg | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | 1 |  |  |  |  | Overcurrent\IDMT neg | resetdis | Real | 0 | 0
x072_u002E_064 | Parameter subset 1->IDMT | 072.064 | Forward directional¦0;Backward directional¦1;Non-directional¦2 |  | Direction N PS1 | Enum | Parameters__Function_parameters | 1;2;0 | Real |  | x003_u002E_060 | E | 1 | 1 |  |  |  | Overcurrent\IDMT N | idir | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Overcurrent\IDMT N | idir | Real |  |  | 1 | 0
x076_u002E_000 | Parameter subset 1->V<> | 076.000 | No¦0;Yes¦1 |  | Enable PS1 | Enum | Parameters__Function_parameters | 1;0 | Real |  | x056_u002E_010;x003_u002E_060 | E;E | 0;1 | 1 |  |  |  | Voltage | outserv | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 |  | Voltage | outserv | Real |  |  | 1 | 0
x076_u002E_001 | Parameter subset 1->V<> | 076.001 | Delta¦0;Star¦1 |  | Operating mode PS1 | Enum | Parameters__Function_parameters | 0;1 | Real |  | x076_u002E_000;x003_u002E_060 | E;E | 0;1 | 0 | 4 | E | 1 | Voltage\V> | outserv | Real | 0 | 1
[16 empty] | E | 1 | Voltage\V>> | outserv | Real | 0 | 1
[16 empty] | E | 1 | Voltage\V< | outserv | Real | 0 | 1
[16 empty] | E | 1 | Voltage\V<< | outserv | Real | 0 | 1
x076_u002E_003 | Parameter subset 1->V<> | 076.003 | 0.2-1.5:0.01;Blocked=1.52 | Vnom(/©3) | V> PS1 | Real | Parameters__Function_parameters |  |  |  | x076_u002E_001;x003_u002E_060 | E;E | 0;1 | 1.1 | 3 | SE | 1.5 | Voltage\V> | Uset | Real | 1 | 0 |  | x076_u002E_001;x003_u002E_060 |  |  | E;E | 0;1 | 2 | Voltage\V> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V> | outserv | Real | 0 | 0 | [7 empty] | Voltage\V> | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\V> | outserv | Real | 0 | 1
x076_u002E_004 | Parameter subset 1->V<> | 076.004 | 0.2-1.5:0.01;Blocked=1.52 | Vnom(/©3) | V>> PS1 | Real | Parameters__Function_parameters |  |  |  | x076_u002E_001;x003_u002E_060 | E;E | 0;1 | 1.1 | 3 | SE | 1.5 | Voltage\V>> | Uset | Real | 1 | 0 |  | x076_u002E_001;x003_u002E_060 |  |  | E;E | 0;1 | 2 | Voltage\V>> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\V>> | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\V>> | outserv | Real | 0 | 1
x076_u002E_005 | Parameter subset 1->V<> | 076.005 | 0-100:0.01;Blocked=100.02 | s | tV> PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 | SE | 100 | Voltage\V> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Voltage\V> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x076_u002E_006 | Parameter subset 1->V<> | 076.006 | 0-100:0.01;Blocked=100.02 | s | tV>> PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 | SE | 100 | Voltage\V>> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Voltage\V>> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V>> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x076_u002E_007 | Parameter subset 1->V<> | 076.007 | 0.2-1.5:0.01;Blocked=1.52 | Vnom(/©3) | V< PS1 | Real | Parameters__Function_parameters |  |  |  | x076_u002E_001;x003_u002E_060 | E;E | 0;1 | 0.8 | 3 | SE | 1.5 | Voltage\V< | Uset | Real | 1 | 0 |  | x076_u002E_001;x003_u002E_060 |  |  | E;E | 0;1 | 2 | Voltage\V< | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V< | outserv | Real | 0 | 0 | [7 empty] | Voltage\V< | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\V< | outserv | Real | 0 | 1
x076_u002E_008 | Parameter subset 1->V<> | 076.008 | 0.2-1.5:0.01;Blocked=1.52 | Vnom(/©3) | V<< PS1 | Real | Parameters__Function_parameters |  |  |  | x076_u002E_001;x003_u002E_060 | E;E | 0;1 | 0.8 | 3 | SE | 1.5 | Voltage\V<< | Uset | Real | 1 | 0 |  | x076_u002E_001;x003_u002E_060 |  |  | E;E | 0;1 | 2 | Voltage\V<< | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V<< | outserv | Real | 0 | 0 | [7 empty] | Voltage\V<< | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\V<< | outserv | Real | 0 | 1
x076_u002E_009 | Parameter subset 1->V<> | 076.009 | 0-100:0.01;Blocked=100.02 | s | tV< PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 | SE | 100 | Voltage\V< | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Voltage\V< | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V< | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x076_u002E_010 | Parameter subset 1->V<> | 076.010 | 0-100:0.01;Blocked=100.02 | s | tV<< PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 | SE | 100 | Voltage\V<< | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Voltage\V<< | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V<< | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x076_u002E_015 | Parameter subset 1->V<> | 076.015 | 0.2-1.5:0.01;Blocked=1.52 | Vnom/©3 | Vpos> PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1.1 | 3 | SE | 1.5 | Voltage\Vpos> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Voltage\Vpos> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos> | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vpos> | outserv | Real | 0 | 1
x076_u002E_016 | Parameter subset 1->V<> | 076.016 | 0.2-1.5:0.01;Blocked=1.52 | Vnom/©3 | Vpos>> PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1.1 | 3 | SE | 1.5 | Voltage\Vpos>> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Voltage\Vpos>> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos>> | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vpos>> | outserv | Real | 0 | 1
x076_u002E_017 | Parameter subset 1->V<> | 076.017 | 0-100:0.01;Blocked=100.02 | s | tVpos> PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 | SE | 100 | Voltage\Vpos> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Voltage\Vpos> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vpos> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x076_u002E_018 | Parameter subset 1->V<> | 076.018 | 0-100:0.01;Blocked=100.02 | s | tVpos>> PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 | SE | 100 | Voltage\Vpos>> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Voltage\Vpos>> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vpos>> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x076_u002E_019 | Parameter subset 1->V<> | 076.019 | 0.2-1.5:0.01;Blocked=1.52 | Vnom/©3 | Vpos< PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 0.8 | 3 | SE | 1.5 | Voltage\Vpos< | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Voltage\Vpos< | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos< | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos< | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vpos< | outserv | Real | 0 | 1
x076_u002E_020 | Parameter subset 1->V<> | 076.020 | 0.2-1.5:0.01;Blocked=1.52 | Vnom/©3 | Vpos<< PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 0.8 | 3 | SE | 1.5 | Voltage\Vpos<< | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Voltage\Vpos<< | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos<< | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos<< | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vpos<< | outserv | Real | 0 | 1
x076_u002E_021 | Parameter subset 1->V<> | 076.021 | 0-100:0.01;Blocked=100.02 | s | tVpos< PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 | SE | 100 | Voltage\Vpos< | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Voltage\Vpos< | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vpos< | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x076_u002E_022 | Parameter subset 1->V<> | 076.022 | 0-100:0.01;Blocked=100.02 | s | tVpos<< PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 | SE | 100 | Voltage\Vpos<< | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Voltage\Vpos<< | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vpos<< | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x076_u002E_023 | Parameter subset 1->V<> | 076.023 | 0.2-1.5:0.01;Blocked=1.52 | Vnom/©3 | Vneg> PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1.52 | 3 | SE | 1.5 | Voltage\Vneg> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Voltage\Vneg> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vneg> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vneg> | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vneg> | outserv | Real | 0 | 1
x076_u002E_024 | Parameter subset 1->V<> | 076.024 | 0.2-1.5:0.01;Blocked=1.52 | Vnom/©3 | Vneg>> PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1.52 | 3 | SE | 1.5 | Voltage\Vneg>> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Voltage\Vneg>> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vneg>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vneg>> | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vneg>> | outserv | Real | 0 | 1
x076_u002E_025 | Parameter subset 1->V<> | 076.025 | 0-100:0.01;Blocked=100.02 | s | tVneg> PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 | SE | 100 | Voltage\Vneg> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Voltage\Vneg> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vneg> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x076_u002E_026 | Parameter subset 1->V<> | 076.026 | 0-100:0.01;Blocked=100.02 | s | tVneg>> PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 | SE | 100 | Voltage\Vneg>> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Voltage\Vneg>> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vneg>> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x076_u002E_011 | Parameter subset 1->V<> | 076.011 | 0.02-1:0.01;Blocked=1.02 | Vnom(/©3) | VNG> PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1.02 | 3 | SE | 1 | Voltage\VNG> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Voltage\VNG> | outserv | Real | E | 1 | 0 | 1.02
[16 empty] | SE | 1 | Voltage\VNG> | outserv | Real | 0 | 0 | [7 empty] | Voltage\VNG> | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1 | Voltage\VNG> | outserv | Real | 0 | 1
x076_u002E_012 | Parameter subset 1->V<> | 076.012 | 0.02-1:0.01;Blocked=1.02 | Vnom(/©3) | VNG>> PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1.02 | 3 | SE | 1 | Voltage\VNG>> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Voltage\VNG>> | outserv | Real | E | 1 | 0 | 1.02
[16 empty] | SE | 1 | Voltage\VNG>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\VNG>> | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1 | Voltage\VNG>> | outserv | Real | 0 | 1
x076_u002E_013 | Parameter subset 1->V<> | 076.013 | 0-100:0.01;Blocked=100.02 | s | tVNG> PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 | SE | 100 | Voltage\VNG> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Voltage\VNG> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\VNG> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x076_u002E_014 | Parameter subset 1->V<> | 076.014 | 0-100:0.01;Blocked=100.02 | s | tVNG>> PS1 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 1 | 1 | 2 | SE | 100 | Voltage\VNG>> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 1 | 2 | Voltage\VNG>> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\VNG>> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x010_u002E_074 | Parameter subset 2->DIST | 010.074 | 0.1-20:0.01 | Inom | I>> PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 |  |  | Distance Circular\Starting | IMM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Circular\Starting | IMM | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | IMM | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Polygonal\Starting | IMM | Real |  |  | 1 | 0
x010_u002E_088 | Parameter subset 2->DIST | 010.088 | 0.1-1:0.01 | Inom | I> (Ibl) high r. PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 0.2 | 2 |  |  | Distance Circular\Starting | IM1 | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Circular\Starting | IM1 | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | IM1 | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Polygonal\Starting | IM1 | Real |  |  | 1 | 0
x010_u002E_087 | Parameter subset 2->DIST | 010.087 | W/o V< starting¦0;With V< start. PG¦1;With V< start.PG,PP¦2 |  | Operat. mode V< PS2 | Enum | Parameters__Function_parameters | 0;1;2 | Real |  | x003_u002E_060 | E | 2 | 2 | 8 | E | 0 | Distance Circular\Starting | iopt_u | Real | 0 | 0 | 4 | Distance Circular;Distance Circular\Starting;x003_u002E_060 | outserv;iopt_u | Real | E;E;E | 0;0;2 | [7 empty] | 0
[16 empty] | E | 0 | Distance Polygonal\Starting | iopt_u | Real | 0 | 0 |  | Distance Circular;Distance Circular\Starting;x003_u002E_060 | outserv;iopt_u | Real | E;E;E | 0;1;2 | 2 | Distance Circular\Starting | iVOpMode | Real | 0 | 0 | 0 | 1
[16 empty] | NE | 0 | Distance Circular\Starting | iopt_u | Real | 0 | 1 | [7 empty] | Distance Circular\Starting | iVOpMode | Real | 0 | 1 | 0 | 2
[16 empty] | NE | 0 | Distance Polygonal\Starting | iopt_u | Real | 0 | 1 |  | Distance Polygonal;Distance Polygonal\Starting;x003_u002E_060 | outserv;iopt_u | Real | E;E;E | 0;0;2 | [7 empty] | 0
[16 empty] | E | 1 | Distance Circular\Starting | iVOpMode | Real | 0 | 0 |  | Distance Polygonal;Distance Polygonal\Starting;x003_u002E_060 | outserv;iopt_u | Real | E;E;E | 0;1;2 | 2 | Distance Polygonal\Starting | iVOpMode | Real | 0 | 0 | 0 | 1
[16 empty] | E | 1 | Distance Polygonal\Starting | iVOpMode | Real | 0 | 0 | [7 empty] | Distance Polygonal\Starting | iVOpMode | Real | 0 | 1 | 0 | 2
[16 empty] | E | 2 | Distance Circular\Starting | iVOpMode | Real | 0 | 1
[16 empty] | E | 2 | Distance Polygonal\Starting | iVOpMode | Real | 0 | 1
x010_u002E_089 | Parameter subset 2->DIST | 010.089 | 0.1-0.9:0.01 | Vnom(/©3) | V< PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 0.7 | 2 |  |  | Distance Circular\Starting | Um | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Circular\Starting | Um | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | Um | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Polygonal\Starting | Um | Real |  |  | 1 | 0
x010_u002E_086 | Parameter subset 2->DIST | 010.086 | W/o Z< starting¦0;With Z< starting P-G¦1;With Z< start.PG,PP¦2 |  | Operat. mode Z< PS2 | Enum | Parameters__Function_parameters | 0;1;2 | Real |  | x003_u002E_060 | E | 2 | 2 | 8 | E | 0 | Distance Circular\Starting | iopt_z | Real | 0 | 0 | 4 | Distance Circular;Distance Circular\Starting;x003_u002E_060 | outserv;iopt_z | Real | E;E;E | 0;0;2 | [7 empty] | 0
[16 empty] | E | 0 | Distance Polygonal\Starting | iopt_z | Real | 0 | 0 |  | Distance Circular;Distance Circular\Starting;x003_u002E_060 | outserv;iopt_z | Real | E;E;E | 0;1;2 | 2 | Distance Circular\Starting | iZOpMode | Real | 0 | 0 | 0 | 1
[16 empty] | NE | 0 | Distance Circular\Starting | iopt_z | Real | 0 | 1 | [7 empty] | Distance Circular\Starting | iZOpMode | Real | 0 | 1 | 0 | 2
[16 empty] | NE | 0 | Distance Polygonal\Starting | iopt_z | Real | 0 | 1 |  | Distance Polygonal;Distance Polygonal\Starting;x003_u002E_060 | outserv;iopt_z | Real | E;E;E | 0;0;2 | [7 empty] | 0
[16 empty] | E | 1 | Distance Circular\Starting | iZOpMode | Real | 0 | 0 |  | Distance Polygonal;Distance Polygonal\Starting;x003_u002E_060 | outserv;iopt_z | Real | E;E;E | 0;1;2 | 2 | Distance Polygonal\Starting | iZOpMode | Real | 0 | 0 | 0 | 1
[16 empty] | E | 1 | Distance Polygonal\Starting | iZOpMode | Real | 0 | 0 | [7 empty] | Distance Polygonal\Starting | iZOpMode | Real | 0 | 1 | 0 | 2
[16 empty] | E | 2 | Distance Circular\Starting | iZOpMode | Real | 0 | 1
[16 empty] | E | 2 | Distance Polygonal\Starting | iZOpMode | Real | 0 | 1
x010_u002E_070 | Parameter subset 2->DIST | 010.070 | 0.1-300:0.01 | — | Xfw PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 10 | 2 |  |  | Distance Circular\Starting | Xfw | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Circular\Starting | Xfw | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | Xfw | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Polygonal\Starting | Xfw | Real |  |  | 1 | 0
x010_u002E_071 | Parameter subset 2->DIST | 010.071 | 0.1-300:0.01 | — | Rfw,PG PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 10 | 2 |  |  | Distance Circular\Starting | RfPG | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Circular\Starting | RfPG | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | RfPG | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Polygonal\Starting | RfPG | Real |  |  | 1 | 0
x010_u002E_072 | Parameter subset 2->DIST | 010.072 | 0.1-300:0.01 | — | Rfw,PP PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 10 | 2 |  |  | Distance Circular\Starting | RfPP | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Circular\Starting | RfPP | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | RfPP | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Polygonal\Starting | RfPP | Real |  |  | 1 | 0
x010_u002E_083 | Parameter subset 2->DIST | 010.083 | 15-65:1 | ° | ß PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 30 | 2 |  |  | Distance Circular\Starting | Beta | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Circular\Starting | Beta | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | Beta | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Polygonal\Starting | Beta | Real |  |  | 1 | 0
x010_u002E_102 | Parameter subset 2->DIST | 010.102 | 0-300:0.01 | — | Zfw,PG PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 10 | 2 |  |  | Distance Circular\Starting | ZfPG | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Circular\Starting | ZfPG | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | ZfPG | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Polygonal\Starting | ZfPG | Real |  |  | 1 | 0
x010_u002E_106 | Parameter subset 2->DIST | 010.106 | 0-300:0.01 | — | Zfw,PP PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 10 | 2 |  |  | Distance Circular\Starting | ZfPP | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Circular\Starting | ZfPP | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | ZfPP | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Polygonal\Starting | ZfPP | Real |  |  | 1 | 0
x010_u002E_073 | Parameter subset 2->DIST | 010.073 | 0.1-4:0.01 |  | Zbw/Zfw PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 0.5 | 2 |  |  | Distance Circular\Starting | ZbwZfw | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Circular\Starting | ZbwZfw | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | ZbwZfw | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Polygonal\Starting | ZbwZfw | Real |  |  | 1 | 0
x010_u002E_075 | Parameter subset 2->DIST | 010.075 | 0.1-2:0.01 | Inom | IN> high range PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 0.2 | 2 |  |  | Distance Circular\Starting | INM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Circular\Starting | INM | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | INM | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Polygonal\Starting | INM | Real |  |  | 1 | 0
x010_u002E_077 | Parameter subset 2->DIST | 010.077 | 0-0.5:0.001 | s | tIN> PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 0.1 | 2 |  |  | Distance Circular\Starting | tINM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Circular\Starting | tINM | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | tINM | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Polygonal\Starting | tINM | Real |  |  | 1 | 0
x010_u002E_076 | Parameter subset 2->DIST | 010.076 | 0.02-1:0.01 | Vnom | VNG> PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 0.1 | 2 |  |  | Distance Circular\Starting | VNGM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Circular\Starting | VNGM | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | VNGM | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Polygonal\Starting | VNGM | Real |  |  | 1 | 0
x010_u002E_082 | Parameter subset 2->DIST | 010.082 | 0.2-1:0.01 | Vnom | VNG>> PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 0.5 | 2 |  |  | Distance Circular\Starting | VNGMM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Circular\Starting | VNGMM | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | VNGMM | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Polygonal\Starting | VNGMM | Real |  |  | 1 | 0
x010_u002E_081 | Parameter subset 2->DIST | 010.081 | 0-60:0.001 | s | tVNG>> PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 |  |  | Distance Circular\Starting | tVNGMM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Circular\Starting | tVNGMM | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | tVNGMM | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Polygonal\Starting | tVNGMM | Real |  |  | 1 | 0
x012_u002E_087 | Parameter subset 2->DIST | 012.087 | 0-8:0.01 |  | Abs. value kG PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 |  |  | Distance Circular\Polarisation | k0 | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Circular\Polarisation | k0 | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Polarisation | k0 | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Polygonal\Polarisation | k0 | Real |  |  | 1 | 0
x012_u002E_086 | Parameter subset 2->DIST | 012.086 | -180-180:1 | ° | Angle kG PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 0 | 2 |  |  | Distance Circular\Polarisation | phik0 | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Circular\Polarisation | phik0 | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Polarisation | phik0 | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;2 |  | Distance Polygonal\Polarisation | phik0 | Real |  |  | 1 | 0
x073_u002E_097 | Parameter subset 2->DIST | 073.097 | Circle¦0;Polygon¦1 |  | Characteristic PS2 | Enum | Parameters__Function_parameters | 0;1 | Real |  | x056_u002E_014;x031_u002E_073;x003_u002E_060 | E;E;E | 0;0;2 | 1 | 4 | E | 0 | Distance Circular | outserv | Real | 0 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Distance Circular | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 0 | Distance Polygonal | outserv | Real | 0 | 1 | [13 empty] | 1
[16 empty] | E | 1 | Distance Circular | outserv | Real | 0 | 1
[16 empty] | E | 1 | Distance Polygonal | outserv | Real | 0 | 0
x012_u002E_051 | Parameter subset 2->DIST | 012.051 | 0.1-200:0.01 | — | X1 (polygon) PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 10 |  |  |  | Distance Polygonal\Z1 | Xmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\Z1 | Xmax | Real |  |  | 1 | 0
x012_u002E_052 | Parameter subset 2->DIST | 012.052 | 0.1-200:0.01 | — | X2 (polygon) PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 20 |  |  |  | Distance Polygonal\Z2 | Xmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\Z2 | Xmax | Real |  |  | 1 | 0
x012_u002E_053 | Parameter subset 2->DIST | 012.053 | 0.1-200:0.01 | — | X3 (polygon) PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 30 |  |  |  | Distance Polygonal\Z3 | Xmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\Z3 | Xmax | Real |  |  | 1 | 0
x012_u002E_054 | Parameter subset 2->DIST | 012.054 | 0.1-200:0.01 | — | X4 (polygon) PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 40 |  |  |  | Distance Polygonal\Z4 | Xmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\Z4 | Xmax | Real |  |  | 1 | 0
x012_u002E_055 | Parameter subset 2->DIST | 012.055 | 0.1-200:0.01 | — | R1,PG (polygon) PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 10 |  |  |  | Distance Polygonal\Z1 | REmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\Z1 | REmax | Real |  |  | 1 | 0
x012_u002E_056 | Parameter subset 2->DIST | 012.056 | 0.1-200:0.01 | — | R1,PP (polygon) PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 10 |  |  |  | Distance Polygonal\Z1 | Rmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\Z1 | Rmax | Real |  |  | 1 | 0
x012_u002E_057 | Parameter subset 2->DIST | 012.057 | 0.1-200:0.01 | — | R2,PG (polygon) PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 20 |  |  |  | Distance Polygonal\Z2 | REmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\Z2 | REmax | Real |  |  | 1 | 0
x012_u002E_058 | Parameter subset 2->DIST | 012.058 | 0.1-200:0.01 | — | R2,PP (polygon) PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 20 |  |  |  | Distance Polygonal\Z2 | Rmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\Z2 | Rmax | Real |  |  | 1 | 0
x012_u002E_059 | Parameter subset 2->DIST | 012.059 | 0.1-200:0.01 | — | R3,PG (polygon) PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 30 |  |  |  | Distance Polygonal\Z3 | REmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\Z3 | REmax | Real |  |  | 1 | 0
x012_u002E_060 | Parameter subset 2->DIST | 012.060 | 0.1-200:0.01 | — | R3,PP (polygon) PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 30 |  |  |  | Distance Polygonal\Z3 | Rmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\Z3 | Rmax | Real |  |  | 1 | 0
x012_u002E_061 | Parameter subset 2->DIST | 012.061 | 0.1-200:0.01 | — | R4,PG (polygon) PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 40 |  |  |  | Distance Polygonal\Z4 | REmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\Z4 | REmax | Real |  |  | 1 | 0
x012_u002E_062 | Parameter subset 2->DIST | 012.062 | 0.1-200:0.01 | — | R4,PP (polygon) PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 40 |  |  |  | Distance Polygonal\Z4 | Rmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\Z4 | Rmax | Real |  |  | 1 | 0
x012_u002E_063 | Parameter subset 2->DIST | 012.063 | 40-90:1 | ° | €1 (polygon) PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 75 |  |  |  | Distance Polygonal\Z1 | phi | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\Z1 | phi | Real |  |  | 1 | 0
x012_u002E_064 | Parameter subset 2->DIST | 012.064 | 40-90:1 | ° | €2 (polygon) PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 75 |  |  |  | Distance Polygonal\Z2 | phi | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\Z2 | phi | Real |  |  | 1 | 0
x012_u002E_065 | Parameter subset 2->DIST | 012.065 | 40-90:1 | ° | €3 (polygon) PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 75 |  |  |  | Distance Polygonal\Z3 | phi | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\Z3 | phi | Real |  |  | 1 | 0
x012_u002E_066 | Parameter subset 2->DIST | 012.066 | 40-90:1 | ° | €4 (polygon) PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 75 |  |  |  | Distance Polygonal\Z4 | phi | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\Z4 | phi | Real |  |  | 1 | 0
x073_u002E_086 | Parameter subset 2->DIST | 073.086 | -20-20:1 | ° | ‹1 (polygon) PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 0 |  |  |  | Distance Polygonal\Z1 | beta | Real | -1 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\Z1 | beta | Real |  |  | -1 | 0
x073_u002E_087 | Parameter subset 2->DIST | 073.087 | -20-20:1 | ° | ‹2 (polygon) PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 0 |  |  |  | Distance Polygonal\Z2 | beta | Real | -1 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\Z2 | beta | Real |  |  | -1 | 0
x073_u002E_088 | Parameter subset 2->DIST | 073.088 | -20-20:1 | ° | ‹3 (polygon) PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 0 |  |  |  | Distance Polygonal\Z3 | beta | Real | -1 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\Z3 | beta | Real |  |  | -1 | 0
x073_u002E_089 | Parameter subset 2->DIST | 073.089 | -20-20:1 | ° | ‹4 (polygon) PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 0 |  |  |  | Distance Polygonal\Z4 | beta | Real | -1 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\Z4 | beta | Real |  |  | -1 | 0
x073_u002E_091 | Parameter subset 2->DIST | 073.091 | 0.05-200:0.01 | — | Z1 (circle) PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 10 |  |  |  | Distance Circular\Z1 | Zm | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Circular\Z1 | Zm | Real |  |  | 1 | 0
x073_u002E_092 | Parameter subset 2->DIST | 073.092 | 0.05-200:0.01 | — | Z2 (circle) PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 20 |  |  |  | Distance Circular\Z2 | Zm | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Circular\Z2 | Zm | Real |  |  | 1 | 0
x073_u002E_093 | Parameter subset 2->DIST | 073.093 | 0.05-200:0.01 | — | Z3 (circle) PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 30 |  |  |  | Distance Circular\Z3 | Zm | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Circular\Z3 | Zm | Real |  |  | 1 | 0
x073_u002E_094 | Parameter subset 2->DIST | 073.094 | 0.05-200:0.01 | — | Z4 (circle) PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 40 |  |  |  | Distance Circular\Z4 | Zm | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Circular\Z4 | Zm | Real |  |  | 1 | 0
x073_u002E_090 | Parameter subset 2->DIST | 073.090 | 10-90:1 | ° | €1 (circle) PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 75 | 2 |  |  | Distance Circular\Z1 | arcalpha | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Circular\Z1 | arcalpha | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z1E | arcalpha | Real | 1 | 0
x073_u002E_095 | Parameter subset 2->DIST | 073.095 | 10-90:1 | ° | €2 (circle) PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 75 |  |  |  | Distance Circular\Z2 | arcalpha | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Circular\Z2 | arcalpha | Real |  |  | 1 | 0
x073_u002E_096 | Parameter subset 2->DIST | 073.096 | 10-90:1 | ° | €3 (circle) PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 75 |  |  |  | Distance Circular\Z3 | arcalpha | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Circular\Z3 | arcalpha | Real |  |  | 1 | 0
x073_u002E_099 | Parameter subset 2->DIST | 073.099 | 10-90:1 | ° | €4 (circle) PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 75 |  |  |  | Distance Circular\Z4 | arcalpha | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Circular\Z4 | arcalpha | Real |  |  | 1 | 0
x012_u002E_090 | Parameter subset 2->DIST | 012.090 | No¦0;Yes¦1 |  | Arc comp. circle PS2 | Enum | Parameters__Function_parameters | 0;1 | Real |  | x003_u002E_060 | E | 2 | 0 | 5 |  |  | Distance Circular\Z1 | arcen | Real | 1 | 0 | 4 | Distance Circular;Distance Circular\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Circular\Z1 | arcen | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z1E | arcen | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Circular\Z2 | arcen | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z2 | arcen | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Circular\Z3 | arcen | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z3 | arcen | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Circular\Z4 | arcen | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z4 | arcen | Real | 1 | 0
x012_u002E_073 | Parameter subset 2->DIST | 012.073 | Forward directional¦0;Backward directional¦1;Non-directional¦2 |  | Direction N1 PS2 | Enum | Parameters__Function_parameters | 0;1;2 | Real |  | x003_u002E_060 | E | 2 | 0 | 4 | NE | 2 | Distance Circular\Z1 | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Circular\Z1 | idir | Real |  |  | 1 | 0
[16 empty] | NE | 2 | Distance Circular\Z1E | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\Z1 | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z1 | idir | Real | 1 | 0
[18 empty] | Distance Polygonal\Z1E | idir | Real | 1 | 0
x012_u002E_074 | Parameter subset 2->DIST | 012.074 | Forward directional¦0;Backward directional¦1;Non-directional¦2 |  | Direction N2 PS2 | Enum | Parameters__Function_parameters | 0;1;2 | Real |  | x003_u002E_060 | E | 2 | 0 |  | NE | 2 | Distance Circular\Z2 | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Circular\Z2 | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z2 | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\Z2 | idir | Real |  |  | 1 | 0
x012_u002E_075 | Parameter subset 2->DIST | 012.075 | Forward directional¦0;Backward directional¦1;Non-directional¦2 |  | Direction N3 PS2 | Enum | Parameters__Function_parameters | 0;1;2 | Real |  | x003_u002E_060 | E | 2 | 0 |  | NE | 2 | Distance Circular\Z3 | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Circular\Z3 | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z3 | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\Z3 | idir | Real |  |  | 1 | 0
x012_u002E_076 | Parameter subset 2->DIST | 012.076 | Forward directional¦0;Backward directional¦1;Non-directional¦2 |  | Direction N4 PS2 | Enum | Parameters__Function_parameters | 0;1;2 | Real |  | x003_u002E_060 | E | 2 | 0 |  | NE | 2 | Distance Circular\Z4 | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Circular\Z4 | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z4 | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\Z4 | idir | Real |  |  | 1 | 0
x012_u002E_077 | Parameter subset 2->DIST | 012.077 | Forward directional¦0;Backward directional¦1;Non-directional¦2 |  | Direction N5 PS2 | Enum | Parameters__Function_parameters | 0;1;2 | Real |  | x003_u002E_060 | E | 2 | 0 |  |  |  | Distance Circular\Directional | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Directional;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Circular\Directional | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Directional | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Directional;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\Directional | idir | Real |  |  | 1 | 0
x012_u002E_078 | Parameter subset 2->DIST | 012.078 | 0-10:0.001;Blocked=10.002 | s | t1 PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 0 | 4 | SE | 10 | Distance Circular\T1 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Circular\T1 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Circular\T1 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
[16 empty] | SE | 10 | Distance Polygonal\T1 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Polygonal\T1 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Polygonal\T1 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
x012_u002E_079 | Parameter subset 2->DIST | 012.079 | 0-10:0.001;Blocked=10.002 | s | t2 PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 | 4 | SE | 10 | Distance Circular\T2 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Circular\T2 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Circular\T2 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
[16 empty] | SE | 10 | Distance Polygonal\T2 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Polygonal\T2 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Polygonal\T2 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
x012_u002E_080 | Parameter subset 2->DIST | 012.080 | 0-10:0.001;Blocked=10.002 | s | t3 PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 2 | 4 | SE | 10 | Distance Circular\T3 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Circular\T3 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Circular\T3 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
[16 empty] | SE | 10 | Distance Polygonal\T3 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Polygonal\T3 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Polygonal\T3 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
x012_u002E_081 | Parameter subset 2->DIST | 012.081 | 0-10:0.001;Blocked=10.002 | s | t4 PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 3 | 4 | SE | 10 | Distance Circular\T4 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Circular\T4 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Circular\T4 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
[16 empty] | SE | 10 | Distance Polygonal\T4 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Polygonal\T4 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Polygonal\T4 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
x012_u002E_082 | Parameter subset 2->DIST | 012.082 | 0-10:0.001;Blocked=10.002 | s | t5 PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 4 | 4 | SE | 10 | Distance Circular\T5 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Circular\T5 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Circular\T5 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
[16 empty] | SE | 10 | Distance Polygonal\T5 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Polygonal\T5 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Polygonal\T5 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
x012_u002E_083 | Parameter subset 2->DIST | 012.083 | 0-10:0.001;Blocked=10.002 | s | t6 PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 5 | 4 | SE | 10 | Distance Circular\T6 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Circular\T6 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Circular\T6 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
[16 empty] | SE | 10 | Distance Polygonal\T6 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Polygonal\T6 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Polygonal\T6 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
x012_u002E_085 | Parameter subset 2->DIST | 012.085 | 1-450:0.01 |  | kze,PP HSR PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1.2 | 3 |  |  | Distance Circular\Z1E | kZ | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z1E;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Circular\Z1E | kZ | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z1E | kX | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z1E;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\Z1E | kX | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z1E | kR | Real | 1 | 0
x015_u002E_015 | Parameter subset 2->PSIG | 015.015 | No¦0;Yes¦1 |  | Enable PS2 | Enum | Parameters__Function_parameters | 0;1 | String |  | x003_u002E_060 | E | 2 | 0 | 2 |  |  | Distance Circular\PSIG Connect | aDipset | String |  |  | 2 | Distance Circular;Distance Circular\PSIG Connect;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Circular\PSIG Connect | aDipset | String
[18 empty] | Distance Polygonal\PSIG Connect | aDipset | String |  |  |  | Distance Polygonal;Distance Polygonal\PSIG Connect;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\PSIG Connect | aDipset | String
x024_u002E_000 | Parameter subset 2->PSIG | 024.000 | Without¦0;Dir.trans.trip.under¦1;PUTT¦2;Zone extension¦3;Release scheme¦4;Blocking scheme¦5;DC loop operat. mode¦6;Reverse interlocking¦7;Direction comparison¦8 |  | Operating mode PS2 | Enum | Parameters__Function_parameters | ;DIRECT = TRIP;PUTT = TRIP;POTT = TRIP;COMP_RELEASE = TRIP;COMP_BLOCK = TRIP;COMP_PILOT = TRIP; | String |  | x003_u002E_060 | E | 2 | PUTT = TRIP | 4 |  |  | Distance Circular\PSIG Receive | sLogic | String |  |  | 2 | Distance Circular;Distance Circular\PSIG Receive;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Circular\PSIG Receive | sLogic | String
[18 empty] | Distance Circular\PSIG Send | sLogic | String |  |  |  | Distance Polygonal;Distance Polygonal\PSIG Receive;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\PSIG Receive | sLogic | String
[18 empty] | Distance Polygonal\PSIG Receive | sLogic | String
[18 empty] | Distance Polygonal\PSIG Send | sLogic | String
x024_u002E_003 | Parameter subset 2->PSIG | 024.003 | 0-10:0.001;Blocked=10.002 | s | Tripping time PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 0.08 | 4 | SE | 10 | Distance Circular\PSIG T | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\PSIG T;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Circular\PSIG T | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Circular\PSIG T | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
[16 empty] | SE | 10 | Distance Polygonal\PSIG T | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\PSIG T;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 | 2 | Distance Polygonal\PSIG T | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Polygonal\PSIG T | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
x024_u002E_001 | Parameter subset 2->PSIG | 024.001 | 0-10:0.001 | s | Release t. send PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 0.25 | 2 |  |  | Distance Circular\PSIG T Reset | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\PSIG T Reset;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Circular\PSIG T Reset | Tdelay | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\PSIG T Reset | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\PSIG T Reset;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;2 |  | Distance Polygonal\PSIG T Reset | Tdelay | Real |  |  | 1 | 0
x073_u002E_098 | Parameter subset 2->DTOC | 073.098 | No¦0;Yes¦1 |  | Enable PS2 | Enum | Parameters__Function_parameters | 1;0 | Real |  | x056_u002E_008;x003_u002E_060 | E;E | 0;2 | 1 | 12 |  |  | Overcurrent\I> | outserv | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 12 | Overcurrent\I> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\I>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\I>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\I>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\I>>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\I>>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\I>>>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\IN> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\IN> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\IN>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\IN>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\IN>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\IN>>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\IN>>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\IN>>>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\Ineg> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\Ineg> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\Ineg>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\Ineg>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\Ineg>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\Ineg>>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\Ineg>>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\Ineg>>>> | outserv | Real |  |  | 1 | 0
x073_u002E_007 | Parameter subset 2->DTOC | 073.007 | 0.1-20:0.01 | Inom | I> PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 |  |  |  | Overcurrent\I> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\I> | Ipset | Real |  |  | 1 | 0
x073_u002E_008 | Parameter subset 2->DTOC | 073.008 | 0.1-20:0.01 | Inom | I>> PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 |  |  |  | Overcurrent\I>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\I>> | Ipset | Real |  |  | 1 | 0
x073_u002E_009 | Parameter subset 2->DTOC | 073.009 | 0.1-20:0.01 | Inom | I>>> PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 |  |  |  | Overcurrent\I>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\I>>> | Ipset | Real |  |  | 1 | 0
x073_u002E_010 | Parameter subset 2->DTOC | 073.010 | 0.1-20:0.01 | Inom | I>>>> PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 |  |  |  | Overcurrent\I>>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\I>>>> | Ipset | Real |  |  | 1 | 0
x073_u002E_019 | Parameter subset 2->DTOC | 073.019 | 0-30:0.001;Blocked=30.002 | s | tI> PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 | SE | 30 | Overcurrent\I> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Overcurrent\I> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\I> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x073_u002E_020 | Parameter subset 2->DTOC | 073.020 | 0-30:0.001;Blocked=30.002 | s | tI>> PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 | SE | 30 | Overcurrent\I>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Overcurrent\I>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\I>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x073_u002E_021 | Parameter subset 2->DTOC | 073.021 | 0-30:0.001;Blocked=30.002 | s | tI>>> PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 | SE | 30 | Overcurrent\I>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Overcurrent\I>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\I>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x073_u002E_022 | Parameter subset 2->DTOC | 073.022 | 0-30:0.001;Blocked=30.002 | s | tI>>>> PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 | SE | 30 | Overcurrent\I>>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Overcurrent\I>>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\I>>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x073_u002E_011 | Parameter subset 2->DTOC | 073.011 | 0.1-20:0.01 | Inom | Ineg> PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 |  |  |  | Overcurrent\IN> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\IN> | Ipset | Real |  |  | 1 | 0
x073_u002E_012 | Parameter subset 2->DTOC | 073.012 | 0.1-20:0.01 | Inom | Ineg>> PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 |  |  |  | Overcurrent\IN>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\IN>> | Ipset | Real |  |  | 1 | 0
x073_u002E_013 | Parameter subset 2->DTOC | 073.013 | 0.1-20:0.01 | Inom | Ineg>>> PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 |  |  |  | Overcurrent\IN>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\IN>>> | Ipset | Real |  |  | 1 | 0
x073_u002E_014 | Parameter subset 2->DTOC | 073.014 | 0.1-20:0.01 | Inom | Ineg>>>> PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 |  |  |  | Overcurrent\IN>>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\IN>>>> | Ipset | Real |  |  | 1 | 0
x073_u002E_023 | Parameter subset 2->DTOC | 073.023 | 0-30:0.001;Blocked=30.002 | s | tIneg> PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 | SE | 30 | Overcurrent\IN> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Overcurrent\IN> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\IN> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x073_u002E_024 | Parameter subset 2->DTOC | 073.024 | 0-30:0.001;Blocked=30.002 | s | tIneg>> PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 | SE | 30 | Overcurrent\IN>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Overcurrent\IN>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\IN>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x073_u002E_025 | Parameter subset 2->DTOC | 073.025 | 0-30:0.001;Blocked=30.002 | s | tIneg>>> PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 | SE | 30 | Overcurrent\IN>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Overcurrent\IN>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\IN>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x073_u002E_026 | Parameter subset 2->DTOC | 073.026 | 0-30:0.001;Blocked=30.002 | s | tIneg>>>> PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 | SE | 30 | Overcurrent\IN>>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Overcurrent\IN>>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\IN>>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x073_u002E_015 | Parameter subset 2->DTOC | 073.015 | 0.1-20:0.01 | Inom | IN> PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 |  |  |  | Overcurrent\Ineg> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\Ineg> | Ipset | Real |  |  | 1 | 0
x073_u002E_016 | Parameter subset 2->DTOC | 073.016 | 0.1-20:0.01 | Inom | IN>> PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 |  |  |  | Overcurrent\Ineg>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\Ineg>> | Ipset | Real |  |  | 1 | 0
x073_u002E_017 | Parameter subset 2->DTOC | 073.017 | 0.1-20:0.01 | Inom | IN>>> PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 |  |  |  | Overcurrent\Ineg>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\Ineg>>> | Ipset | Real |  |  | 1 | 0
x073_u002E_018 | Parameter subset 2->DTOC | 073.018 | 0.1-20:0.01 | Inom | IN>>>> PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 |  |  |  | Overcurrent\Ineg>>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\Ineg>>>> | Ipset | Real |  |  | 1 | 0
x073_u002E_027 | Parameter subset 2->DTOC | 073.027 | 0-30:0.001;Blocked=30.002 | s | tIN> PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 | SE | 30 | Overcurrent\Ineg> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Overcurrent\Ineg> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\Ineg> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x073_u002E_028 | Parameter subset 2->DTOC | 073.028 | 0-30:0.001;Blocked=30.002 | s | tIN>> PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 | SE | 30 | Overcurrent\Ineg>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Overcurrent\Ineg>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\Ineg>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x073_u002E_029 | Parameter subset 2->DTOC | 073.029 | 0-30:0.001;Blocked=30.002 | s | tIN>>> PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 | SE | 30 | Overcurrent\Ineg>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Overcurrent\Ineg>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\Ineg>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x073_u002E_030 | Parameter subset 2->DTOC | 073.030 | 0-30:0.001;Blocked=30.002 | s | tIN>>>> PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 | SE | 30 | Overcurrent\Ineg>>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Overcurrent\Ineg>>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\Ineg>>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x073_u002E_000 | Parameter subset 2->IDMT | 073.000 | No¦0;Yes¦1 |  | Enable P PS2 | Enum | Parameters__Function_parameters | 1;0 | Real |  | x056_u002E_009;x003_u002E_060 | E;E | 0;2 | 1 |  |  |  | Overcurrent\IDMT P | outserv | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\IDMT P | outserv | Real |  |  | 1 | 0
x073_u002E_050 | Parameter subset 2->IDMT | 073.050 | 0.1-4:0.01 | Inom | Iref,P PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 |  |  |  | Overcurrent\IDMT P | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\IDMT P | Ipset | Real |  |  | 1 | 0
x073_u002E_056 | Parameter subset 2->IDMT | 073.056 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Characterist. P PS2 | Enum | Parameters__Function_parameters | Definite Time;IEC 255-3 Standard Inverse;IEC 255-3 Very Inverse;IEC 255-3 Extremly Inverse;IEC 255-3 Long-Time Inverse;IEEE C37.112 Moderately Inverse;IEEE C37.112 Very Inverse;IEEE C37.112 Extremely Inverse;ANSI Normally Inverse;ANSI Short-Time Inverse;ANSI Long-Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | [8 empty] | Overcurrent\IDMT P | pcharac |  |  |  |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\IDMT P | pcharac
x073_u002E_053 | Parameter subset 2->IDMT | 073.053 | 0.01-10:0.01 |  | Ch. factor kt,P PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 |  |  |  | Overcurrent\IDMT P | Tpset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\IDMT P | Tpset | Real |  |  | 1 | 0
x073_u002E_059 | Parameter subset 2->IDMT | 073.059 | Without delay¦0;Delayed as per char.¦1 |  | Reset P PS2 | Enum | Parameters__Function_parameters | 0;1 | Real | 3 | x003_u002E_060;x073_u002E_056 | E;SW | 2;IEEE | 0 |  |  |  | Overcurrent\IDMT P | resetdis | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\IDMT P | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x072_u002E_056 | E;SW | 2;ANSI |  |  |  |  | Overcurrent\IDMT P | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | 2 |  |  |  |  | Overcurrent\IDMT P | resetdis | Real | 0 | 0
x073_u002E_062 | Parameter subset 2->IDMT | 073.062 | Forward directional¦0;Backward directional¦1;Non-directional¦2 |  | Direction P PS2 | Enum | Parameters__Function_parameters | 1;2;0 | Real |  | x003_u002E_060 | E | 2 | 1 |  |  |  | Overcurrent\IDMT P | idir | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\IDMT P | idir | Real |  |  | 1 | 0
x073_u002E_001 | Parameter subset 2->IDMT | 073.001 | No¦0;Yes¦1 |  | Enable neg. PS2 | Enum | Parameters__Function_parameters | 1;0 | Real |  | x056_u002E_009;x003_u002E_060 | E;E | 0;2 | 1 |  |  |  | Overcurrent\IDMT neg | outserv | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\IDMT neg | outserv | Real |  |  | 1 | 0
x073_u002E_051 | Parameter subset 2->IDMT | 073.051 | 0.1-4:0.01 | Inom | Iref,neg PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 |  |  |  | Overcurrent\IDMT neg | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\IDMT neg | Ipset | Real |  |  | 1 | 0
x073_u002E_057 | Parameter subset 2->IDMT | 073.057 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Character. neg. PS2 | Enum | Parameters__Function_parameters | Definite Time;IEC 255-3 Standard Inverse;IEC 255-3 Very Inverse;IEC 255-3 Extremly Inverse;IEC 255-3 Long-Time Inverse;IEEE C37.112 Moderately Inverse;IEEE C37.112 Very Inverse;IEEE C37.112 Extremely Inverse;ANSI Normally Inverse;ANSI Short-Time Inverse;ANSI Long-Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | [8 empty] | Overcurrent\IDMT neg | pcharac |  |  |  |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\IDMT neg | pcharac
x073_u002E_054 | Parameter subset 2->IDMT | 073.054 | 0.01-10:0.01 |  | Factor kt,neg PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 |  |  |  | Overcurrent\IDMT neg | Tpset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\IDMT neg | Tpset | Real |  |  | 1 | 0
x073_u002E_060 | Parameter subset 2->IDMT | 073.060 | Without delay¦0;Delayed as per char.¦1 |  | Reset neg. PS2 | Enum | Parameters__Function_parameters | 0;1 | Real | 3 | x003_u002E_060;x073_u002E_057 | E;SW | 2;IEEE | 0 |  |  |  | Overcurrent\IDMT neg | resetdis | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\IDMT neg | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x073_u002E_057 | E;SW | 2;ANSI |  |  |  |  | Overcurrent\IDMT neg | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | 2 |  |  |  |  | Overcurrent\IDMT neg | resetdis | Real | 0 | 0
x073_u002E_063 | Parameter subset 2->IDMT | 073.063 | Forward directional¦0;Backward directional¦1;Non-directional¦2 |  | Direction neg. PS2 | Enum | Parameters__Function_parameters | 1;2;0 | Real |  | x003_u002E_060 | E | 2 | 1 |  |  |  | Overcurrent\IDMT neg | idir | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\IDMT neg | idir | Real |  |  | 1 | 0
x073_u002E_002 | Parameter subset 2->IDMT | 073.002 | No¦0;Yes¦1 |  | Enable N PS2 | Enum | Parameters__Function_parameters | 1;0 | Real |  | x056_u002E_009;x003_u002E_060 | E;E | 0;2 | 1 |  |  |  | Overcurrent\IDMT N | outserv | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\IDMT N | outserv | Real |  |  | 1 | 0
x073_u002E_052 | Parameter subset 2->IDMT | 073.052 | 0.1-4:0.01 | Inom | Iref,N PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 |  |  |  | Overcurrent\IDMT N | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\IDMT N | Ipset | Real |  |  | 1 | 0
x073_u002E_058 | Parameter subset 2->IDMT | 073.058 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Characterist. N PS2 | Enum | Parameters__Function_parameters | Definite Time;IEC 255-3 Standard Inverse;IEC 255-3 Very Inverse;IEC 255-3 Extremly Inverse;IEC 255-3 Long-Time Inverse;IEEE C37.112 Moderately Inverse;IEEE C37.112 Very Inverse;IEEE C37.112 Extremely Inverse;ANSI Normally Inverse;ANSI Short-Time Inverse;ANSI Long-Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | [8 empty] | Overcurrent\IDMT N | pcharac |  |  |  |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\IDMT N | pcharac
x073_u002E_055 | Parameter subset 2->IDMT | 073.055 | 0.01-10:0.01 |  | Factor kt,N PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 |  |  |  | Overcurrent\IDMT N | Tpset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\IDMT N | Tpset | Real |  |  | 1 | 0
x073_u002E_061 | Parameter subset 2->IDMT | 073.061 | Without delay¦0;Delayed as per char.¦1 |  | Reset N PS2 | Enum | Parameters__Function_parameters | 0;1 | Real | 3 | x003_u002E_060;x073_u002E_058 | E;SW | 2;IEEE | 0 |  |  |  | Overcurrent\IDMT neg | resetdis | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\IDMT neg | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x073_u002E_058 | E;SW | 2;ANSI |  |  |  |  | Overcurrent\IDMT neg | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | 2 |  |  |  |  | Overcurrent\IDMT neg | resetdis | Real | 0 | 0
x073_u002E_064 | Parameter subset 2->IDMT | 073.064 | Forward directional¦0;Backward directional¦1;Non-directional¦2 |  | Direction N PS2 | Enum | Parameters__Function_parameters | 1;2;0 | Real |  | x003_u002E_060 | E | 2 | 1 |  |  |  | Overcurrent\IDMT N | idir | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Overcurrent\IDMT N | idir | Real |  |  | 1 | 0
x077_u002E_000 | Parameter subset 2->V<> | 077.000 | No¦0;Yes¦1 |  | Enable PS2 | Enum | Parameters__Function_parameters | 1;0 | Real |  | x056_u002E_010;x003_u002E_060 | E;E | 0;2 | 1 |  |  |  | Voltage | outserv | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 |  | Voltage | outserv | Real |  |  | 1 | 0
x077_u002E_001 | Parameter subset 2->V<> | 077.001 | Delta¦0;Star¦1 |  | Operating mode PS2 | Enum | Parameters__Function_parameters | 0;1 | Real |  | x077_u002E_000;x003_u002E_060 | E;E | 0;2 | 0 | 4 | E | 1 | Voltage\V> | outserv | Real | 0 | 1
[16 empty] | E | 1 | Voltage\V>> | outserv | Real | 0 | 1
[16 empty] | E | 1 | Voltage\V< | outserv | Real | 0 | 1
[16 empty] | E | 1 | Voltage\V<< | outserv | Real | 0 | 1
x077_u002E_003 | Parameter subset 2->V<> | 077.003 | 0.2-1.5:0.01;Blocked=1.52 | Vnom(/©3) | V> PS2 | Real | Parameters__Function_parameters |  |  |  | x077_u002E_001;x003_u002E_060 | E;E | 0;2 | 1.1 | 3 | SE | 1.5 | Voltage\V> | Uset | Real | 1 | 0 |  | x077_u002E_001;x003_u002E_060 |  |  | E;E | 0;2 | 2 | Voltage\V> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V> | outserv | Real | 0 | 0 | [7 empty] | Voltage\V> | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\V> | outserv | Real | 0 | 1
x077_u002E_004 | Parameter subset 2->V<> | 077.004 | 0.2-1.5:0.01;Blocked=1.52 | Vnom(/©3) | V>> PS2 | Real | Parameters__Function_parameters |  |  |  | x077_u002E_001;x003_u002E_060 | E;E | 0;2 | 1.1 | 3 | SE | 1.5 | Voltage\V>> | Uset | Real | 1 | 0 |  | x077_u002E_001;x003_u002E_060 |  |  | E;E | 0;2 | 2 | Voltage\V>> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\V>> | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\V>> | outserv | Real | 0 | 1
x077_u002E_005 | Parameter subset 2->V<> | 077.005 | 0-100:0.01;Blocked=100.02 | s | tV> PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 | SE | 100 | Voltage\V> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Voltage\V> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x077_u002E_006 | Parameter subset 2->V<> | 077.006 | 0-100:0.01;Blocked=100.02 | s | tV>> PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 | SE | 100 | Voltage\V>> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Voltage\V>> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V>> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x077_u002E_007 | Parameter subset 2->V<> | 077.007 | 0.2-1.5:0.01;Blocked=1.52 | Vnom(/©3) | V< PS2 | Real | Parameters__Function_parameters |  |  |  | x077_u002E_001;x003_u002E_060 | E;E | 0;2 | 0.8 | 3 | SE | 1.5 | Voltage\V< | Uset | Real | 1 | 0 |  | x077_u002E_001;x003_u002E_060 |  |  | E;E | 0;2 | 2 | Voltage\V< | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V< | outserv | Real | 0 | 0 | [7 empty] | Voltage\V< | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\V< | outserv | Real | 0 | 1
x077_u002E_008 | Parameter subset 2->V<> | 077.008 | 0.2-1.5:0.01;Blocked=1.52 | Vnom(/©3) | V<< PS2 | Real | Parameters__Function_parameters |  |  |  | x077_u002E_001;x003_u002E_060 | E;E | 0;2 | 0.8 | 3 | SE | 1.5 | Voltage\V<< | Uset | Real | 1 | 0 |  | x077_u002E_001;x003_u002E_060 |  |  | E;E | 0;2 | 2 | Voltage\V<< | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V<< | outserv | Real | 0 | 0 | [7 empty] | Voltage\V<< | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\V<< | outserv | Real | 0 | 1
x077_u002E_009 | Parameter subset 2->V<> | 077.009 | 0-100:0.01;Blocked=100.02 | s | tV< PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 | SE | 100 | Voltage\V< | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Voltage\V< | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V< | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x077_u002E_010 | Parameter subset 2->V<> | 077.010 | 0-100:0.01;Blocked=100.02 | s | tV<< PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 | SE | 100 | Voltage\V<< | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Voltage\V<< | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V<< | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x077_u002E_015 | Parameter subset 2->V<> | 077.015 | 0.2-1.5:0.01;Blocked=1.52 | Vnom/©3 | Vpos> PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1.1 | 3 | SE | 1.5 | Voltage\Vpos> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Voltage\Vpos> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos> | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vpos> | outserv | Real | 0 | 1
x077_u002E_016 | Parameter subset 2->V<> | 077.016 | 0.2-1.5:0.01;Blocked=1.52 | Vnom/©3 | Vpos>> PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1.1 | 3 | SE | 1.5 | Voltage\Vpos>> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Voltage\Vpos>> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos>> | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vpos>> | outserv | Real | 0 | 1
x077_u002E_017 | Parameter subset 2->V<> | 077.017 | 0-100:0.01;Blocked=100.02 | s | tVpos> PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 | SE | 100 | Voltage\Vpos> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Voltage\Vpos> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vpos> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x077_u002E_018 | Parameter subset 2->V<> | 077.018 | 0-100:0.01;Blocked=100.02 | s | tVpos>> PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 | SE | 100 | Voltage\Vpos>> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Voltage\Vpos>> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vpos>> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x077_u002E_019 | Parameter subset 2->V<> | 077.019 | 0.2-1.5:0.01;Blocked=1.52 | Vnom/©3 | Vpos< PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 0.8 | 3 | SE | 1.5 | Voltage\Vpos< | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Voltage\Vpos< | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos< | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos< | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vpos< | outserv | Real | 0 | 1
x077_u002E_020 | Parameter subset 2->V<> | 077.020 | 0.2-1.5:0.01;Blocked=1.52 | Vnom/©3 | Vpos<< PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 0.8 | 3 | SE | 1.5 | Voltage\Vpos<< | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Voltage\Vpos<< | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos<< | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos<< | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vpos<< | outserv | Real | 0 | 1
x077_u002E_021 | Parameter subset 2->V<> | 077.021 | 0-100:0.01;Blocked=100.02 | s | tVpos< PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 | SE | 100 | Voltage\Vpos< | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Voltage\Vpos< | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vpos< | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x077_u002E_022 | Parameter subset 2->V<> | 077.022 | 0-100:0.01;Blocked=100.02 | s | tVpos<< PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 | SE | 100 | Voltage\Vpos<< | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Voltage\Vpos<< | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vpos<< | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x077_u002E_023 | Parameter subset 2->V<> | 077.023 | 0.2-1.5:0.01;Blocked=1.52 | Vnom/©3 | Vneg> PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1.52 | 3 | SE | 1.5 | Voltage\Vneg> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Voltage\Vneg> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vneg> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vneg> | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vneg> | outserv | Real | 0 | 1
x077_u002E_024 | Parameter subset 2->V<> | 077.024 | 0.2-1.5:0.01;Blocked=1.52 | Vnom/©3 | Vneg>> PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1.52 | 3 | SE | 1.5 | Voltage\Vneg>> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Voltage\Vneg>> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vneg>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vneg>> | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vneg>> | outserv | Real | 0 | 1
x077_u002E_025 | Parameter subset 2->V<> | 077.025 | 0-100:0.01;Blocked=100.02 | s | tVneg> PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 | SE | 100 | Voltage\Vneg> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Voltage\Vneg> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vneg> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x077_u002E_026 | Parameter subset 2->V<> | 077.026 | 0-100:0.01;Blocked=100.02 | s | tVneg>> PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 | SE | 100 | Voltage\Vneg>> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Voltage\Vneg>> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vneg>> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x077_u002E_011 | Parameter subset 2->V<> | 077.011 | 0.02-1:0.01;Blocked=1.02 | Vnom(/©3) | VNG> PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1.02 | 3 | SE | 1 | Voltage\VNG> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Voltage\VNG> | outserv | Real | E | 1 | 0 | 1.02
[16 empty] | SE | 1 | Voltage\VNG> | outserv | Real | 0 | 0 | [7 empty] | Voltage\VNG> | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1 | Voltage\VNG> | outserv | Real | 0 | 1
x077_u002E_012 | Parameter subset 2->V<> | 077.012 | 0.02-1:0.01;Blocked=1.02 | Vnom(/©3) | VNG>> PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1.02 | 3 | SE | 1 | Voltage\VNG>> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Voltage\VNG>> | outserv | Real | E | 1 | 0 | 1.02
[16 empty] | SE | 1 | Voltage\VNG>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\VNG>> | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1 | Voltage\VNG>> | outserv | Real | 0 | 1
x077_u002E_013 | Parameter subset 2->V<> | 077.013 | 0-100:0.01;Blocked=100.02 | s | tVNG> PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 | SE | 100 | Voltage\VNG> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Voltage\VNG> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\VNG> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x077_u002E_014 | Parameter subset 2->V<> | 077.014 | 0-100:0.01;Blocked=100.02 | s | tVNG>> PS2 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 2 | 1 | 2 | SE | 100 | Voltage\VNG>> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 2 | 2 | Voltage\VNG>> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\VNG>> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x010_u002E_094 | Parameter subset 3->DIST | 010.094 | 0.1-20:0.01 | Inom | I>> PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 |  |  | Distance Circular\Starting | IMM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Circular\Starting | IMM | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | IMM | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Polygonal\Starting | IMM | Real |  |  | 1 | 0
x011_u002E_008 | Parameter subset 3->DIST | 011.008 | 0.1-1:0.01 | Inom | I> (Ibl) high r. PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 0.2 | 2 |  |  | Distance Circular\Starting | IM1 | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Circular\Starting | IM1 | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | IM1 | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Polygonal\Starting | IM1 | Real |  |  | 1 | 0
x011_u002E_007 | Parameter subset 3->DIST | 011.007 | W/o V< starting¦0;With V< start. PG¦1;With V< start.PG,PP¦2 |  | Operat. mode V< PS3 | Enum | Parameters__Function_parameters | 0;1;2 | Real |  | x003_u002E_060 | E | 3 | 2 | 8 | E | 0 | Distance Circular\Starting | iopt_u | Real | 0 | 0 | 4 | Distance Circular;Distance Circular\Starting;x003_u002E_060 | outserv;iopt_u | Real | E;E;E | 0;0;3 | [7 empty] | 0
[16 empty] | E | 0 | Distance Polygonal\Starting | iopt_u | Real | 0 | 0 |  | Distance Circular;Distance Circular\Starting;x003_u002E_060 | outserv;iopt_u | Real | E;E;E | 0;1;3 | 2 | Distance Circular\Starting | iVOpMode | Real | 0 | 0 | 0 | 1
[16 empty] | NE | 0 | Distance Circular\Starting | iopt_u | Real | 0 | 1 | [7 empty] | Distance Circular\Starting | iVOpMode | Real | 0 | 1 | 0 | 2
[16 empty] | NE | 0 | Distance Polygonal\Starting | iopt_u | Real | 0 | 1 |  | Distance Polygonal;Distance Polygonal\Starting;x003_u002E_060 | outserv;iopt_u | Real | E;E;E | 0;0;3 | [7 empty] | 0
[16 empty] | E | 1 | Distance Circular\Starting | iVOpMode | Real | 0 | 0 |  | Distance Polygonal;Distance Polygonal\Starting;x003_u002E_060 | outserv;iopt_u | Real | E;E;E | 0;1;3 | 2 | Distance Polygonal\Starting | iVOpMode | Real | 0 | 0 | 0 | 1
[16 empty] | E | 1 | Distance Polygonal\Starting | iVOpMode | Real | 0 | 0 | [7 empty] | Distance Polygonal\Starting | iVOpMode | Real | 0 | 1 | 0 | 2
[16 empty] | E | 2 | Distance Circular\Starting | iVOpMode | Real | 0 | 1
[16 empty] | E | 2 | Distance Polygonal\Starting | iVOpMode | Real | 0 | 1
x011_u002E_009 | Parameter subset 3->DIST | 011.009 | 0.1-0.9:0.01 | Vnom(/©3) | V< PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 0.7 | 2 |  |  | Distance Circular\Starting | Um | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Circular\Starting | Um | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | Um | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Polygonal\Starting | Um | Real |  |  | 1 | 0
x011_u002E_006 | Parameter subset 3->DIST | 011.006 | W/o Z< starting¦0;With Z< starting P-G¦1;With Z< start.PG,PP¦2 |  | Operat. mode Z< PS3 | Enum | Parameters__Function_parameters | 0;1;2 | Real |  | x003_u002E_060 | E | 3 | 2 | 8 | E | 0 | Distance Circular\Starting | iopt_z | Real | 0 | 0 | 4 | Distance Circular;Distance Circular\Starting;x003_u002E_060 | outserv;iopt_z | Real | E;E;E | 0;0;3 | [7 empty] | 0
[16 empty] | E | 0 | Distance Polygonal\Starting | iopt_z | Real | 0 | 0 |  | Distance Circular;Distance Circular\Starting;x003_u002E_060 | outserv;iopt_z | Real | E;E;E | 0;1;3 | 2 | Distance Circular\Starting | iZOpMode | Real | 0 | 0 | 0 | 1
[16 empty] | NE | 0 | Distance Circular\Starting | iopt_z | Real | 0 | 1 | [7 empty] | Distance Circular\Starting | iZOpMode | Real | 0 | 1 | 0 | 2
[16 empty] | NE | 0 | Distance Polygonal\Starting | iopt_z | Real | 0 | 1 |  | Distance Polygonal;Distance Polygonal\Starting;x003_u002E_060 | outserv;iopt_z | Real | E;E;E | 0;0;3 | [7 empty] | 0
[16 empty] | E | 1 | Distance Circular\Starting | iZOpMode | Real | 0 | 0 |  | Distance Polygonal;Distance Polygonal\Starting;x003_u002E_060 | outserv;iopt_z | Real | E;E;E | 0;1;3 | 2 | Distance Polygonal\Starting | iZOpMode | Real | 0 | 0 | 0 | 1
[16 empty] | E | 1 | Distance Polygonal\Starting | iZOpMode | Real | 0 | 0 | [7 empty] | Distance Polygonal\Starting | iZOpMode | Real | 0 | 1 | 0 | 2
[16 empty] | E | 2 | Distance Circular\Starting | iZOpMode | Real | 0 | 1
[16 empty] | E | 2 | Distance Polygonal\Starting | iZOpMode | Real | 0 | 1
x010_u002E_090 | Parameter subset 3->DIST | 010.090 | 0.1-300:0.01 | — | Xfw PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 10 | 2 |  |  | Distance Circular\Starting | Xfw | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Circular\Starting | Xfw | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | Xfw | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Polygonal\Starting | Xfw | Real |  |  | 1 | 0
x010_u002E_091 | Parameter subset 3->DIST | 010.091 | 0.1-300:0.01 | — | Rfw,PG PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 10 | 2 |  |  | Distance Circular\Starting | RfPG | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Circular\Starting | RfPG | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | RfPG | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Polygonal\Starting | RfPG | Real |  |  | 1 | 0
x010_u002E_092 | Parameter subset 3->DIST | 010.092 | 0.1-300:0.01 | — | Rfw,PP PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 10 | 2 |  |  | Distance Circular\Starting | RfPP | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Circular\Starting | RfPP | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | RfPP | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Polygonal\Starting | RfPP | Real |  |  | 1 | 0
x011_u002E_003 | Parameter subset 3->DIST | 011.003 | 15-65:1 | ° | ß PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 30 | 2 |  |  | Distance Circular\Starting | Beta | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Circular\Starting | Beta | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | Beta | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Polygonal\Starting | Beta | Real |  |  | 1 | 0
x010_u002E_103 | Parameter subset 3->DIST | 010.103 | 0-300:0.01 | — | Zfw,PG PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 10 | 2 |  |  | Distance Circular\Starting | ZfPG | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Circular\Starting | ZfPG | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | ZfPG | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Polygonal\Starting | ZfPG | Real |  |  | 1 | 0
x010_u002E_107 | Parameter subset 3->DIST | 010.107 | 0-300:0.01 | — | Zfw,PP PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 10 | 2 |  |  | Distance Circular\Starting | ZfPP | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Circular\Starting | ZfPP | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | ZfPP | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Polygonal\Starting | ZfPP | Real |  |  | 1 | 0
x010_u002E_093 | Parameter subset 3->DIST | 010.093 | 0.1-4:0.01 |  | Zbw/Zfw PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 0.5 | 2 |  |  | Distance Circular\Starting | ZbwZfw | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Circular\Starting | ZbwZfw | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | ZbwZfw | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Polygonal\Starting | ZbwZfw | Real |  |  | 1 | 0
x010_u002E_095 | Parameter subset 3->DIST | 010.095 | 0.1-2:0.01 | Inom | IN> high range PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 0.2 | 2 |  |  | Distance Circular\Starting | INM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Circular\Starting | INM | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | INM | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Polygonal\Starting | INM | Real |  |  | 1 | 0
x010_u002E_097 | Parameter subset 3->DIST | 010.097 | 0-0.5:0.001 | s | tIN> PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 0.1 | 2 |  |  | Distance Circular\Starting | tINM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Circular\Starting | tINM | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | tINM | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Polygonal\Starting | tINM | Real |  |  | 1 | 0
x010_u002E_096 | Parameter subset 3->DIST | 010.096 | 0.02-1:0.01 | Vnom | VNG> PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 0.1 | 2 |  |  | Distance Circular\Starting | VNGM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Circular\Starting | VNGM | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | VNGM | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Polygonal\Starting | VNGM | Real |  |  | 1 | 0
x011_u002E_002 | Parameter subset 3->DIST | 011.002 | 0.2-1:0.01 | Vnom | VNG>> PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 0.5 | 2 |  |  | Distance Circular\Starting | VNGMM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Circular\Starting | VNGMM | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | VNGMM | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Polygonal\Starting | VNGMM | Real |  |  | 1 | 0
x011_u002E_001 | Parameter subset 3->DIST | 011.001 | 0-60:0.001 | s | tVNG>> PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 |  |  | Distance Circular\Starting | tVNGMM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Circular\Starting | tVNGMM | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | tVNGMM | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Polygonal\Starting | tVNGMM | Real |  |  | 1 | 0
x013_u002E_037 | Parameter subset 3->DIST | 013.037 | 0-8:0.01 |  | Abs. value kG PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 |  |  | Distance Circular\Polarisation | k0 | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Circular\Polarisation | k0 | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Polarisation | k0 | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Polygonal\Polarisation | k0 | Real |  |  | 1 | 0
x013_u002E_036 | Parameter subset 3->DIST | 013.036 | -180-180:1 | ° | Angle kG PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 0 | 2 |  |  | Distance Circular\Polarisation | phik0 | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Circular\Polarisation | phik0 | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Polarisation | phik0 | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;3 |  | Distance Polygonal\Polarisation | phik0 | Real |  |  | 1 | 0
x074_u002E_097 | Parameter subset 3->DIST | 074.097 | Circle¦0;Polygon¦1 |  | Characteristic PS3 | Enum | Parameters__Function_parameters | 0;1 | Real |  | x056_u002E_014;x031_u002E_073;x003_u002E_060 | E;E;E | 0;0;3 | 1 | 4 | E | 0 | Distance Circular | outserv | Real | 0 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Distance Circular | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 0 | Distance Polygonal | outserv | Real | 0 | 1 | [13 empty] | 1
[16 empty] | E | 1 | Distance Circular | outserv | Real | 0 | 1
[16 empty] | E | 1 | Distance Polygonal | outserv | Real | 0 | 0
x013_u002E_001 | Parameter subset 3->DIST | 013.001 | 0.1-200:0.01 | — | X1 (polygon) PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 10 |  |  |  | Distance Polygonal\Z1 | Xmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\Z1 | Xmax | Real |  |  | 1 | 0
x013_u002E_002 | Parameter subset 3->DIST | 013.002 | 0.1-200:0.01 | — | X2 (polygon) PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 20 |  |  |  | Distance Polygonal\Z2 | Xmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\Z2 | Xmax | Real |  |  | 1 | 0
x013_u002E_003 | Parameter subset 3->DIST | 013.003 | 0.1-200:0.01 | — | X3 (polygon) PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 30 |  |  |  | Distance Polygonal\Z3 | Xmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\Z3 | Xmax | Real |  |  | 1 | 0
x013_u002E_004 | Parameter subset 3->DIST | 013.004 | 0.1-200:0.01 | — | X4 (polygon) PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 40 |  |  |  | Distance Polygonal\Z4 | Xmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\Z4 | Xmax | Real |  |  | 1 | 0
x013_u002E_005 | Parameter subset 3->DIST | 013.005 | 0.1-200:0.01 | — | R1,PG (polygon) PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 10 |  |  |  | Distance Polygonal\Z1 | REmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\Z1 | REmax | Real |  |  | 1 | 0
x013_u002E_006 | Parameter subset 3->DIST | 013.006 | 0.1-200:0.01 | — | R1,PP (polygon) PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 10 |  |  |  | Distance Polygonal\Z1 | Rmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\Z1 | Rmax | Real |  |  | 1 | 0
x013_u002E_007 | Parameter subset 3->DIST | 013.007 | 0.1-200:0.01 | — | R2,PG (polygon) PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 20 |  |  |  | Distance Polygonal\Z2 | REmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\Z2 | REmax | Real |  |  | 1 | 0
x013_u002E_008 | Parameter subset 3->DIST | 013.008 | 0.1-200:0.01 | — | R2,PP (polygon) PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 20 |  |  |  | Distance Polygonal\Z2 | Rmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\Z2 | Rmax | Real |  |  | 1 | 0
x013_u002E_009 | Parameter subset 3->DIST | 013.009 | 0.1-200:0.01 | — | R3,PG (polygon) PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 30 |  |  |  | Distance Polygonal\Z3 | REmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\Z3 | REmax | Real |  |  | 1 | 0
x013_u002E_010 | Parameter subset 3->DIST | 013.010 | 0.1-200:0.01 | — | R3,PP (polygon) PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 30 |  |  |  | Distance Polygonal\Z3 | Rmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\Z3 | Rmax | Real |  |  | 1 | 0
x013_u002E_011 | Parameter subset 3->DIST | 013.011 | 0.1-200:0.01 | — | R4,PG (polygon) PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 40 |  |  |  | Distance Polygonal\Z4 | REmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\Z4 | REmax | Real |  |  | 1 | 0
x013_u002E_012 | Parameter subset 3->DIST | 013.012 | 0.1-200:0.01 | — | R4,PP (polygon) PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 40 |  |  |  | Distance Polygonal\Z4 | Rmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\Z4 | Rmax | Real |  |  | 1 | 0
x013_u002E_013 | Parameter subset 3->DIST | 013.013 | 40-90:1 | ° | €1 (polygon) PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 75 |  |  |  | Distance Polygonal\Z1 | phi | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\Z1 | phi | Real |  |  | 1 | 0
x013_u002E_014 | Parameter subset 3->DIST | 013.014 | 40-90:1 | ° | €2 (polygon) PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 75 |  |  |  | Distance Polygonal\Z2 | phi | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\Z2 | phi | Real |  |  | 1 | 0
x013_u002E_015 | Parameter subset 3->DIST | 013.015 | 40-90:1 | ° | €3 (polygon) PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 75 |  |  |  | Distance Polygonal\Z3 | phi | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\Z3 | phi | Real |  |  | 1 | 0
x013_u002E_016 | Parameter subset 3->DIST | 013.016 | 40-90:1 | ° | €4 (polygon) PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 75 |  |  |  | Distance Polygonal\Z4 | phi | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\Z4 | phi | Real |  |  | 1 | 0
x074_u002E_086 | Parameter subset 3->DIST | 074.086 | -20-20:1 | ° | ‹1 (polygon) PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 0 |  |  |  | Distance Polygonal\Z1 | beta | Real | -1 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\Z1 | beta | Real |  |  | -1 | 0
x074_u002E_087 | Parameter subset 3->DIST | 074.087 | -20-20:1 | ° | ‹2 (polygon) PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 0 |  |  |  | Distance Polygonal\Z2 | beta | Real | -1 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\Z2 | beta | Real |  |  | -1 | 0
x074_u002E_088 | Parameter subset 3->DIST | 074.088 | -20-20:1 | ° | ‹3 (polygon) PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 0 |  |  |  | Distance Polygonal\Z3 | beta | Real | -1 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\Z3 | beta | Real |  |  | -1 | 0
x074_u002E_089 | Parameter subset 3->DIST | 074.089 | -20-20:1 | ° | ‹4 (polygon) PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 0 |  |  |  | Distance Polygonal\Z4 | beta | Real | -1 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\Z4 | beta | Real |  |  | -1 | 0
x074_u002E_091 | Parameter subset 3->DIST | 074.091 | 0.05-200:0.01 | — | Z1 (circle) PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 10 |  |  |  | Distance Circular\Z1 | Zm | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Circular\Z1 | Zm | Real |  |  | 1 | 0
x074_u002E_092 | Parameter subset 3->DIST | 074.092 | 0.05-200:0.01 | — | Z2 (circle) PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 20 |  |  |  | Distance Circular\Z2 | Zm | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Circular\Z2 | Zm | Real |  |  | 1 | 0
x074_u002E_093 | Parameter subset 3->DIST | 074.093 | 0.05-200:0.01 | — | Z3 (circle) PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 30 |  |  |  | Distance Circular\Z3 | Zm | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Circular\Z3 | Zm | Real |  |  | 1 | 0
x074_u002E_094 | Parameter subset 3->DIST | 074.094 | 0.05-200:0.01 | — | Z4 (circle) PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 40 |  |  |  | Distance Circular\Z4 | Zm | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Circular\Z4 | Zm | Real |  |  | 1 | 0
x074_u002E_090 | Parameter subset 3->DIST | 074.090 | 10-90:1 | ° | €1 (circle) PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 75 | 2 |  |  | Distance Circular\Z1 | arcalpha | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Circular\Z1 | arcalpha | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z1E | arcalpha | Real | 1 | 0
x074_u002E_095 | Parameter subset 3->DIST | 074.095 | 10-90:1 | ° | €2 (circle) PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 75 |  |  |  | Distance Circular\Z2 | arcalpha | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Circular\Z2 | arcalpha | Real |  |  | 1 | 0
x074_u002E_096 | Parameter subset 3->DIST | 074.096 | 10-90:1 | ° | €3 (circle) PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 75 |  |  |  | Distance Circular\Z3 | arcalpha | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Circular\Z3 | arcalpha | Real |  |  | 1 | 0
x074_u002E_099 | Parameter subset 3->DIST | 074.099 | 10-90:1 | ° | €4 (circle) PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 75 |  |  |  | Distance Circular\Z4 | arcalpha | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Circular\Z4 | arcalpha | Real |  |  | 1 | 0
x012_u002E_091 | Parameter subset 3->DIST | 012.091 | No¦0;Yes¦1 |  | Arc comp. circle PS3 | Enum | Parameters__Function_parameters | 0;1 | Real |  | x003_u002E_060 | E | 3 | 0 | 5 |  |  | Distance Circular\Z1 | arcen | Real | 1 | 0 | 4 | Distance Circular;Distance Circular\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Circular\Z1 | arcen | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z1E | arcen | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Circular\Z2 | arcen | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z2 | arcen | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Circular\Z3 | arcen | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z3 | arcen | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Circular\Z4 | arcen | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z4 | arcen | Real | 1 | 0
x013_u002E_023 | Parameter subset 3->DIST | 013.023 | Forward directional¦0;Backward directional¦1;Non-directional¦2 |  | Direction N1 PS3 | Enum | Parameters__Function_parameters | 0;1;2 | Real |  | x003_u002E_060 | E | 3 | 0 | 4 | NE | 2 | Distance Circular\Z1 | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Circular\Z1 | idir | Real |  |  | 1 | 0
[16 empty] | NE | 2 | Distance Circular\Z1E | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\Z1 | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z1 | idir | Real | 1 | 0
[18 empty] | Distance Polygonal\Z1E | idir | Real | 1 | 0
x013_u002E_024 | Parameter subset 3->DIST | 013.024 | Forward directional¦0;Backward directional¦1;Non-directional¦2 |  | Direction N2 PS3 | Enum | Parameters__Function_parameters | 0;1;2 | Real |  | x003_u002E_060 | E | 3 | 0 |  | NE | 2 | Distance Circular\Z2 | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Circular\Z2 | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z2 | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\Z2 | idir | Real |  |  | 1 | 0
x013_u002E_025 | Parameter subset 3->DIST | 013.025 | Forward directional¦0;Backward directional¦1;Non-directional¦2 |  | Direction N3 PS3 | Enum | Parameters__Function_parameters | 0;1;2 | Real |  | x003_u002E_060 | E | 3 | 0 |  | NE | 2 | Distance Circular\Z3 | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Circular\Z3 | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z3 | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\Z3 | idir | Real |  |  | 1 | 0
x013_u002E_026 | Parameter subset 3->DIST | 013.026 | Forward directional¦0;Backward directional¦1;Non-directional¦2 |  | Direction N4 PS3 | Enum | Parameters__Function_parameters | 0;1;2 | Real |  | x003_u002E_060 | E | 3 | 0 |  | NE | 2 | Distance Circular\Z4 | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Circular\Z4 | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z4 | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\Z4 | idir | Real |  |  | 1 | 0
x013_u002E_027 | Parameter subset 3->DIST | 013.027 | Forward directional¦0;Backward directional¦1;Non-directional¦2 |  | Direction N5 PS3 | Enum | Parameters__Function_parameters | 0;1;2 | Real |  | x003_u002E_060 | E | 3 | 0 |  |  |  | Distance Circular\Directional | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Directional;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Circular\Directional | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Directional | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Directional;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\Directional | idir | Real |  |  | 1 | 0
x013_u002E_028 | Parameter subset 3->DIST | 013.028 | 0-10:0.001;Blocked=10.002 | s | t1 PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 0 | 4 | SE | 10 | Distance Circular\T1 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Circular\T1 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Circular\T1 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
[16 empty] | SE | 10 | Distance Polygonal\T1 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Polygonal\T1 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Polygonal\T1 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
x013_u002E_029 | Parameter subset 3->DIST | 013.029 | 0-10:0.001;Blocked=10.002 | s | t2 PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 | 4 | SE | 10 | Distance Circular\T2 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Circular\T2 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Circular\T2 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
[16 empty] | SE | 10 | Distance Polygonal\T2 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Polygonal\T2 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Polygonal\T2 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
x013_u002E_030 | Parameter subset 3->DIST | 013.030 | 0-10:0.001;Blocked=10.002 | s | t3 PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 2 | 4 | SE | 10 | Distance Circular\T3 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Circular\T3 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Circular\T3 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
[16 empty] | SE | 10 | Distance Polygonal\T3 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Polygonal\T3 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Polygonal\T3 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
x013_u002E_031 | Parameter subset 3->DIST | 013.031 | 0-10:0.001;Blocked=10.002 | s | t4 PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 3 | 4 | SE | 10 | Distance Circular\T4 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Circular\T4 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Circular\T4 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
[16 empty] | SE | 10 | Distance Polygonal\T4 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Polygonal\T4 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Polygonal\T4 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
x013_u002E_032 | Parameter subset 3->DIST | 013.032 | 0-10:0.001;Blocked=10.002 | s | t5 PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 4 | 4 | SE | 10 | Distance Circular\T5 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Circular\T5 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Circular\T5 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
[16 empty] | SE | 10 | Distance Polygonal\T5 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Polygonal\T5 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Polygonal\T5 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
x013_u002E_033 | Parameter subset 3->DIST | 013.033 | 0-10:0.001;Blocked=10.002 | s | t6 PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 5 | 4 | SE | 10 | Distance Circular\T6 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Circular\T6 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Circular\T6 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
[16 empty] | SE | 10 | Distance Polygonal\T6 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Polygonal\T6 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Polygonal\T6 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
x013_u002E_035 | Parameter subset 3->DIST | 013.035 | 1-450:0.01 |  | kze,PP HSR PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1.2 | 3 |  |  | Distance Circular\Z1E | kZ | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z1E;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Circular\Z1E | kZ | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z1E | kX | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z1E;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\Z1E | kX | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z1E | kR | Real | 1 | 0
x015_u002E_016 | Parameter subset 3->PSIG | 015.016 | No¦0;Yes¦1 |  | Enable PS3 | Enum | Parameters__Function_parameters | 0;1 | String |  | x003_u002E_060 | E | 3 | 0 | 2 |  |  | Distance Circular\PSIG Connect | aDipset | String |  |  | 2 | Distance Circular;Distance Circular\PSIG Connect;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Circular\PSIG Connect | aDipset | String
[18 empty] | Distance Polygonal\PSIG Connect | aDipset | String |  |  |  | Distance Polygonal;Distance Polygonal\PSIG Connect;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\PSIG Connect | aDipset | String
x024_u002E_060 | Parameter subset 3->PSIG | 024.060 | Without¦0;Dir.trans.trip.under¦1;PUTT¦2;Zone extension¦3;Release scheme¦4;Blocking scheme¦5;DC loop operat. mode¦6;Reverse interlocking¦7;Direction comparison¦8 |  | Operating mode PS3 | Enum | Parameters__Function_parameters | ;DIRECT = TRIP;PUTT = TRIP;POTT = TRIP;COMP_RELEASE = TRIP;COMP_BLOCK = TRIP;COMP_PILOT = TRIP; | String |  | x003_u002E_060 | E | 3 | PUTT = TRIP | 4 |  |  | Distance Circular\PSIG Receive | sLogic | String |  |  | 2 | Distance Circular;Distance Circular\PSIG Receive;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Circular\PSIG Receive | sLogic | String
[18 empty] | Distance Circular\PSIG Send | sLogic | String |  |  |  | Distance Polygonal;Distance Polygonal\PSIG Receive;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\PSIG Receive | sLogic | String
[18 empty] | Distance Polygonal\PSIG Receive | sLogic | String
[18 empty] | Distance Polygonal\PSIG Send | sLogic | String
x024_u002E_063 | Parameter subset 3->PSIG | 024.063 | 0-10:0.001;Blocked=10.002 | s | Tripping time PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 0.08 | 4 | SE | 10 | Distance Circular\PSIG T | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\PSIG T;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Circular\PSIG T | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Circular\PSIG T | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
[16 empty] | SE | 10 | Distance Polygonal\PSIG T | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\PSIG T;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 | 2 | Distance Polygonal\PSIG T | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Polygonal\PSIG T | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
x024_u002E_061 | Parameter subset 3->PSIG | 024.061 | 0-10:0.001 | s | Release t. send PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 0.25 | 2 |  |  | Distance Circular\PSIG T Reset | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\PSIG T Reset;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Circular\PSIG T Reset | Tdelay | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\PSIG T Reset | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\PSIG T Reset;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;3 |  | Distance Polygonal\PSIG T Reset | Tdelay | Real |  |  | 1 | 0
x074_u002E_098 | Parameter subset 3->DTOC | 074.098 | No¦0;Yes¦1 |  | Enable PS3 | Enum | Parameters__Function_parameters | 1;0 | Real |  | x056_u002E_008;x003_u002E_060 | E;E | 0;3 | 1 | 12 |  |  | Overcurrent\I> | outserv | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 12 | Overcurrent\I> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\I>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\I>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\I>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\I>>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\I>>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\I>>>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\IN> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\IN> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\IN>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\IN>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\IN>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\IN>>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\IN>>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\IN>>>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\Ineg> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\Ineg> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\Ineg>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\Ineg>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\Ineg>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\Ineg>>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\Ineg>>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\Ineg>>>> | outserv | Real |  |  | 1 | 0
x074_u002E_007 | Parameter subset 3->DTOC | 074.007 | 0.1-20:0.01 | Inom | I> PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 |  |  |  | Overcurrent\I> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\I> | Ipset | Real |  |  | 1 | 0
x074_u002E_008 | Parameter subset 3->DTOC | 074.008 | 0.1-20:0.01 | Inom | I>> PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 |  |  |  | Overcurrent\I>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\I>> | Ipset | Real |  |  | 1 | 0
x074_u002E_009 | Parameter subset 3->DTOC | 074.009 | 0.1-20:0.01 | Inom | I>>> PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 |  |  |  | Overcurrent\I>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\I>>> | Ipset | Real |  |  | 1 | 0
x074_u002E_010 | Parameter subset 3->DTOC | 074.010 | 0.1-20:0.01 | Inom | I>>>> PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 |  |  |  | Overcurrent\I>>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\I>>>> | Ipset | Real |  |  | 1 | 0
x074_u002E_019 | Parameter subset 3->DTOC | 074.019 | 0-30:0.001;Blocked=30.002 | s | tI> PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 | SE | 30 | Overcurrent\I> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Overcurrent\I> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\I> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x074_u002E_020 | Parameter subset 3->DTOC | 074.020 | 0-30:0.001;Blocked=30.002 | s | tI>> PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 | SE | 30 | Overcurrent\I>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Overcurrent\I>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\I>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x074_u002E_021 | Parameter subset 3->DTOC | 074.021 | 0-30:0.001;Blocked=30.002 | s | tI>>> PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 | SE | 30 | Overcurrent\I>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Overcurrent\I>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\I>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x074_u002E_022 | Parameter subset 3->DTOC | 074.022 | 0-30:0.001;Blocked=30.002 | s | tI>>>> PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 | SE | 30 | Overcurrent\I>>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Overcurrent\I>>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\I>>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x074_u002E_011 | Parameter subset 3->DTOC | 074.011 | 0.1-20:0.01 | Inom | Ineg> PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 |  |  |  | Overcurrent\IN> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\IN> | Ipset | Real |  |  | 1 | 0
x074_u002E_012 | Parameter subset 3->DTOC | 074.012 | 0.1-20:0.01 | Inom | Ineg>> PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 |  |  |  | Overcurrent\IN>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\IN>> | Ipset | Real |  |  | 1 | 0
x074_u002E_013 | Parameter subset 3->DTOC | 074.013 | 0.1-20:0.01 | Inom | Ineg>>> PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 |  |  |  | Overcurrent\IN>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\IN>>> | Ipset | Real |  |  | 1 | 0
x074_u002E_014 | Parameter subset 3->DTOC | 074.014 | 0.1-20:0.01 | Inom | Ineg>>>> PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 |  |  |  | Overcurrent\IN>>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\IN>>>> | Ipset | Real |  |  | 1 | 0
x074_u002E_023 | Parameter subset 3->DTOC | 074.023 | 0-30:0.001;Blocked=30.002 | s | tIneg> PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 | SE | 30 | Overcurrent\IN> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Overcurrent\IN> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\IN> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x074_u002E_024 | Parameter subset 3->DTOC | 074.024 | 0-30:0.001;Blocked=30.002 | s | tIneg>> PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 | SE | 30 | Overcurrent\IN>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Overcurrent\IN>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\IN>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x074_u002E_025 | Parameter subset 3->DTOC | 074.025 | 0-30:0.001;Blocked=30.002 | s | tIneg>>> PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 | SE | 30 | Overcurrent\IN>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Overcurrent\IN>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\IN>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x074_u002E_026 | Parameter subset 3->DTOC | 074.026 | 0-30:0.001;Blocked=30.002 | s | tIneg>>>> PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 | SE | 30 | Overcurrent\IN>>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Overcurrent\IN>>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\IN>>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x074_u002E_015 | Parameter subset 3->DTOC | 074.015 | 0.1-20:0.01 | Inom | IN> PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 |  |  |  | Overcurrent\Ineg> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\Ineg> | Ipset | Real |  |  | 1 | 0
x074_u002E_016 | Parameter subset 3->DTOC | 074.016 | 0.1-20:0.01 | Inom | IN>> PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 |  |  |  | Overcurrent\Ineg>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\Ineg>> | Ipset | Real |  |  | 1 | 0
x074_u002E_017 | Parameter subset 3->DTOC | 074.017 | 0.1-20:0.01 | Inom | IN>>> PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 |  |  |  | Overcurrent\Ineg>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\Ineg>>> | Ipset | Real |  |  | 1 | 0
x074_u002E_018 | Parameter subset 3->DTOC | 074.018 | 0.1-20:0.01 | Inom | IN>>>> PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 |  |  |  | Overcurrent\Ineg>>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\Ineg>>>> | Ipset | Real |  |  | 1 | 0
x074_u002E_027 | Parameter subset 3->DTOC | 074.027 | 0-30:0.001;Blocked=30.002 | s | tIN> PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 | SE | 30 | Overcurrent\Ineg> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Overcurrent\Ineg> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\Ineg> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x074_u002E_028 | Parameter subset 3->DTOC | 074.028 | 0-30:0.001;Blocked=30.002 | s | tIN>> PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 | SE | 30 | Overcurrent\Ineg>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Overcurrent\Ineg>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\Ineg>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x074_u002E_029 | Parameter subset 3->DTOC | 074.029 | 0-30:0.001;Blocked=30.002 | s | tIN>>> PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 | SE | 30 | Overcurrent\Ineg>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Overcurrent\Ineg>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\Ineg>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x074_u002E_030 | Parameter subset 3->DTOC | 074.030 | 0-30:0.001;Blocked=30.002 | s | tIN>>>> PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 | SE | 30 | Overcurrent\Ineg>>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Overcurrent\Ineg>>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\Ineg>>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x074_u002E_000 | Parameter subset 3->IDMT | 074.000 | No¦0;Yes¦1 |  | Enable P PS3 | Enum | Parameters__Function_parameters | 1;0 | Real |  | x056_u002E_009;x003_u002E_060 | E;E | 0;3 | 1 |  |  |  | Overcurrent\IDMT P | outserv | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\IDMT P | outserv | Real |  |  | 1 | 0
x074_u002E_050 | Parameter subset 3->IDMT | 074.050 | 0.1-4:0.01 | Inom | Iref,P PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 |  |  |  | Overcurrent\IDMT P | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\IDMT P | Ipset | Real |  |  | 1 | 0
x074_u002E_056 | Parameter subset 3->IDMT | 074.056 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Characterist. P PS3 | Enum | Parameters__Function_parameters | Definite Time;IEC 255-3 Standard Inverse;IEC 255-3 Very Inverse;IEC 255-3 Extremly Inverse;IEC 255-3 Long-Time Inverse;IEEE C37.112 Moderately Inverse;IEEE C37.112 Very Inverse;IEEE C37.112 Extremely Inverse;ANSI Normally Inverse;ANSI Short-Time Inverse;ANSI Long-Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | [8 empty] | Overcurrent\IDMT P | pcharac |  |  |  |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\IDMT P | pcharac
x074_u002E_053 | Parameter subset 3->IDMT | 074.053 | 0.01-10:0.01 |  | Ch. factor kt,P PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 |  |  |  | Overcurrent\IDMT P | Tpset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\IDMT P | Tpset | Real |  |  | 1 | 0
x074_u002E_059 | Parameter subset 3->IDMT | 074.059 | Without delay¦0;Delayed as per char.¦1 |  | Reset P PS3 | Enum | Parameters__Function_parameters | 0;1 | Real | 3 | x003_u002E_060;x074_u002E_056 | E;SW | 3;IEEE | 0 |  |  |  | Overcurrent\IDMT P | resetdis | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\IDMT P | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x074_u002E_056 | E;SW | 3;ANSI |  |  |  |  | Overcurrent\IDMT P | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | 3 |  |  |  |  | Overcurrent\IDMT P | resetdis | Real | 0 | 0
x074_u002E_062 | Parameter subset 3->IDMT | 074.062 | Forward directional¦0;Backward directional¦1;Non-directional¦2 |  | Direction P PS3 | Enum | Parameters__Function_parameters | 1;2;0 | Real |  | x003_u002E_060 | E | 3 | 1 |  |  |  | Overcurrent\IDMT P | idir | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\IDMT P | idir | Real |  |  | 1 | 0
x074_u002E_001 | Parameter subset 3->IDMT | 074.001 | No¦0;Yes¦1 |  | Enable neg. PS3 | Enum | Parameters__Function_parameters | 1;0 | Real |  | x056_u002E_009;x003_u002E_060 | E;E | 0;3 | 1 |  |  |  | Overcurrent\IDMT neg | outserv | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\IDMT neg | outserv | Real |  |  | 1 | 0
x074_u002E_051 | Parameter subset 3->IDMT | 074.051 | 0.1-4:0.01 | Inom | Iref,neg PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 |  |  |  | Overcurrent\IDMT neg | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\IDMT neg | Ipset | Real |  |  | 1 | 0
x074_u002E_057 | Parameter subset 3->IDMT | 074.057 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Character. neg. PS3 | Enum | Parameters__Function_parameters | Definite Time;IEC 255-3 Standard Inverse;IEC 255-3 Very Inverse;IEC 255-3 Extremly Inverse;IEC 255-3 Long-Time Inverse;IEEE C37.112 Moderately Inverse;IEEE C37.112 Very Inverse;IEEE C37.112 Extremely Inverse;ANSI Normally Inverse;ANSI Short-Time Inverse;ANSI Long-Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | [8 empty] | Overcurrent\IDMT neg | pcharac |  |  |  |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\IDMT neg | pcharac
x074_u002E_054 | Parameter subset 3->IDMT | 074.054 | 0.01-10:0.01 |  | Factor kt,neg PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 |  |  |  | Overcurrent\IDMT neg | Tpset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\IDMT neg | Tpset | Real |  |  | 1 | 0
x074_u002E_060 | Parameter subset 3->IDMT | 074.060 | Without delay¦0;Delayed as per char.¦1 |  | Reset neg. PS3 | Enum | Parameters__Function_parameters | 0;1 | Real | 3 | x003_u002E_060;x074_u002E_057 | E;SW | 3;IEEE | 0 |  |  |  | Overcurrent\IDMT neg | resetdis | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\IDMT neg | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x074_u002E_057 | E;SW | 3;ANSI |  |  |  |  | Overcurrent\IDMT neg | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | 3 |  |  |  |  | Overcurrent\IDMT neg | resetdis | Real | 0 | 0
x074_u002E_063 | Parameter subset 3->IDMT | 074.063 | Forward directional¦0;Backward directional¦1;Non-directional¦2 |  | Direction neg. PS3 | Enum | Parameters__Function_parameters | 1;2;0 | Real |  | x003_u002E_060 | E | 3 | 1 |  |  |  | Overcurrent\IDMT neg | idir | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\IDMT neg | idir | Real |  |  | 1 | 0
x074_u002E_002 | Parameter subset 3->IDMT | 074.002 | No¦0;Yes¦1 |  | Enable N PS3 | Enum | Parameters__Function_parameters | 1;0 | Real |  | x056_u002E_009;x003_u002E_060 | E;E | 0;3 | 1 |  |  |  | Overcurrent\IDMT N | outserv | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\IDMT N | outserv | Real |  |  | 1 | 0
x074_u002E_052 | Parameter subset 3->IDMT | 074.052 | 0.1-4:0.01 | Inom | Iref,N PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 |  |  |  | Overcurrent\IDMT N | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\IDMT N | Ipset | Real |  |  | 1 | 0
x074_u002E_058 | Parameter subset 3->IDMT | 074.058 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Characterist. N PS3 | Enum | Parameters__Function_parameters | Definite Time;IEC 255-3 Standard Inverse;IEC 255-3 Very Inverse;IEC 255-3 Extremly Inverse;IEC 255-3 Long-Time Inverse;IEEE C37.112 Moderately Inverse;IEEE C37.112 Very Inverse;IEEE C37.112 Extremely Inverse;ANSI Normally Inverse;ANSI Short-Time Inverse;ANSI Long-Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | [8 empty] | Overcurrent\IDMT N | pcharac |  |  |  |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\IDMT N | pcharac
x074_u002E_055 | Parameter subset 3->IDMT | 074.055 | 0.01-10:0.01 |  | Factor kt,N PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 |  |  |  | Overcurrent\IDMT N | Tpset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\IDMT N | Tpset | Real |  |  | 1 | 0
x074_u002E_061 | Parameter subset 3->IDMT | 074.061 | Without delay¦0;Delayed as per char.¦1 |  | Reset N PS3 | Enum | Parameters__Function_parameters | 0;1 | Real | 3 | x003_u002E_060;x074_u002E_058 | E;SW | 3;IEEE | 0 |  |  |  | Overcurrent\IDMT neg | resetdis | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\IDMT neg | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x074_u002E_058 | E;SW | 3;ANSI |  |  |  |  | Overcurrent\IDMT neg | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | 3 |  |  |  |  | Overcurrent\IDMT neg | resetdis | Real | 0 | 0
x074_u002E_064 | Parameter subset 3->IDMT | 074.064 | Forward directional¦0;Backward directional¦1;Non-directional¦2 |  | Direction N PS3 | Enum | Parameters__Function_parameters | 1;2;0 | Real |  | x003_u002E_060 | E | 3 | 1 |  |  |  | Overcurrent\IDMT N | idir | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Overcurrent\IDMT N | idir | Real |  |  | 1 | 0
x078_u002E_000 | Parameter subset 3->V<> | 078.000 | No¦0;Yes¦1 |  | Enable PS3 | Enum | Parameters__Function_parameters | 1;0 | Real |  | x056_u002E_010;x003_u002E_060 | E;E | 0;3 | 1 |  |  |  | Voltage | outserv | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 |  | Voltage | outserv | Real |  |  | 1 | 0
x078_u002E_001 | Parameter subset 3->V<> | 078.001 | Delta¦0;Star¦1 |  | Operating mode PS3 | Enum | Parameters__Function_parameters | 0;1 | Real |  | x078_u002E_000;x003_u002E_060 | E;E | 0;3 | 0 | 4 | E | 1 | Voltage\V> | outserv | Real | 0 | 1
[16 empty] | E | 1 | Voltage\V>> | outserv | Real | 0 | 1
[16 empty] | E | 1 | Voltage\V< | outserv | Real | 0 | 1
[16 empty] | E | 1 | Voltage\V<< | outserv | Real | 0 | 1
x078_u002E_003 | Parameter subset 3->V<> | 078.003 | 0.2-1.5:0.01;Blocked=1.52 | Vnom(/©3) | V> PS3 | Real | Parameters__Function_parameters |  |  |  | x078_u002E_001;x003_u002E_060 | E;E | 0;3 | 1.1 | 3 | SE | 1.5 | Voltage\V> | Uset | Real | 1 | 0 |  | x078_u002E_001;x003_u002E_060 |  |  | E;E | 0;3 | 2 | Voltage\V> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V> | outserv | Real | 0 | 0 | [7 empty] | Voltage\V> | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\V> | outserv | Real | 0 | 1
x078_u002E_004 | Parameter subset 3->V<> | 078.004 | 0.2-1.5:0.01;Blocked=1.52 | Vnom(/©3) | V>> PS3 | Real | Parameters__Function_parameters |  |  |  | x078_u002E_001;x003_u002E_060 | E;E | 0;3 | 1.1 | 3 | SE | 1.5 | Voltage\V>> | Uset | Real | 1 | 0 |  | x078_u002E_001;x003_u002E_060 |  |  | E;E | 0;3 | 2 | Voltage\V>> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\V>> | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\V>> | outserv | Real | 0 | 1
x078_u002E_005 | Parameter subset 3->V<> | 078.005 | 0-100:0.01;Blocked=100.02 | s | tV> PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 | SE | 100 | Voltage\V> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Voltage\V> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x078_u002E_006 | Parameter subset 3->V<> | 078.006 | 0-100:0.01;Blocked=100.02 | s | tV>> PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 | SE | 100 | Voltage\V>> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Voltage\V>> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V>> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x078_u002E_007 | Parameter subset 3->V<> | 078.007 | 0.2-1.5:0.01;Blocked=1.52 | Vnom(/©3) | V< PS3 | Real | Parameters__Function_parameters |  |  |  | x078_u002E_001;x003_u002E_060 | E;E | 0;3 | 0.8 | 3 | SE | 1.5 | Voltage\V< | Uset | Real | 1 | 0 |  | x078_u002E_001;x003_u002E_060 |  |  | E;E | 0;3 | 2 | Voltage\V< | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V< | outserv | Real | 0 | 0 | [7 empty] | Voltage\V< | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\V< | outserv | Real | 0 | 1
x078_u002E_008 | Parameter subset 3->V<> | 078.008 | 0.2-1.5:0.01;Blocked=1.52 | Vnom(/©3) | V<< PS3 | Real | Parameters__Function_parameters |  |  |  | x078_u002E_001;x003_u002E_060 | E;E | 0;3 | 0.8 | 3 | SE | 1.5 | Voltage\V<< | Uset | Real | 1 | 0 |  | x078_u002E_001;x003_u002E_060 |  |  | E;E | 0;3 | 2 | Voltage\V<< | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V<< | outserv | Real | 0 | 0 | [7 empty] | Voltage\V<< | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\V<< | outserv | Real | 0 | 1
x078_u002E_009 | Parameter subset 3->V<> | 078.009 | 0-100:0.01;Blocked=100.02 | s | tV< PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 | SE | 100 | Voltage\V< | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Voltage\V< | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V< | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x078_u002E_010 | Parameter subset 3->V<> | 078.010 | 0-100:0.01;Blocked=100.02 | s | tV<< PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 | SE | 100 | Voltage\V<< | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Voltage\V<< | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V<< | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x078_u002E_015 | Parameter subset 3->V<> | 078.015 | 0.2-1.5:0.01;Blocked=1.52 | Vnom/©3 | Vpos> PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1.1 | 3 | SE | 1.5 | Voltage\Vpos> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Voltage\Vpos> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos> | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vpos> | outserv | Real | 0 | 1
x078_u002E_016 | Parameter subset 3->V<> | 078.016 | 0.2-1.5:0.01;Blocked=1.52 | Vnom/©3 | Vpos>> PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1.1 | 3 | SE | 1.5 | Voltage\Vpos>> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Voltage\Vpos>> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos>> | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vpos>> | outserv | Real | 0 | 1
x078_u002E_017 | Parameter subset 3->V<> | 078.017 | 0-100:0.01;Blocked=100.02 | s | tVpos> PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 | SE | 100 | Voltage\Vpos> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Voltage\Vpos> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vpos> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x078_u002E_018 | Parameter subset 3->V<> | 078.018 | 0-100:0.01;Blocked=100.02 | s | tVpos>> PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 | SE | 100 | Voltage\Vpos>> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Voltage\Vpos>> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vpos>> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x078_u002E_019 | Parameter subset 3->V<> | 078.019 | 0.2-1.5:0.01;Blocked=1.52 | Vnom/©3 | Vpos< PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 0.8 | 3 | SE | 1.5 | Voltage\Vpos< | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Voltage\Vpos< | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos< | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos< | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vpos< | outserv | Real | 0 | 1
x078_u002E_020 | Parameter subset 3->V<> | 078.020 | 0.2-1.5:0.01;Blocked=1.52 | Vnom/©3 | Vpos<< PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 0.8 | 3 | SE | 1.5 | Voltage\Vpos<< | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Voltage\Vpos<< | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos<< | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos<< | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vpos<< | outserv | Real | 0 | 1
x078_u002E_021 | Parameter subset 3->V<> | 078.021 | 0-100:0.01;Blocked=100.02 | s | tVpos< PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 | SE | 100 | Voltage\Vpos< | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Voltage\Vpos< | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vpos< | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x078_u002E_022 | Parameter subset 3->V<> | 078.022 | 0-100:0.01;Blocked=100.02 | s | tVpos<< PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 | SE | 100 | Voltage\Vpos<< | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Voltage\Vpos<< | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vpos<< | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x078_u002E_023 | Parameter subset 3->V<> | 078.023 | 0.2-1.5:0.01;Blocked=1.52 | Vnom/©3 | Vneg> PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1.52 | 3 | SE | 1.5 | Voltage\Vneg> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Voltage\Vneg> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vneg> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vneg> | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vneg> | outserv | Real | 0 | 1
x078_u002E_024 | Parameter subset 3->V<> | 078.024 | 0.2-1.5:0.01;Blocked=1.52 | Vnom/©3 | Vneg>> PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1.52 | 3 | SE | 1.5 | Voltage\Vneg>> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Voltage\Vneg>> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vneg>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vneg>> | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vneg>> | outserv | Real | 0 | 1
x078_u002E_025 | Parameter subset 3->V<> | 078.025 | 0-100:0.01;Blocked=100.02 | s | tVneg> PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 | SE | 100 | Voltage\Vneg> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Voltage\Vneg> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vneg> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x078_u002E_026 | Parameter subset 3->V<> | 078.026 | 0-100:0.01;Blocked=100.02 | s | tVneg>> PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 | SE | 100 | Voltage\Vneg>> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Voltage\Vneg>> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vneg>> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x078_u002E_011 | Parameter subset 3->V<> | 078.011 | 0.02-1:0.01;Blocked=1.02 | Vnom(/©3) | VNG> PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1.02 | 3 | SE | 1 | Voltage\VNG> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Voltage\VNG> | outserv | Real | E | 1 | 0 | 1.02
[16 empty] | SE | 1 | Voltage\VNG> | outserv | Real | 0 | 0 | [7 empty] | Voltage\VNG> | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1 | Voltage\VNG> | outserv | Real | 0 | 1
x078_u002E_012 | Parameter subset 3->V<> | 078.012 | 0.02-1:0.01;Blocked=1.02 | Vnom(/©3) | VNG>> PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1.02 | 3 | SE | 1 | Voltage\VNG>> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Voltage\VNG>> | outserv | Real | E | 1 | 0 | 1.02
[16 empty] | SE | 1 | Voltage\VNG>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\VNG>> | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1 | Voltage\VNG>> | outserv | Real | 0 | 1
x078_u002E_013 | Parameter subset 3->V<> | 078.013 | 0-100:0.01;Blocked=100.02 | s | tVNG> PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 | SE | 100 | Voltage\VNG> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Voltage\VNG> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\VNG> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x078_u002E_014 | Parameter subset 3->V<> | 078.014 | 0-100:0.01;Blocked=100.02 | s | tVNG>> PS3 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 3 | 1 | 2 | SE | 100 | Voltage\VNG>> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 3 | 2 | Voltage\VNG>> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\VNG>> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x011_u002E_014 | Parameter subset 4->DIST | 011.014 | 0.1-20:0.01 | Inom | I>> PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 |  |  | Distance Circular\Starting | IMM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Circular\Starting | IMM | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | IMM | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Polygonal\Starting | IMM | Real |  |  | 1 | 0
x011_u002E_028 | Parameter subset 4->DIST | 011.028 | 0.1-1:0.01 | Inom | I> (Ibl) high r. PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 0.2 | 2 |  |  | Distance Circular\Starting | IM1 | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Circular\Starting | IM1 | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | IM1 | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Polygonal\Starting | IM1 | Real |  |  | 1 | 0
x011_u002E_027 | Parameter subset 4->DIST | 011.027 | W/o V< starting¦0;With V< start. PG¦1;With V< start.PG,PP¦2 |  | Operat. mode V< PS4 | Enum | Parameters__Function_parameters | 0;1;2 | Real |  | x003_u002E_060 | E | 4 | 2 | 8 | E | 0 | Distance Circular\Starting | iopt_u | Real | 0 | 0 | 4 | Distance Circular;Distance Circular\Starting;x003_u002E_060 | outserv;iopt_u | Real | E;E;E | 0;0;4 | [7 empty] | 0
[16 empty] | E | 0 | Distance Polygonal\Starting | iopt_u | Real | 0 | 0 |  | Distance Circular;Distance Circular\Starting;x003_u002E_060 | outserv;iopt_u | Real | E;E;E | 0;1;4 | 2 | Distance Circular\Starting | iVOpMode | Real | 0 | 0 | 0 | 1
[16 empty] | NE | 0 | Distance Circular\Starting | iopt_u | Real | 0 | 1 | [7 empty] | Distance Circular\Starting | iVOpMode | Real | 0 | 1 | 0 | 2
[16 empty] | NE | 0 | Distance Polygonal\Starting | iopt_u | Real | 0 | 1 |  | Distance Polygonal;Distance Polygonal\Starting;x003_u002E_060 | outserv;iopt_u | Real | E;E;E | 0;0;4 | [7 empty] | 0
[16 empty] | E | 1 | Distance Circular\Starting | iVOpMode | Real | 0 | 0 |  | Distance Polygonal;Distance Polygonal\Starting;x003_u002E_060 | outserv;iopt_u | Real | E;E;E | 0;1;4 | 2 | Distance Polygonal\Starting | iVOpMode | Real | 0 | 0 | 0 | 1
[16 empty] | E | 1 | Distance Polygonal\Starting | iVOpMode | Real | 0 | 0 | [7 empty] | Distance Polygonal\Starting | iVOpMode | Real | 0 | 1 | 0 | 2
[16 empty] | E | 2 | Distance Circular\Starting | iVOpMode | Real | 0 | 1
[16 empty] | E | 2 | Distance Polygonal\Starting | iVOpMode | Real | 0 | 1
x011_u002E_029 | Parameter subset 4->DIST | 011.029 | 0.1-0.9:0.01 | Vnom(/©3) | V< PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 0.7 | 2 |  |  | Distance Circular\Starting | Um | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Circular\Starting | Um | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | Um | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Polygonal\Starting | Um | Real |  |  | 1 | 0
x011_u002E_026 | Parameter subset 4->DIST | 011.026 | W/o Z< starting¦0;With Z< starting P-G¦1;With Z< start.PG,PP¦2 |  | Operat. mode Z< PS4 | Enum | Parameters__Function_parameters | 0;1;2 | Real |  | x003_u002E_060 | E | 4 | 2 | 8 | E | 0 | Distance Circular\Starting | iopt_z | Real | 0 | 0 | 4 | Distance Circular;Distance Circular\Starting;x003_u002E_060 | outserv;iopt_z | Real | E;E;E | 0;0;4 | [7 empty] | 0
[16 empty] | E | 0 | Distance Polygonal\Starting | iopt_z | Real | 0 | 0 |  | Distance Circular;Distance Circular\Starting;x003_u002E_060 | outserv;iopt_z | Real | E;E;E | 0;1;4 | 2 | Distance Circular\Starting | iZOpMode | Real | 0 | 0 | 0 | 1
[16 empty] | NE | 0 | Distance Circular\Starting | iopt_z | Real | 0 | 1 | [7 empty] | Distance Circular\Starting | iZOpMode | Real | 0 | 1 | 0 | 2
[16 empty] | NE | 0 | Distance Polygonal\Starting | iopt_z | Real | 0 | 1 |  | Distance Polygonal;Distance Polygonal\Starting;x003_u002E_060 | outserv;iopt_z | Real | E;E;E | 0;0;4 | [7 empty] | 0
[16 empty] | E | 1 | Distance Circular\Starting | iZOpMode | Real | 0 | 0 |  | Distance Polygonal;Distance Polygonal\Starting;x003_u002E_060 | outserv;iopt_z | Real | E;E;E | 0;1;4 | 2 | Distance Polygonal\Starting | iZOpMode | Real | 0 | 0 | 0 | 1
[16 empty] | E | 1 | Distance Polygonal\Starting | iZOpMode | Real | 0 | 0 | [7 empty] | Distance Polygonal\Starting | iZOpMode | Real | 0 | 1 | 0 | 2
[16 empty] | E | 2 | Distance Circular\Starting | iZOpMode | Real | 0 | 1
[16 empty] | E | 2 | Distance Polygonal\Starting | iZOpMode | Real | 0 | 1
x011_u002E_010 | Parameter subset 4->DIST | 011.010 | 0.1-300:0.01 | — | Xfw PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 10 | 2 |  |  | Distance Circular\Starting | Xfw | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Circular\Starting | Xfw | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | Xfw | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Polygonal\Starting | Xfw | Real |  |  | 1 | 0
x011_u002E_011 | Parameter subset 4->DIST | 011.011 | 0.1-300:0.01 | — | Rfw,PG PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 10 | 2 |  |  | Distance Circular\Starting | RfPG | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Circular\Starting | RfPG | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | RfPG | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Polygonal\Starting | RfPG | Real |  |  | 1 | 0
x011_u002E_012 | Parameter subset 4->DIST | 011.012 | 0.1-300:0.01 | — | Rfw,PP PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 10 | 2 |  |  | Distance Circular\Starting | RfPP | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Circular\Starting | RfPP | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | RfPP | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Polygonal\Starting | RfPP | Real |  |  | 1 | 0
x011_u002E_023 | Parameter subset 4->DIST | 011.023 | 15-65:1 | ° | ß PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 30 | 2 |  |  | Distance Circular\Starting | Beta | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Circular\Starting | Beta | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | Beta | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Polygonal\Starting | Beta | Real |  |  | 1 | 0
x010_u002E_104 | Parameter subset 4->DIST | 010.104 | 0-300:0.01 | — | Zfw,PG PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 10 | 2 |  |  | Distance Circular\Starting | ZfPG | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Circular\Starting | ZfPG | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | ZfPG | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Polygonal\Starting | ZfPG | Real |  |  | 1 | 0
x010_u002E_108 | Parameter subset 4->DIST | 010.108 | 0-300:0.01 | — | Zfw,PP PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 10 | 2 |  |  | Distance Circular\Starting | ZfPP | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Circular\Starting | ZfPP | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | ZfPP | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Polygonal\Starting | ZfPP | Real |  |  | 1 | 0
x011_u002E_013 | Parameter subset 4->DIST | 011.013 | 0.1-4:0.01 |  | Zbw/Zfw PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 0.5 | 2 |  |  | Distance Circular\Starting | ZbwZfw | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Circular\Starting | ZbwZfw | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | ZbwZfw | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Polygonal\Starting | ZbwZfw | Real |  |  | 1 | 0
x011_u002E_015 | Parameter subset 4->DIST | 011.015 | 0.1-2:0.01 | Inom | IN> high range PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 0.2 | 2 |  |  | Distance Circular\Starting | INM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Circular\Starting | INM | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | INM | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Polygonal\Starting | INM | Real |  |  | 1 | 0
x011_u002E_017 | Parameter subset 4->DIST | 011.017 | 0-0.5:0.001 | s | tIN> PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 0.1 | 2 |  |  | Distance Circular\Starting | tINM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Circular\Starting | tINM | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | tINM | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Polygonal\Starting | tINM | Real |  |  | 1 | 0
x011_u002E_016 | Parameter subset 4->DIST | 011.016 | 0.02-1:0.01 | Vnom | VNG> PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 0.1 | 2 |  |  | Distance Circular\Starting | VNGM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Circular\Starting | VNGM | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | VNGM | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Polygonal\Starting | VNGM | Real |  |  | 1 | 0
x011_u002E_022 | Parameter subset 4->DIST | 011.022 | 0.2-1:0.01 | Vnom | VNG>> PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 0.5 | 2 |  |  | Distance Circular\Starting | VNGMM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Circular\Starting | VNGMM | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | VNGMM | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Polygonal\Starting | VNGMM | Real |  |  | 1 | 0
x011_u002E_021 | Parameter subset 4->DIST | 011.021 | 0-60:0.001 | s | tVNG>> PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 |  |  | Distance Circular\Starting | tVNGMM | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Circular\Starting | tVNGMM | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Starting | tVNGMM | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Polygonal\Starting | tVNGMM | Real |  |  | 1 | 0
x013_u002E_087 | Parameter subset 4->DIST | 013.087 | 0-8:0.01 |  | Abs. value kG PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 |  |  | Distance Circular\Polarisation | k0 | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Circular\Polarisation | k0 | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Polarisation | k0 | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Polygonal\Polarisation | k0 | Real |  |  | 1 | 0
x013_u002E_086 | Parameter subset 4->DIST | 013.086 | -180-180:1 | ° | Angle kG PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 0 | 2 |  |  | Distance Circular\Polarisation | phik0 | Real | 1 | 0 | 2 | Distance Circular;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Circular\Polarisation | phik0 | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Polarisation | phik0 | Real | 1 | 0 |  | Distance Polygonal;x003_u002E_060 | outserv | Real | E;E | 0;4 |  | Distance Polygonal\Polarisation | phik0 | Real |  |  | 1 | 0
x075_u002E_097 | Parameter subset 4->DIST | 075.097 | Circle¦0;Polygon¦1 |  | Characteristic PS4 | Enum | Parameters__Function_parameters | 0;1 | Real |  | x056_u002E_014;x031_u002E_073;x003_u002E_060 | E;E;E | 0;0;4 | 1 | 4 | E | 0 | Distance Circular | outserv | Real | 0 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Distance Circular | outserv | Real | E | 0 | 0 | 0
[16 empty] | E | 0 | Distance Polygonal | outserv | Real | 0 | 1 | [13 empty] | 1
[16 empty] | E | 1 | Distance Circular | outserv | Real | 0 | 1
[16 empty] | E | 1 | Distance Polygonal | outserv | Real | 0 | 0
x013_u002E_051 | Parameter subset 4->DIST | 013.051 | 0.1-200:0.01 | — | X1 (polygon) PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 10 |  |  |  | Distance Polygonal\Z1 | Xmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\Z1 | Xmax | Real |  |  | 1 | 0
x013_u002E_052 | Parameter subset 4->DIST | 013.052 | 0.1-200:0.01 | — | X2 (polygon) PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 20 |  |  |  | Distance Polygonal\Z2 | Xmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\Z2 | Xmax | Real |  |  | 1 | 0
x013_u002E_053 | Parameter subset 4->DIST | 013.053 | 0.1-200:0.01 | — | X3 (polygon) PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 30 |  |  |  | Distance Polygonal\Z3 | Xmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\Z3 | Xmax | Real |  |  | 1 | 0
x013_u002E_054 | Parameter subset 4->DIST | 013.054 | 0.1-200:0.01 | — | X4 (polygon) PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 40 |  |  |  | Distance Polygonal\Z4 | Xmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\Z4 | Xmax | Real |  |  | 1 | 0
x013_u002E_055 | Parameter subset 4->DIST | 013.055 | 0.1-200:0.01 | — | R1,PG (polygon) PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 10 |  |  |  | Distance Polygonal\Z1 | REmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\Z1 | REmax | Real |  |  | 1 | 0
x013_u002E_056 | Parameter subset 4->DIST | 013.056 | 0.1-200:0.01 | — | R1,PP (polygon) PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 10 |  |  |  | Distance Polygonal\Z1 | Rmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\Z1 | Rmax | Real |  |  | 1 | 0
x013_u002E_057 | Parameter subset 4->DIST | 013.057 | 0.1-200:0.01 | — | R2,PG (polygon) PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 20 |  |  |  | Distance Polygonal\Z2 | REmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\Z2 | REmax | Real |  |  | 1 | 0
x013_u002E_058 | Parameter subset 4->DIST | 013.058 | 0.1-200:0.01 | — | R2,PP (polygon) PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 20 |  |  |  | Distance Polygonal\Z2 | Rmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\Z2 | Rmax | Real |  |  | 1 | 0
x013_u002E_059 | Parameter subset 4->DIST | 013.059 | 0.1-200:0.01 | — | R3,PG (polygon) PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 30 |  |  |  | Distance Polygonal\Z3 | REmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\Z3 | REmax | Real |  |  | 1 | 0
x013_u002E_060 | Parameter subset 4->DIST | 013.060 | 0.1-200:0.01 | — | R3,PP (polygon) PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 30 |  |  |  | Distance Polygonal\Z3 | Rmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\Z3 | Rmax | Real |  |  | 1 | 0
x013_u002E_061 | Parameter subset 4->DIST | 013.061 | 0.1-200:0.01 | — | R4,PG (polygon) PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 40 |  |  |  | Distance Polygonal\Z4 | REmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\Z4 | REmax | Real |  |  | 1 | 0
x013_u002E_062 | Parameter subset 4->DIST | 013.062 | 0.1-200:0.01 | — | R4,PP (polygon) PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 40 |  |  |  | Distance Polygonal\Z4 | Rmax | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\Z4 | Rmax | Real |  |  | 1 | 0
x013_u002E_063 | Parameter subset 4->DIST | 013.063 | 40-90:1 | ° | €1 (polygon) PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 75 |  |  |  | Distance Polygonal\Z1 | phi | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\Z1 | phi | Real |  |  | 1 | 0
x013_u002E_064 | Parameter subset 4->DIST | 013.064 | 40-90:1 | ° | €2 (polygon) PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 75 |  |  |  | Distance Polygonal\Z2 | phi | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\Z2 | phi | Real |  |  | 1 | 0
x013_u002E_065 | Parameter subset 4->DIST | 013.065 | 40-90:1 | ° | €3 (polygon) PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 75 |  |  |  | Distance Polygonal\Z3 | phi | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\Z3 | phi | Real |  |  | 1 | 0
x013_u002E_066 | Parameter subset 4->DIST | 013.066 | 40-90:1 | ° | €4 (polygon) PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 75 |  |  |  | Distance Polygonal\Z4 | phi | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\Z4 | phi | Real |  |  | 1 | 0
x075_u002E_086 | Parameter subset 4->DIST | 075.086 | -20-20:1 | ° | ‹1 (polygon) PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 0 |  |  |  | Distance Polygonal\Z1 | beta | Real | -1 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\Z1 | beta | Real |  |  | -1 | 0
x075_u002E_087 | Parameter subset 4->DIST | 075.087 | -20-20:1 | ° | ‹2 (polygon) PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 0 |  |  |  | Distance Polygonal\Z2 | beta | Real | -1 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\Z2 | beta | Real |  |  | -1 | 0
x075_u002E_088 | Parameter subset 4->DIST | 075.088 | -20-20:1 | ° | ‹3 (polygon) PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 0 |  |  |  | Distance Polygonal\Z3 | beta | Real | -1 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\Z3 | beta | Real |  |  | -1 | 0
x075_u002E_089 | Parameter subset 4->DIST | 075.089 | -20-20:1 | ° | ‹4 (polygon) PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 0 |  |  |  | Distance Polygonal\Z4 | beta | Real | -1 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\Z4 | beta | Real |  |  | -1 | 0
x075_u002E_091 | Parameter subset 4->DIST | 075.091 | 0.05-200:0.01 | — | Z1 (circle) PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 10 |  |  |  | Distance Circular\Z1 | Zm | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Circular\Z1 | Zm | Real |  |  | 1 | 0
x075_u002E_092 | Parameter subset 4->DIST | 075.092 | 0.05-200:0.01 | — | Z2 (circle) PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 20 |  |  |  | Distance Circular\Z2 | Zm | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Circular\Z2 | Zm | Real |  |  | 1 | 0
x075_u002E_093 | Parameter subset 4->DIST | 075.093 | 0.05-200:0.01 | — | Z3 (circle) PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 30 |  |  |  | Distance Circular\Z3 | Zm | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Circular\Z3 | Zm | Real |  |  | 1 | 0
x075_u002E_094 | Parameter subset 4->DIST | 075.094 | 0.05-200:0.01 | — | Z4 (circle) PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 40 |  |  |  | Distance Circular\Z4 | Zm | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Circular\Z4 | Zm | Real |  |  | 1 | 0
x075_u002E_090 | Parameter subset 4->DIST | 075.090 | 10-90:1 | ° | €1 (circle) PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 75 | 2 |  |  | Distance Circular\Z1 | arcalpha | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Circular\Z1 | arcalpha | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z1E | arcalpha | Real | 1 | 0
x075_u002E_095 | Parameter subset 4->DIST | 075.095 | 10-90:1 | ° | €2 (circle) PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 75 |  |  |  | Distance Circular\Z2 | arcalpha | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Circular\Z2 | arcalpha | Real |  |  | 1 | 0
x075_u002E_096 | Parameter subset 4->DIST | 075.096 | 10-90:1 | ° | €3 (circle) PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 75 |  |  |  | Distance Circular\Z3 | arcalpha | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Circular\Z3 | arcalpha | Real |  |  | 1 | 0
x075_u002E_099 | Parameter subset 4->DIST | 075.099 | 10-90:1 | ° | €4 (circle) PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 75 |  |  |  | Distance Circular\Z4 | arcalpha | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Circular\Z4 | arcalpha | Real |  |  | 1 | 0
x012_u002E_092 | Parameter subset 4->DIST | 012.092 | No¦0;Yes¦1 |  | Arc comp. circle PS4 | Enum | Parameters__Function_parameters | 0;1 | Real |  | x003_u002E_060 | E | 4 | 0 | 5 |  |  | Distance Circular\Z1 | arcen | Real | 1 | 0 | 4 | Distance Circular;Distance Circular\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Circular\Z1 | arcen | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z1E | arcen | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Circular\Z2 | arcen | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z2 | arcen | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Circular\Z3 | arcen | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z3 | arcen | Real | 1 | 0 |  | Distance Circular;Distance Circular\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Circular\Z4 | arcen | Real |  |  | 1 | 0
[18 empty] | Distance Circular\Z4 | arcen | Real | 1 | 0
x013_u002E_073 | Parameter subset 4->DIST | 013.073 | Forward directional¦0;Backward directional¦1;Non-directional¦2 |  | Direction N1 PS4 | Enum | Parameters__Function_parameters | 0;1;2 | Real |  | x003_u002E_060 | E | 4 | 0 | 4 | NE | 2 | Distance Circular\Z1 | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Circular\Z1 | idir | Real |  |  | 1 | 0
[16 empty] | NE | 2 | Distance Circular\Z1E | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\Z1 | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z1 | idir | Real | 1 | 0
[18 empty] | Distance Polygonal\Z1E | idir | Real | 1 | 0
x013_u002E_074 | Parameter subset 4->DIST | 013.074 | Forward directional¦0;Backward directional¦1;Non-directional¦2 |  | Direction N2 PS4 | Enum | Parameters__Function_parameters | 0;1;2 | Real |  | x003_u002E_060 | E | 4 | 0 |  | NE | 2 | Distance Circular\Z2 | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Circular\Z2 | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z2 | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\Z2 | idir | Real |  |  | 1 | 0
x013_u002E_075 | Parameter subset 4->DIST | 013.075 | Forward directional¦0;Backward directional¦1;Non-directional¦2 |  | Direction N3 PS4 | Enum | Parameters__Function_parameters | 0;1;2 | Real |  | x003_u002E_060 | E | 4 | 0 |  | NE | 2 | Distance Circular\Z3 | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Circular\Z3 | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z3 | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\Z3 | idir | Real |  |  | 1 | 0
x013_u002E_076 | Parameter subset 4->DIST | 013.076 | Forward directional¦0;Backward directional¦1;Non-directional¦2 |  | Direction N4 PS4 | Enum | Parameters__Function_parameters | 0;1;2 | Real |  | x003_u002E_060 | E | 4 | 0 |  | NE | 2 | Distance Circular\Z4 | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Circular\Z4 | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z4 | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\Z4 | idir | Real |  |  | 1 | 0
x013_u002E_077 | Parameter subset 4->DIST | 013.077 | Forward directional¦0;Backward directional¦1;Non-directional¦2 |  | Direction N5 PS4 | Enum | Parameters__Function_parameters | 0;1;2 | Real |  | x003_u002E_060 | E | 4 | 0 |  |  |  | Distance Circular\Directional | idir | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Directional;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Circular\Directional | idir | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Directional | idir | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Directional;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\Directional | idir | Real |  |  | 1 | 0
x013_u002E_078 | Parameter subset 4->DIST | 013.078 | 0-10:0.001;Blocked=10.002 | s | t1 PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 0 | 4 | SE | 10 | Distance Circular\T1 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Circular\T1 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Circular\T1 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
[16 empty] | SE | 10 | Distance Polygonal\T1 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T1;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Polygonal\T1 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Polygonal\T1 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
x013_u002E_079 | Parameter subset 4->DIST | 013.079 | 0-10:0.001;Blocked=10.002 | s | t2 PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 | 4 | SE | 10 | Distance Circular\T2 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Circular\T2 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Circular\T2 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
[16 empty] | SE | 10 | Distance Polygonal\T2 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T2;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Polygonal\T2 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Polygonal\T2 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
x013_u002E_080 | Parameter subset 4->DIST | 013.080 | 0-10:0.001;Blocked=10.002 | s | t3 PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 2 | 4 | SE | 10 | Distance Circular\T3 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Circular\T3 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Circular\T3 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
[16 empty] | SE | 10 | Distance Polygonal\T3 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T3;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Polygonal\T3 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Polygonal\T3 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
x013_u002E_081 | Parameter subset 4->DIST | 013.081 | 0-10:0.001;Blocked=10.002 | s | t4 PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 3 | 4 | SE | 10 | Distance Circular\T4 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Circular\T4 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Circular\T4 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
[16 empty] | SE | 10 | Distance Polygonal\T4 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T4;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Polygonal\T4 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Polygonal\T4 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
x013_u002E_082 | Parameter subset 4->DIST | 013.082 | 0-10:0.001;Blocked=10.002 | s | t5 PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 4 | 4 | SE | 10 | Distance Circular\T5 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Circular\T5 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Circular\T5 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
[16 empty] | SE | 10 | Distance Polygonal\T5 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T5;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Polygonal\T5 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Polygonal\T5 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
x013_u002E_083 | Parameter subset 4->DIST | 013.083 | 0-10:0.001;Blocked=10.002 | s | t6 PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 5 | 4 | SE | 10 | Distance Circular\T6 | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\T6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Circular\T6 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Circular\T6 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
[16 empty] | SE | 10 | Distance Polygonal\T6 | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\T6;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Polygonal\T6 | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Polygonal\T6 | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
x013_u002E_085 | Parameter subset 4->DIST | 013.085 | 1-450:0.01 |  | kze,PP HSR PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1.2 | 3 |  |  | Distance Circular\Z1E | kZ | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\Z1E;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Circular\Z1E | kZ | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z1E | kX | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\Z1E;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\Z1E | kX | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\Z1E | kR | Real | 1 | 0
x015_u002E_017 | Parameter subset 4->PSIG | 015.017 | No¦0;Yes¦1 |  | Enable PS4 | Enum | Parameters__Function_parameters | 0;1 | String |  | x003_u002E_060 | E | 4 | 0 | 2 |  |  | Distance Circular\PSIG Connect | aDipset | String |  |  | 2 | Distance Circular;Distance Circular\PSIG Connect;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Circular\PSIG Connect | aDipset | String
[18 empty] | Distance Polygonal\PSIG Connect | aDipset | String |  |  |  | Distance Polygonal;Distance Polygonal\PSIG Connect;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\PSIG Connect | aDipset | String
x025_u002E_020 | Parameter subset 4->PSIG | 025.020 | Without¦0;Dir.trans.trip.under¦1;PUTT¦2;Zone extension¦3;Release scheme¦4;Blocking scheme¦5;DC loop operat. mode¦6;Reverse interlocking¦7;Direction comparison¦8 |  | Operating mode PS4 | Enum | Parameters__Function_parameters | ;DIRECT = TRIP;PUTT = TRIP;POTT = TRIP;COMP_RELEASE = TRIP;COMP_BLOCK = TRIP;COMP_PILOT = TRIP; | String |  | x003_u002E_060 | E | 4 | PUTT = TRIP | 4 |  |  | Distance Circular\PSIG Receive | sLogic | String |  |  | 2 | Distance Circular;Distance Circular\PSIG Receive;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Circular\PSIG Receive | sLogic | String
[18 empty] | Distance Circular\PSIG Send | sLogic | String |  |  |  | Distance Polygonal;Distance Polygonal\PSIG Receive;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\PSIG Receive | sLogic | String
[18 empty] | Distance Polygonal\PSIG Receive | sLogic | String
[18 empty] | Distance Polygonal\PSIG Send | sLogic | String
x025_u002E_023 | Parameter subset 4->PSIG | 025.023 | 0-10:0.001;Blocked=10.002 | s | Tripping time PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 0.08 | 4 | SE | 10 | Distance Circular\PSIG T | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\PSIG T;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Circular\PSIG T | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Circular\PSIG T | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
[16 empty] | SE | 10 | Distance Polygonal\PSIG T | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\PSIG T;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 | 2 | Distance Polygonal\PSIG T | Tdelay | Real | SE | 10 | 1 | 0
[16 empty] | G | 10 | Distance Polygonal\PSIG T | Tdelay | Real | 0 | 9999999 | [13 empty] | 10.002
x025_u002E_021 | Parameter subset 4->PSIG | 025.021 | 0-10:0.001 | s | Release t. send PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 0.25 | 2 |  |  | Distance Circular\PSIG T Reset | Tdelay | Real | 1 | 0 | 2 | Distance Circular;Distance Circular\PSIG T Reset;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Circular\PSIG T Reset | Tdelay | Real |  |  | 1 | 0
[18 empty] | Distance Polygonal\PSIG T Reset | Tdelay | Real | 1 | 0 |  | Distance Polygonal;Distance Polygonal\PSIG T Reset;x003_u002E_060 | outserv;outserv | Real;Real | E;E;E | 0;0;4 |  | Distance Polygonal\PSIG T Reset | Tdelay | Real |  |  | 1 | 0
x075_u002E_098 | Parameter subset 4->DTOC | 075.098 | No¦0;Yes¦1 |  | Enable PS4 | Enum | Parameters__Function_parameters | 1;0 | Real |  | x056_u002E_008;x003_u002E_060 | E;E | 0;4 | 1 | 12 |  |  | Overcurrent\I> | outserv | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 12 | Overcurrent\I> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\I>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\I>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\I>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\I>>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\I>>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\I>>>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\IN> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\IN> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\IN>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\IN>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\IN>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\IN>>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\IN>>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\IN>>>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\Ineg> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\Ineg> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\Ineg>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\Ineg>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\Ineg>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\Ineg>>> | outserv | Real | E | 0 | 0 | 0
[18 empty] | Overcurrent\Ineg>>>> | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\Ineg>>>> | outserv | Real |  |  | 1 | 0
x075_u002E_007 | Parameter subset 4->DTOC | 075.007 | 0.1-20:0.01 | Inom | I> PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 |  |  |  | Overcurrent\I> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\I> | Ipset | Real |  |  | 1 | 0
x075_u002E_008 | Parameter subset 4->DTOC | 075.008 | 0.1-20:0.01 | Inom | I>> PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 |  |  |  | Overcurrent\I>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\I>> | Ipset | Real |  |  | 1 | 0
x075_u002E_009 | Parameter subset 4->DTOC | 075.009 | 0.1-20:0.01 | Inom | I>>> PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 |  |  |  | Overcurrent\I>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\I>>> | Ipset | Real |  |  | 1 | 0
x075_u002E_010 | Parameter subset 4->DTOC | 075.010 | 0.1-20:0.01 | Inom | I>>>> PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 |  |  |  | Overcurrent\I>>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\I>>>> | Ipset | Real |  |  | 1 | 0
x075_u002E_019 | Parameter subset 4->DTOC | 075.019 | 0-30:0.001;Blocked=30.002 | s | tI> PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 | SE | 30 | Overcurrent\I> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Overcurrent\I> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\I> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x075_u002E_020 | Parameter subset 4->DTOC | 075.020 | 0-30:0.001;Blocked=30.002 | s | tI>> PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 | SE | 30 | Overcurrent\I>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Overcurrent\I>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\I>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x075_u002E_021 | Parameter subset 4->DTOC | 075.021 | 0-30:0.001;Blocked=30.002 | s | tI>>> PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 | SE | 30 | Overcurrent\I>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Overcurrent\I>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\I>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x075_u002E_022 | Parameter subset 4->DTOC | 075.022 | 0-30:0.001;Blocked=30.002 | s | tI>>>> PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 | SE | 30 | Overcurrent\I>>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Overcurrent\I>>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\I>>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x075_u002E_011 | Parameter subset 4->DTOC | 075.011 | 0.1-20:0.01 | Inom | Ineg> PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 |  |  |  | Overcurrent\IN> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\IN> | Ipset | Real |  |  | 1 | 0
x075_u002E_012 | Parameter subset 4->DTOC | 075.012 | 0.1-20:0.01 | Inom | Ineg>> PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 |  |  |  | Overcurrent\IN>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\IN>> | Ipset | Real |  |  | 1 | 0
x075_u002E_013 | Parameter subset 4->DTOC | 075.013 | 0.1-20:0.01 | Inom | Ineg>>> PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 |  |  |  | Overcurrent\IN>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\IN>>> | Ipset | Real |  |  | 1 | 0
x075_u002E_014 | Parameter subset 4->DTOC | 075.014 | 0.1-20:0.01 | Inom | Ineg>>>> PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 |  |  |  | Overcurrent\IN>>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\IN>>>> | Ipset | Real |  |  | 1 | 0
x075_u002E_023 | Parameter subset 4->DTOC | 075.023 | 0-30:0.001;Blocked=30.002 | s | tIneg> PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 | SE | 30 | Overcurrent\IN> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Overcurrent\IN> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\IN> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x075_u002E_024 | Parameter subset 4->DTOC | 075.024 | 0-30:0.001;Blocked=30.002 | s | tIneg>> PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 | SE | 30 | Overcurrent\IN>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Overcurrent\IN>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\IN>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x075_u002E_025 | Parameter subset 4->DTOC | 075.025 | 0-30:0.001;Blocked=30.002 | s | tIneg>>> PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 | SE | 30 | Overcurrent\IN>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Overcurrent\IN>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\IN>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x075_u002E_026 | Parameter subset 4->DTOC | 075.026 | 0-30:0.001;Blocked=30.002 | s | tIneg>>>> PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 | SE | 30 | Overcurrent\IN>>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Overcurrent\IN>>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\IN>>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x075_u002E_015 | Parameter subset 4->DTOC | 075.015 | 0.1-20:0.01 | Inom | IN> PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 |  |  |  | Overcurrent\Ineg> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\Ineg> | Ipset | Real |  |  | 1 | 0
x075_u002E_016 | Parameter subset 4->DTOC | 075.016 | 0.1-20:0.01 | Inom | IN>> PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 |  |  |  | Overcurrent\Ineg>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\Ineg>> | Ipset | Real |  |  | 1 | 0
x075_u002E_017 | Parameter subset 4->DTOC | 075.017 | 0.1-20:0.01 | Inom | IN>>> PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 |  |  |  | Overcurrent\Ineg>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\Ineg>>> | Ipset | Real |  |  | 1 | 0
x075_u002E_018 | Parameter subset 4->DTOC | 075.018 | 0.1-20:0.01 | Inom | IN>>>> PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 |  |  |  | Overcurrent\Ineg>>>> | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\Ineg>>>> | Ipset | Real |  |  | 1 | 0
x075_u002E_027 | Parameter subset 4->DTOC | 075.027 | 0-30:0.001;Blocked=30.002 | s | tIN> PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 | SE | 30 | Overcurrent\Ineg> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Overcurrent\Ineg> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\Ineg> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x075_u002E_028 | Parameter subset 4->DTOC | 075.028 | 0-30:0.001;Blocked=30.002 | s | tIN>> PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 | SE | 30 | Overcurrent\Ineg>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Overcurrent\Ineg>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\Ineg>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x075_u002E_029 | Parameter subset 4->DTOC | 075.029 | 0-30:0.001;Blocked=30.002 | s | tIN>>> PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 | SE | 30 | Overcurrent\Ineg>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Overcurrent\Ineg>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\Ineg>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x075_u002E_030 | Parameter subset 4->DTOC | 075.030 | 0-30:0.001;Blocked=30.002 | s | tIN>>>> PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 | SE | 30 | Overcurrent\Ineg>>>> | Tset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Overcurrent\Ineg>>>> | Tset | Real | SE | 30 | 1 | 0
[16 empty] | G | 30 | Overcurrent\Ineg>>>> | Tset | Real | 0 | 9999999 | [13 empty] | 30.002
x075_u002E_000 | Parameter subset 4->IDMT | 075.000 | No¦0;Yes¦1 |  | Enable P PS4 | Enum | Parameters__Function_parameters | 1;0 | Real |  | x056_u002E_009;x003_u002E_060 | E;E | 0;4 | 1 |  |  |  | Overcurrent\IDMT P | outserv | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\IDMT P | outserv | Real |  |  | 1 | 0
x075_u002E_050 | Parameter subset 4->IDMT | 075.050 | 0.1-4:0.01 | Inom | Iref,P PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 |  |  |  | Overcurrent\IDMT P | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\IDMT P | Ipset | Real |  |  | 1 | 0
x075_u002E_056 | Parameter subset 4->IDMT | 075.056 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Characterist. P PS4 | Enum | Parameters__Function_parameters | Definite Time;IEC 255-3 Standard Inverse;IEC 255-3 Very Inverse;IEC 255-3 Extremly Inverse;IEC 255-3 Long-Time Inverse;IEEE C37.112 Moderately Inverse;IEEE C37.112 Very Inverse;IEEE C37.112 Extremely Inverse;ANSI Normally Inverse;ANSI Short-Time Inverse;ANSI Long-Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | [8 empty] | Overcurrent\IDMT P | pcharac |  |  |  |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\IDMT P | pcharac
x075_u002E_053 | Parameter subset 4->IDMT | 075.053 | 0.01-10:0.01 |  | Ch. factor kt,P PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 |  |  |  | Overcurrent\IDMT P | Tpset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\IDMT P | Tpset | Real |  |  | 1 | 0
x075_u002E_059 | Parameter subset 4->IDMT | 075.059 | Without delay¦0;Delayed as per char.¦1 |  | Reset P PS4 | Enum | Parameters__Function_parameters | 0;1 | Real | 3 | x003_u002E_060;x075_u002E_056 | E;SW | 4;IEEE | 0 |  |  |  | Overcurrent\IDMT P | resetdis | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\IDMT P | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x075_u002E_056 | E;SW | 4;ANSI |  |  |  |  | Overcurrent\IDMT P | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | 4 |  |  |  |  | Overcurrent\IDMT P | resetdis | Real | 0 | 0
x075_u002E_062 | Parameter subset 4->IDMT | 075.062 | Forward directional¦0;Backward directional¦1;Non-directional¦2 |  | Direction P PS4 | Enum | Parameters__Function_parameters | 1;2;0 | Real |  | x003_u002E_060 | E | 4 | 1 |  |  |  | Overcurrent\IDMT P | idir | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\IDMT P | idir | Real |  |  | 1 | 0
x075_u002E_001 | Parameter subset 4->IDMT | 075.001 | No¦0;Yes¦1 |  | Enable neg. PS4 | Enum | Parameters__Function_parameters | 1;0 | Real |  | x056_u002E_009;x003_u002E_060 | E;E | 0;4 | 1 |  |  |  | Overcurrent\IDMT neg | outserv | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\IDMT neg | outserv | Real |  |  | 1 | 0
x075_u002E_051 | Parameter subset 4->IDMT | 075.051 | 0.1-4:0.01 | Inom | Iref,neg PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 |  |  |  | Overcurrent\IDMT neg | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\IDMT neg | Ipset | Real |  |  | 1 | 0
x075_u002E_057 | Parameter subset 4->IDMT | 075.057 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Character. neg. PS4 | Enum | Parameters__Function_parameters | Definite Time;IEC 255-3 Standard Inverse;IEC 255-3 Very Inverse;IEC 255-3 Extremly Inverse;IEC 255-3 Long-Time Inverse;IEEE C37.112 Moderately Inverse;IEEE C37.112 Very Inverse;IEEE C37.112 Extremely Inverse;ANSI Normally Inverse;ANSI Short-Time Inverse;ANSI Long-Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | [8 empty] | Overcurrent\IDMT neg | pcharac |  |  |  |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\IDMT neg | pcharac
x075_u002E_054 | Parameter subset 4->IDMT | 075.054 | 0.01-10:0.01 |  | Factor kt,neg PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 |  |  |  | Overcurrent\IDMT neg | Tpset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\IDMT neg | Tpset | Real |  |  | 1 | 0
x075_u002E_060 | Parameter subset 4->IDMT | 075.060 | Without delay¦0;Delayed as per char.¦1 |  | Reset neg. PS4 | Enum | Parameters__Function_parameters | 0;1 | Real | 3 | x003_u002E_060;x075_u002E_057 | E;SW | 4;IEEE | 0 |  |  |  | Overcurrent\IDMT neg | resetdis | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\IDMT neg | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x075_u002E_057 | E;SW | 4;ANSI |  |  |  |  | Overcurrent\IDMT neg | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | 4 |  |  |  |  | Overcurrent\IDMT neg | resetdis | Real | 0 | 0
x075_u002E_063 | Parameter subset 4->IDMT | 075.063 | Forward directional¦0;Backward directional¦1;Non-directional¦2 |  | Direction neg. PS4 | Enum | Parameters__Function_parameters | 1;2;0 | Real |  | x003_u002E_060 | E | 4 | 1 |  |  |  | Overcurrent\IDMT neg | idir | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\IDMT neg | idir | Real |  |  | 1 | 0
x075_u002E_002 | Parameter subset 4->IDMT | 075.002 | No¦0;Yes¦1 |  | Enable N PS4 | Enum | Parameters__Function_parameters | 1;0 | Real |  | x056_u002E_009;x003_u002E_060 | E;E | 0;4 | 1 |  |  |  | Overcurrent\IDMT N | outserv | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\IDMT N | outserv | Real |  |  | 1 | 0
x075_u002E_052 | Parameter subset 4->IDMT | 075.052 | 0.1-4:0.01 | Inom | Iref,N PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 |  |  |  | Overcurrent\IDMT N | Ipset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\IDMT N | Ipset | Real |  |  | 1 | 0
x075_u002E_058 | Parameter subset 4->IDMT | 075.058 | Definite Time¦0;IEC Standard Inverse¦1;IEC Very Inverse¦2;IEC Extr. Inverse¦3;IEC Long Time Inv.¦4;IEEE Moderately Inv.¦5;IEEE Very Inverse¦6;IEEE Extremely Inv.¦7;ANSI Normally Inv.¦8;ANSI Short Time Inv.¦9;ANSI Long Time Inv.¦10;RI-Type Inverse¦11;RXIDG-Type Inverse¦12 |  | Characterist. N PS4 | Enum | Parameters__Function_parameters | Definite Time;IEC 255-3 Standard Inverse;IEC 255-3 Very Inverse;IEC 255-3 Extremly Inverse;IEC 255-3 Long-Time Inverse;IEEE C37.112 Moderately Inverse;IEEE C37.112 Very Inverse;IEEE C37.112 Extremely Inverse;ANSI Normally Inverse;ANSI Short-Time Inverse;ANSI Long-Time Inverse;RI-Type Inverse;RXIDG-Type Inverse | String | [8 empty] | Overcurrent\IDMT N | pcharac |  |  |  |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\IDMT N | pcharac
x075_u002E_055 | Parameter subset 4->IDMT | 075.055 | 0.01-10:0.01 |  | Factor kt,N PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 |  |  |  | Overcurrent\IDMT N | Tpset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\IDMT N | Tpset | Real |  |  | 1 | 0
x075_u002E_061 | Parameter subset 4->IDMT | 075.061 | Without delay¦0;Delayed as per char.¦1 |  | Reset N PS4 | Enum | Parameters__Function_parameters | 0;1 | Real | 3 | x003_u002E_060;x075_u002E_058 | E;SW | 4;IEEE | 0 |  |  |  | Overcurrent\IDMT neg | resetdis | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\IDMT neg | resetdis | Real |  |  | 1 | 0
[11 empty] | x003_u002E_060;x075_u002E_058 | E;SW | 4;ANSI |  |  |  |  | Overcurrent\IDMT neg | resetdis | Real | 1 | 0
[11 empty] | x003_u002E_060 | E | 4 |  |  |  |  | Overcurrent\IDMT neg | resetdis | Real | 0 | 0
x075_u002E_064 | Parameter subset 4->IDMT | 075.064 | Forward directional¦0;Backward directional¦1;Non-directional¦2 |  | Direction N PS4 | Enum | Parameters__Function_parameters | 1;2;0 | Real |  | x003_u002E_060 | E | 4 | 1 |  |  |  | Overcurrent\IDMT N | idir | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Overcurrent\IDMT N | idir | Real |  |  | 1 | 0
x079_u002E_000 | Parameter subset 4->V<> | 079.000 | No¦0;Yes¦1 |  | Enable PS4 | Enum | Parameters__Function_parameters | 1;0 | Real |  | x056_u002E_010;x003_u002E_060 | E;E | 0;4 | 1 |  |  |  | Voltage | outserv | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 |  | Voltage | outserv | Real |  |  | 1 | 0
x079_u002E_001 | Parameter subset 4->V<> | 079.001 | Delta¦0;Star¦1 |  | Operating mode PS4 | Enum | Parameters__Function_parameters | 0;1 | Real |  | x079_u002E_000;x003_u002E_060 | E;E | 0;4 | 0 | 4 | E | 1 | Voltage\V> | outserv | Real | 0 | 1
[16 empty] | E | 1 | Voltage\V>> | outserv | Real | 0 | 1
[16 empty] | E | 1 | Voltage\V< | outserv | Real | 0 | 1
[16 empty] | E | 1 | Voltage\V<< | outserv | Real | 0 | 1
x079_u002E_003 | Parameter subset 4->V<> | 079.003 | 0.2-1.5:0.01;Blocked=1.52 | Vnom(/©3) | V> PS4 | Real | Parameters__Function_parameters |  |  |  | x079_u002E_001;x003_u002E_060 | E;E | 0;4 | 1.1 | 3 | SE | 1.5 | Voltage\V> | Uset | Real | 1 | 0 |  | x079_u002E_001;x003_u002E_060 |  |  | E;E | 0;4 | 2 | Voltage\V> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V> | outserv | Real | 0 | 0 | [7 empty] | Voltage\V> | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\V> | outserv | Real | 0 | 1
x079_u002E_004 | Parameter subset 4->V<> | 079.004 | 0.2-1.5:0.01;Blocked=1.52 | Vnom(/©3) | V>> PS4 | Real | Parameters__Function_parameters |  |  |  | x079_u002E_001;x003_u002E_060 | E;E | 0;4 | 1.1 | 3 | SE | 1.5 | Voltage\V>> | Uset | Real | 1 | 0 |  | x079_u002E_001;x003_u002E_060 |  |  | E;E | 0;4 | 2 | Voltage\V>> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\V>> | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\V>> | outserv | Real | 0 | 1
x079_u002E_005 | Parameter subset 4->V<> | 079.005 | 0-100:0.01;Blocked=100.02 | s | tV> PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 | SE | 100 | Voltage\V> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Voltage\V> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x079_u002E_006 | Parameter subset 4->V<> | 079.006 | 0-100:0.01;Blocked=100.02 | s | tV>> PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 | SE | 100 | Voltage\V>> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Voltage\V>> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V>> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x079_u002E_007 | Parameter subset 4->V<> | 079.007 | 0.2-1.5:0.01;Blocked=1.52 | Vnom(/©3) | V< PS4 | Real | Parameters__Function_parameters |  |  |  | x079_u002E_001;x003_u002E_060 | E;E | 0;4 | 0.8 | 3 | SE | 1.5 | Voltage\V< | Uset | Real | 1 | 0 |  | x079_u002E_001;x003_u002E_060 |  |  | E;E | 0;4 | 2 | Voltage\V< | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V< | outserv | Real | 0 | 0 | [7 empty] | Voltage\V< | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\V< | outserv | Real | 0 | 1
x079_u002E_008 | Parameter subset 4->V<> | 079.008 | 0.2-1.5:0.01;Blocked=1.52 | Vnom(/©3) | V<< PS4 | Real | Parameters__Function_parameters |  |  |  | x079_u002E_001;x003_u002E_060 | E;E | 0;4 | 0.8 | 3 | SE | 1.5 | Voltage\V<< | Uset | Real | 1 | 0 |  | x079_u002E_001;x003_u002E_060 |  |  | E;E | 0;4 | 2 | Voltage\V<< | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\V<< | outserv | Real | 0 | 0 | [7 empty] | Voltage\V<< | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\V<< | outserv | Real | 0 | 1
x079_u002E_009 | Parameter subset 4->V<> | 079.009 | 0-100:0.01;Blocked=100.02 | s | tV< PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 | SE | 100 | Voltage\V< | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Voltage\V< | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V< | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x079_u002E_010 | Parameter subset 4->V<> | 079.010 | 0-100:0.01;Blocked=100.02 | s | tV<< PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 | SE | 100 | Voltage\V<< | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Voltage\V<< | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\V<< | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x079_u002E_015 | Parameter subset 4->V<> | 079.015 | 0.2-1.5:0.01;Blocked=1.52 | Vnom/©3 | Vpos> PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1.1 | 3 | SE | 1.5 | Voltage\Vpos> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Voltage\Vpos> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos> | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vpos> | outserv | Real | 0 | 1
x079_u002E_016 | Parameter subset 4->V<> | 079.016 | 0.2-1.5:0.01;Blocked=1.52 | Vnom/©3 | Vpos>> PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1.1 | 3 | SE | 1.5 | Voltage\Vpos>> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Voltage\Vpos>> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos>> | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vpos>> | outserv | Real | 0 | 1
x079_u002E_017 | Parameter subset 4->V<> | 079.017 | 0-100:0.01;Blocked=100.02 | s | tVpos> PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 | SE | 100 | Voltage\Vpos> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Voltage\Vpos> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vpos> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x079_u002E_018 | Parameter subset 4->V<> | 079.018 | 0-100:0.01;Blocked=100.02 | s | tVpos>> PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 | SE | 100 | Voltage\Vpos>> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Voltage\Vpos>> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vpos>> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x079_u002E_019 | Parameter subset 4->V<> | 079.019 | 0.2-1.5:0.01;Blocked=1.52 | Vnom/©3 | Vpos< PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 0.8 | 3 | SE | 1.5 | Voltage\Vpos< | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Voltage\Vpos< | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos< | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos< | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vpos< | outserv | Real | 0 | 1
x079_u002E_020 | Parameter subset 4->V<> | 079.020 | 0.2-1.5:0.01;Blocked=1.52 | Vnom/©3 | Vpos<< PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 0.8 | 3 | SE | 1.5 | Voltage\Vpos<< | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Voltage\Vpos<< | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vpos<< | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vpos<< | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vpos<< | outserv | Real | 0 | 1
x079_u002E_021 | Parameter subset 4->V<> | 079.021 | 0-100:0.01;Blocked=100.02 | s | tVpos< PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 | SE | 100 | Voltage\Vpos< | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Voltage\Vpos< | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vpos< | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x079_u002E_022 | Parameter subset 4->V<> | 079.022 | 0-100:0.01;Blocked=100.02 | s | tVpos<< PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 | SE | 100 | Voltage\Vpos<< | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Voltage\Vpos<< | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vpos<< | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x079_u002E_023 | Parameter subset 4->V<> | 079.023 | 0.2-1.5:0.01;Blocked=1.52 | Vnom/©3 | Vneg> PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1.52 | 3 | SE | 1.5 | Voltage\Vneg> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Voltage\Vneg> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vneg> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vneg> | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vneg> | outserv | Real | 0 | 1
x079_u002E_024 | Parameter subset 4->V<> | 079.024 | 0.2-1.5:0.01;Blocked=1.52 | Vnom/©3 | Vneg>> PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1.52 | 3 | SE | 1.5 | Voltage\Vneg>> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Voltage\Vneg>> | outserv | Real | E | 1 | 0 | 1.52
[16 empty] | SE | 1.5 | Voltage\Vneg>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\Vneg>> | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1.5 | Voltage\Vneg>> | outserv | Real | 0 | 1
x079_u002E_025 | Parameter subset 4->V<> | 079.025 | 0-100:0.01;Blocked=100.02 | s | tVneg> PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 | SE | 100 | Voltage\Vneg> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Voltage\Vneg> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vneg> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x079_u002E_026 | Parameter subset 4->V<> | 079.026 | 0-100:0.01;Blocked=100.02 | s | tVneg>> PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 | SE | 100 | Voltage\Vneg>> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Voltage\Vneg>> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\Vneg>> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x079_u002E_011 | Parameter subset 4->V<> | 079.011 | 0.02-1:0.01;Blocked=1.02 | Vnom(/©3) | VNG> PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1.02 | 3 | SE | 1 | Voltage\VNG> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Voltage\VNG> | outserv | Real | E | 1 | 0 | 1.02
[16 empty] | SE | 1 | Voltage\VNG> | outserv | Real | 0 | 0 | [7 empty] | Voltage\VNG> | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1 | Voltage\VNG> | outserv | Real | 0 | 1
x079_u002E_012 | Parameter subset 4->V<> | 079.012 | 0.02-1:0.01;Blocked=1.02 | Vnom(/©3) | VNG>> PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1.02 | 3 | SE | 1 | Voltage\VNG>> | Uset | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Voltage\VNG>> | outserv | Real | E | 1 | 0 | 1.02
[16 empty] | SE | 1 | Voltage\VNG>> | outserv | Real | 0 | 0 | [7 empty] | Voltage\VNG>> | Uset | Real |  |  | 1 | 0
[16 empty] | G | 1 | Voltage\VNG>> | outserv | Real | 0 | 1
x079_u002E_013 | Parameter subset 4->V<> | 079.013 | 0-100:0.01;Blocked=100.02 | s | tVNG> PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 | SE | 100 | Voltage\VNG> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Voltage\VNG> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\VNG> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
x079_u002E_014 | Parameter subset 4->V<> | 079.014 | 0-100:0.01;Blocked=100.02 | s | tVNG>> PS4 | Real | Parameters__Function_parameters |  |  |  | x003_u002E_060 | E | 4 | 1 | 2 | SE | 100 | Voltage\VNG>> | Tdel | Real | 1 | 0 |  | x003_u002E_060 |  |  | E | 4 | 2 | Voltage\VNG>> | Tdel | Real | SE | 100 | 1 | 0
[16 empty] | G | 100 | Voltage\VNG>> | Tdel | Real | 0 | 9999999 | [13 empty] | 100.02
_END_