## Mapping
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37
StationWare | [6 empty] | Common |  |  | Import | [12 empty] | Export
[8 empty] | Enumeration |  | Pre-Condition |  |  |  |  | Instruction | [7 empty] | Pre-Condition | [5 empty] | Instruction
Key | Chapter | Display name | Range | Unit | Description | Type | Group | Mapping | Type |  | Setting | Operator | Value | Default |  | Operator | Value | Target | Parameter | Type | Scale | Offset |  | Source | Parameter | Type | Operator | Value |  | Source | Parameter | Type | Operator | Value | Scale | Offset
HW_Configuration_u002D__gt_AIM__2_u003A_CTsec1 | HW Configuration->AIM_2 | CTsec1 | 0.1-10:0.1 | A | Rated CT secondary current | Real | IED_Configuration | [7 empty] | 3 |  |  | Measurement | Inom | Real | 1 | 0
[18 empty] | Measurement Delta | Inom | Real | 1 | 0
[18 empty] | Measurement Seq | Inom | Real | 1 | 0
HW_Configuration_u002D__gt_AIM__2_u003A_CTsec5 | HW Configuration->AIM_2 | CTsec5 | 0.1-10:0.1 | A | Rated CT secondary current | Real | IED_Configuration | [10 empty] | Measurement Zero Seq | Inom | Real | 1 | 0
HW_Configuration_u002D__gt_AIM__2_u003A_VTsec7 | HW Configuration->AIM_2 | VTsec7 | 0.001-999.999:0.001 | V | Rated VT secondary voltage | Real | IED_Configuration | [7 empty] | 2 |  |  | Measurement Delta | Unom | Real | 1 | 0
[18 empty] | Measurement Seq | Unom | Real | 1 | 0
Current_protection_u002D__gt_EFHPTOC_u003A__1_u003A_Operation | Current protection->EFHPTOC: 1 | Operation | Off;On |  | Operation Off / On | Enum | Application_Configuration | 1;0 | Real | [8 empty] | Earth-fault\EFHPTOC1 | outserv | Real | 1 | 0 | [7 empty] | Earth-fault\EFHPTOC1 | outserv | Real |  |  | 1 | 0
Current_protection_u002D__gt_EFHPTOC_u003A__1_u003A_Reset_delay_time | Current protection->EFHPTOC: 1 | Reset delay time | 0-60:0.001 | s | Reset delay time | Real | Application_Configuration | [10 empty] | Earth-fault\EFHPTOC1 | ResetT | Real | 1 | 0 | [7 empty] | Earth-fault\EFHPTOC1 | ResetT | Real |  |  | 1 | 0
Current_protection_u002D__gt_EFHPTOC_u003A__1_u003A_Minimum_operate_time | Current protection->EFHPTOC: 1 | Minimum operate time | 0.02-60:0.001 | s | Minimum operate time for IDMT curves | Real | Application_Configuration |  |  |  | Current_protection_u002D__gt_EFHPTOC_u003A__1_u003A_Operating_curve_type | NEW | Time |  |  |  |  | Earth-fault\EFHPTOC1 | udeftmin | Real | 1 | 0 |  | Earth-fault\EFHPTOC1 | pcharac |  | NEW | Time |  | Earth-fault\EFHPTOC1 | udeftmin | Real |  |  | 1 | 0
Current_protection_u002D__gt_EFLPTOC_u003A__1_u003A_Operation | Current protection->EFLPTOC: 1 | Operation | Off;On |  | Operation Off / On | Enum | Application_Configuration | 1;0 | Real | [8 empty] | Earth-fault\EFLPTOC1 | outserv | Real | 1 | 0 | [7 empty] | Earth-fault\EFLPTOC1 | outserv | Real |  |  | 1 | 0
Current_protection_u002D__gt_EFLPTOC_u003A__1_u003A_Reset_delay_time | Current protection->EFLPTOC: 1 | Reset delay time | 0-60:0.001 | s | Reset delay time | Real | Application_Configuration | [10 empty] | Earth-fault\EFLPTOC1 | ResetT | Real | 1 | 0 | [7 empty] | Earth-fault\EFLPTOC1 | ResetT | Real |  |  | 1 | 0
Current_protection_u002D__gt_EFLPTOC_u003A__1_u003A_Minimum_operate_time | Current protection->EFLPTOC: 1 | Minimum operate time | 0.04-60:0.001 | s | Minimum operate time for IDMT curves | Real | Application_Configuration |  |  |  | Current_protection_u002D__gt_EFLPTOC_u003A__1_u003A_Operating_curve_type | NEW | Time |  |  |  |  | Earth-fault\EFLPTOC1 | udeftmin | Real | 1 | 0 |  | Earth-fault\EFLPTOC1 | pcharac |  | NEW | Time | 2 | Earth-fault\EFLPTOC1 | udeftmin | Real | GE | 0.04 | 1 | 0
0.04
Current_protection_u002D__gt_LOFLPTUC_u003A__1_u003A_Operation | Current protection->LOFLPTUC: 1 | Operation | Off;On |  | Operation On / Off | Enum | Application_Configuration | 1;0 | Real | [8 empty] | Loss of load | outserv | Real | 1 | 0 | [7 empty] | Loss of load | outserv | Real |  |  | 1 | 0
Current_protection_u002D__gt_PHLPTOC_u003A__1_u003A_Operation | Current protection->PHLPTOC: 1 | Operation | Off;On |  | Operation Off / On | Enum | Application_Configuration | 1;0 | Real | [8 empty] | Overcurrent\PHLPTOC1 | outserv | Real | 1 | 0 | [7 empty] | Overcurrent\PHLPTOC1 | outserv | Real |  |  | 1 | 0
Current_protection_u002D__gt_PHLPTOC_u003A__1_u003A_Reset_delay_time | Current protection->PHLPTOC: 1 | Reset delay time | 0-60:0.001 | s | Reset delay time | Real | Application_Configuration | [10 empty] | Overcurrent\PHLPTOC1 | ResetT | Real | 1 | 0 | [7 empty] | Overcurrent\PHLPTOC1 | ResetT | Real |  |  | 1 | 0
Current_protection_u002D__gt_PHLPTOC_u003A__1_u003A_Minimum_operate_time | Current protection->PHLPTOC: 1 | Minimum operate time | 0.04-60:0.001 | s | Minimum operate time for IDMT curves | Real | Application_Configuration |  |  |  | Current_protection_u002D__gt_PHLPTOC_u003A__1_u003A_Operating_curve_type | NEW | Time |  |  |  |  | Overcurrent\PHLPTOC1 | udeftmin | Real | 1 | 0 |  | Overcurrent\PHLPTOC1 | pcharac |  | NEW | Time | 2 | Overcurrent\PHLPTOC1 | udeftmin | Real | GE | 0.04 | 1 | 0
0.04
Current_protection_u002D__gt_MNSPTOC_u003A__1_u003A_Operation | Current protection->MNSPTOC: 1 | Operation | Off;On |  | Operation Off / On | Enum | Application_Configuration | 1;0 | Real | [8 empty] | Unbalance\MNSPTOC1 | outserv | Real | 1 | 0 | [7 empty] | Unbalance\MNSPTOC1 | outserv | Real |  |  | 1 | 0
Current_protection_u002D__gt_MNSPTOC_u003A__1_u003A_Reset_delay_time | Current protection->MNSPTOC: 1 | Reset delay time | 0-60:0.01 | s | Resetting time of the operate time counter in DT mode | Real | Application_Configuration |  |  |  | Current_protection_u002D__gt_MNSPTOC_u003A__1_u003A_Operating_curve_type | EW | Time (46) |  |  |  |  | Unbalance\MNSPTOC1 | ResetT | Real | 1 | 0 |  | Unbalance\MNSPTOC1 | pcharac |  | EW | Time (46) |  | Unbalance\MNSPTOC1 | ResetT | Real |  |  | 1 | 0
Current_protection_u002D__gt_MNSPTOC_u003A__2_u003A_Operation | Current protection->MNSPTOC: 2 | Operation | Off;On |  | Operation Off / On | Enum | Application_Configuration | 1;0 | Real | [8 empty] | Unbalance\MNSPTOC2 | outserv | Real | 1 | 0 | [7 empty] | Unbalance\MNSPTOC2 | outserv | Real |  |  | 1 | 0
Current_protection_u002D__gt_MNSPTOC_u003A__2_u003A_Reset_delay_time | Current protection->MNSPTOC: 2 | Reset delay time | 0-60:0.01 | s | Resetting time of the operate time counter in DT mode | Real | Application_Configuration |  |  |  | Current_protection_u002D__gt_MNSPTOC_u003A__2_u003A_Operating_curve_type | EW | Time (46) |  |  |  |  | Unbalance\MNSPTOC2 | ResetT | Real | 1 | 0 |  | Unbalance\MNSPTOC2 | pcharac |  | EW | Time (46) |  | Unbalance\MNSPTOC2 | ResetT | Real |  |  | 1 | 0
Voltage_protection_u002D__gt_NSPTOV_u003A__1_u003A_Operation | Voltage protection->NSPTOV: 1 | Operation | Off;On |  | Operation Off/On | Enum | Application_Configuration | 1;0 | Real | [8 empty] | Under-Overvoltage\NSPTOV1 | outserv | Real | 1 | 0 | [7 empty] | Under-Overvoltage\NSPTOV1 | outserv | Real |  |  | 1 | 0
Voltage_protection_u002D__gt_NSPTOV_u003A__1_u003A_Reset_delay_time | Voltage protection->NSPTOV: 1 | Reset delay time | 0-60:0.001 | s | Reset delay time | Real | Application_Configuration | [10 empty] | Under-Overvoltage\NSPTOV1 | ResetT | Real | 1 | 0 | [7 empty] | Under-Overvoltage\NSPTOV1 | ResetT | Real |  |  | 1 | 0
Voltage_protection_u002D__gt_PHPTOV_u003A__1_u003A_Operation | Voltage protection->PHPTOV: 1 | Operation | Off;On |  | Operation Off/On | Enum | Application_Configuration | 1;0 | Real | [8 empty] | Under-Overvoltage\PHPTOV1 PhPh | outserv | Real | 1 | 0 | [7 empty] | Under-Overvoltage\PHPTOV1 PhPh | outserv | Real |  |  | 1 | 0
Voltage_protection_u002D__gt_PHPTOV_u003A__1_u003A_Reset_delay_time | Voltage protection->PHPTOV: 1 | Reset delay time | 0-60:0.001 | s | Delay time provided to reset the timers | Real | Application_Configuration |  |  |  | Voltage_protection_u002D__gt_PHPTOV_u003A__1_u003A_Operating_curve_type | EW | Time (59) |  |  |  |  | Under-Overvoltage\PHPTOV1 PhPh | ResetT | Real | 1 | 0 |  | Under-Overvoltage\PHPTOV1 PhPh | pcharac |  | EW | Time (59) |  | Under-Overvoltage\PHPTOV1 PhPh | ResetT | Real |  |  | 1 | 0
Voltage_protection_u002D__gt_PHPTOV_u003A__1_u003A_Minimum_operate_time | Voltage protection->PHPTOV: 1 | Minimum operate time | 0.04-60:0.001 | s | Minimum operate time delay for IDMT curves | Real | Application_Configuration |  |  |  | Voltage_protection_u002D__gt_PHPTOV_u003A__1_u003A_Operating_curve_type | NEW | Time (59) |  |  |  |  | Under-Overvoltage\PHPTOV1 PhPh | udeftmin | Real | 1 | 0 |  | Under-Overvoltage\PHPTOV1 PhPh | pcharac |  | NEW | Time (59) |  | Under-Overvoltage\PHPTOV1 PhPh | udeftmin | Real |  |  | 1 | 0
Voltage_protection_u002D__gt_PHPTUV_u003A__1_u003A_Operation | Voltage protection->PHPTUV: 1 | Operation | Off;On |  | Operation Off/On | Enum | Application_Configuration | 1;0 | Real | [8 empty] | Under-Overvoltage\PHPTUV1 PhPh | outserv | Real | 1 | 0 | [7 empty] | Under-Overvoltage\PHPTUV1 PhPh | outserv | Real |  |  | 1 | 0
Voltage_protection_u002D__gt_PHPTUV_u003A__1_u003A_Reset_delay_time | Voltage protection->PHPTUV: 1 | Reset delay time | 0-60:0.001 | s | Delay time provided to reset the timers | Real | Application_Configuration |  |  |  | Voltage_protection_u002D__gt_PHPTUV_u003A__1_u003A_Operating_curve_type | EW | Time (27) |  |  |  |  | Under-Overvoltage\PHPTUV1 PhPh | ResetT | Real | 1 | 0 |  | Under-Overvoltage\PHPTUV1 PhPh | pcharac |  | EW | Time (27) |  | Under-Overvoltage\PHPTUV1 PhPh | ResetT | Real |  |  | 1 | 0
Voltage_protection_u002D__gt_PHPTUV_u003A__1_u003A_Minimum_operate_time | Voltage protection->PHPTUV: 1 | Minimum operate time | 0.04-60:0.001 | s | Minimum operate time delay for IDMT curves | Real | Application_Configuration |  |  |  | Voltage_protection_u002D__gt_PHPTUV_u003A__1_u003A_Operating_curve_type | NEW | Time (27) |  |  |  |  | Under-Overvoltage\PHPTUV1 PhPh | udeftmin | Real | 1 | 0 |  | Under-Overvoltage\PHPTUV1 PhPh | pcharac |  | NEW | Time (27) |  | Under-Overvoltage\PHPTUV1 PhPh | udeftmin | Real |  |  | 1 | 0
Current_protection_u002D__gt_EFHPTOC_u003A__1_u003A_Start_value | Current protection->EFHPTOC: 1 | Start value | 0.1-40:0.01 | pu | Start value | Real | Setting_Group | [10 empty] | Earth-fault\EFHPTOC1 | Ipset | Real | 1 | 0 | [7 empty] | Earth-fault\EFHPTOC1 | Ipset | Real |  |  | 1 | 0
Current_protection_u002D__gt_EFHPTOC_u003A__1_u003A_Time_multiplier | Current protection->EFHPTOC: 1 | Time multiplier | 0.05-15:0.01 |  | Time multiplier in IEC/ANSI IDMT curves | Real | Setting_Group |  |  |  | Current_protection_u002D__gt_EFHPTOC_u003A__1_u003A_Operating_curve_type | NEW | Time |  |  |  |  | Earth-fault\EFHPTOC1 | Tpset | Real | 1 | 0 |  | Earth-fault\EFHPTOC1 | pcharac |  | NEW | Time |  | Earth-fault\EFHPTOC1 | Tpset | Real |  |  | 1 | 0
Current_protection_u002D__gt_EFHPTOC_u003A__1_u003A_Operating_curve_type | Current protection->EFHPTOC: 1 | Operating curve type | ANSI Ext. inv.;ANSI Norm. inv.;ANSI Def. Time;IEC Norm. inv.;IEC Very inv.;IEC Ext. inv.;IEC Def. Time;Programmable |  | Selection of time delay curve type | Enum | Setting_Group | ANSI Ext. inv.;ANSI Norm. inv.;ANSI Def. Time;IEC Norm. inv.;IEC Very inv.;IEC Ext. inv.;IEC Def. Time; | String | [8 empty] | Earth-fault\EFHPTOC1 | pcharac | [10 empty] | Earth-fault\EFHPTOC1 | pcharac
Current_protection_u002D__gt_EFHPTOC_u003A__1_u003A_Operate_delay_time | Current protection->EFHPTOC: 1 | Operate delay time | 0.02-200:0.01 | s | Operate delay time | Real | Setting_Group |  |  |  | Current_protection_u002D__gt_EFHPTOC_u003A__1_u003A_Operating_curve_type | EW | Time |  |  |  |  | Earth-fault\EFHPTOC1 | Tpset | Real | 1 | 0 |  | Earth-fault\EFHPTOC1 | pcharac |  | EW | Time |  | Earth-fault\EFHPTOC1 | Tpset | Real |  |  | 1 | 0
Current_protection_u002D__gt_EFLPTOC_u003A__1_u003A_Start_value | Current protection->EFLPTOC: 1 | Start value | 0.01-5:0.001 | pu | Start value | Real | Setting_Group | [10 empty] | Earth-fault\EFLPTOC1 | Ipset | Real | 1 | 0 | [7 empty] | Earth-fault\EFLPTOC1 | Ipset | Real |  |  | 1 | 0
Current_protection_u002D__gt_EFLPTOC_u003A__1_u003A_Time_multiplier | Current protection->EFLPTOC: 1 | Time multiplier | 0.05-15:0.01 |  | Time multiplier in IEC/ANSI IDMT curves | Real | Setting_Group |  |  |  | Current_protection_u002D__gt_EFLPTOC_u003A__1_u003A_Operating_curve_type | NEW | Time |  |  |  |  | Earth-fault\EFLPTOC1 | Tpset | Real | 1 | 0 |  | Earth-fault\EFLPTOC1 | pcharac |  | NEW | Time |  | Earth-fault\EFLPTOC1 | Tpset | Real |  |  | 1 | 0
Current_protection_u002D__gt_EFLPTOC_u003A__1_u003A_Operating_curve_type | Current protection->EFLPTOC: 1 | Operating curve type | ANSI Ext. inv.;ANSI Very inv.;ANSI Norm. inv.;ANSI Mod. inv.;ANSI Def. Time;L.T.E. inv.;L.T.V. inv.;L.T. inv.;IEC Norm. inv.;IEC Very inv.;IEC inv.;IEC Ext. inv.;IEC S.T. inv.;IEC L.T. inv.;IEC Def. Time;Programmable;RI type;RD type |  | Selection of time delay curve type | Enum | Setting_Group | ANSI Ext. inv.;ANSI Very inv.;ANSI Norm. inv.;ANSI Mod. inv.;ANSI Def. Time;L.T.E. inv.;L.T.V. inv.;L.T. inv.;IEC Norm. inv.;IEC Very inv.;IEC inv.;IEC Ext. inv.;IEC S.T. inv.;IEC L.T. inv.;IEC Def. Time; ;RI type;RD type | String | [8 empty] | Earth-fault\EFLPTOC1 | pcharac | [10 empty] | Earth-fault\EFLPTOC1 | pcharac
Current_protection_u002D__gt_EFLPTOC_u003A__1_u003A_Operate_delay_time | Current protection->EFLPTOC: 1 | Operate delay time | 0.04-200:0.01 | s | Operate delay time | Real | Setting_Group |  |  |  | Current_protection_u002D__gt_EFLPTOC_u003A__1_u003A_Operating_curve_type | EW | Time |  |  |  |  | Earth-fault\EFLPTOC1 | Tpset | Real | 1 | 0 |  | Earth-fault\EFLPTOC1 | pcharac |  | EW | Time |  | Earth-fault\EFLPTOC1 | Tpset | Real |  |  | 1 | 0
Current_protection_u002D__gt_LOFLPTUC_u003A__1_u003A_Start_value_high | Current protection->LOFLPTUC: 1 | Start value high | 0.01-1:0.01 | pu | Current setting/Start value high | Real | Setting_Group | [10 empty] | Loss of load\LOFLPTUC1 lev1 | Ipset | Real | 1 | 0 | [7 empty] | Loss of load\LOFLPTUC1 lev1 | Ipset | Real |  |  | 1 | 0
Current_protection_u002D__gt_LOFLPTUC_u003A__1_u003A_Start_value_low | Current protection->LOFLPTUC: 1 | Start value low | 0.01-0.5:0.01 | pu | Current setting/Start value low | Real | Setting_Group | [10 empty] | Loss of load\LOFLPTUC1 lev2 | Ipset | Real | 1 | 0 | [7 empty] | Loss of load\LOFLPTUC1 lev2 | Ipset | Real |  |  | 1 | 0
Current_protection_u002D__gt_LOFLPTUC_u003A__1_u003A_Operate_delay_time | Current protection->LOFLPTUC: 1 | Operate delay time | 0.4-600:0.01 | s | Operate time delay | Real | Setting_Group | [10 empty] | Loss of load\Timer LOFLPTUC1 | Tdelay | Real | 1 | 0 | [7 empty] | Loss of load\Timer LOFLPTUC1 | Tdelay | Real |  |  | 1 | 0
Current_protection_u002D__gt_PHLPTOC_u003A__1_u003A_Start_value | Current protection->PHLPTOC: 1 | Start value | 0.05-5:0.01 | pu | Start value | Real | Setting_Group | [10 empty] | Overcurrent\PHLPTOC1 | Ipset | Real | 1 | 0 | [7 empty] | Overcurrent\PHLPTOC1 | Ipset | Real |  |  | 1 | 0
Current_protection_u002D__gt_PHLPTOC_u003A__1_u003A_Time_multiplier | Current protection->PHLPTOC: 1 | Time multiplier | 0.05-15:0.01 |  | Time multiplier in IEC/ANSI curves | Real | Setting_Group |  |  |  | Current_protection_u002D__gt_PHLPTOC_u003A__1_u003A_Operating_curve_type | NEW | Time |  |  |  |  | Overcurrent\PHLPTOC1 | Tpset | Real | 1 | 0 |  | Overcurrent\PHLPTOC1 | pcharac |  | NEW | Time |  | Overcurrent\PHLPTOC1 | Tpset | Real |  |  | 1 | 0
Current_protection_u002D__gt_PHLPTOC_u003A__1_u003A_Operating_curve_type | Current protection->PHLPTOC: 1 | Operating curve type | ANSI Ext. inv.;ANSI Very inv.;ANSI Norm. inv.;ANSI Mod. inv.;ANSI Def. Time;L.T.E. inv.;L.T.V. inv.;L.T. inv.;IEC Norm. inv.;IEC Very inv.;IEC inv.;IEC Ext. inv.;IEC S.T. inv.;IEC L.T. inv.;IEC Def. Time;Programmable;RI type;RD type |  | Selection of time delay curve type | Enum | Setting_Group | ANSI Ext. inv.;ANSI Very inv.;ANSI Norm. inv.;ANSI Mod. inv.;ANSI Def. Time;L.T.E. inv.;L.T.V. inv.;L.T. inv.;IEC Norm. inv.;IEC Very inv.;IEC inv.;IEC Ext. inv.;IEC S.T. inv.;IEC L.T. inv.;IEC Def. Time; ;RI type;RD type | String | [8 empty] | Overcurrent\PHLPTOC1 | pcharac | [10 empty] | Overcurrent\PHLPTOC1 | pcharac
Current_protection_u002D__gt_PHLPTOC_u003A__1_u003A_Operate_delay_time | Current protection->PHLPTOC: 1 | Operate delay time | 0.04-200:0.01 | s | Operate delay time | Real | Setting_Group |  |  |  | Current_protection_u002D__gt_PHLPTOC_u003A__1_u003A_Operating_curve_type | EW | Time |  |  |  |  | Overcurrent\PHLPTOC1 | Tpset | Real | 1 | 0 |  | Overcurrent\PHLPTOC1 | pcharac |  | EW | Time |  | Overcurrent\PHLPTOC1 | Tpset | Real |  |  | 1 | 0
Current_protection_u002D__gt_MNSPTOC_u003A__1_u003A_Start_value | Current protection->MNSPTOC: 1 | Start value | 0.01-0.5:0.01 | pu | Start value of negative-sequence current | Real | Setting_Group | [7 empty] | 2 |  |  | Unbalance\MNSPTOC1 | Ipset | Real | 1 | 0 | [7 empty] | Unbalance\MNSPTOC1 | Ipset | Real |  |  | 1 | 0
[18 empty] | Unbalance\Start MNSPTOC1 | Ipset | Real | 1 | 0
Current_protection_u002D__gt_MNSPTOC_u003A__1_u003A_Operating_curve_type | Current protection->MNSPTOC: 1 | Operating curve type | ANSI Def. Time;IEC Def. Time;Inv. Curve A;Inv. Curve B |  | Selection of time delay curve type | Enum | Setting_Group | ANSI Def. Time (46);IEC Def. Time (46);Inverse curve A (46);Inverse curve B (46) | String | [8 empty] | Unbalance\MNSPTOC1 | pcharac | [10 empty] | Unbalance\MNSPTOC1 | pcharac
Current_protection_u002D__gt_MNSPTOC_u003A__1_u003A_Machine_time_Mult | Current protection->MNSPTOC: 1 | Machine time Mult | 5-100:0.1 |  | Machine time multiplier | Real | Setting_Group |  |  |  | Current_protection_u002D__gt_MNSPTOC_u003A__1_u003A_Operating_curve_type | NEW | Time (46) |  |  |  |  | Unbalance\MNSPTOC1 | Tpset | Real | 1 | 0 |  | Unbalance\MNSPTOC1 | pcharac |  | NEW | Time (46) |  | Unbalance\MNSPTOC1 | Tpset | Real |  |  | 1 | 0
Current_protection_u002D__gt_MNSPTOC_u003A__1_u003A_Operate_delay_time | Current protection->MNSPTOC: 1 | Operate delay time | 0.1-120:0.01 | s | Operate time in definite-time mode | Real | Setting_Group |  |  |  | Current_protection_u002D__gt_MNSPTOC_u003A__1_u003A_Operating_curve_type | EW | Time (46) |  |  |  |  | Unbalance\MNSPTOC1 | Tpset | Real | 1 | 0 |  | Unbalance\MNSPTOC1 | pcharac |  | EW | Time (46) |  | Unbalance\MNSPTOC1 | Tpset | Real |  |  | 1 | 0
Current_protection_u002D__gt_MNSPTOC_u003A__1_u003A_Maximum_operate_time | Current protection->MNSPTOC: 1 | Maximum operate time | 500-7200:1 | s | Max operate time regardless of the inverse characteristic | Real | Setting_Group |  |  |  | Current_protection_u002D__gt_MNSPTOC_u003A__1_u003A_Operating_curve_type | NEW | Time (46) |  |  |  |  | Unbalance\MNSPTOC1 | udeftmax | Real | 1 | 0 |  | Unbalance\MNSPTOC1 | pcharac |  | NEW | Time (46) |  | Unbalance\MNSPTOC1 | udeftmax | Real |  |  | 1 | 0
Current_protection_u002D__gt_MNSPTOC_u003A__1_u003A_Minimum_operate_time | Current protection->MNSPTOC: 1 | Minimum operate time | 0.1-120:0.01 | s | Definite minimum operate time | Real | Setting_Group |  |  |  | Current_protection_u002D__gt_MNSPTOC_u003A__1_u003A_Operating_curve_type | NEW | Time (46) |  |  |  |  | Unbalance\MNSPTOC1 | udeftmin | Real | 1 | 0 |  | Unbalance\MNSPTOC1 | pcharac |  | NEW | Time (46) |  | Unbalance\MNSPTOC1 | udeftmin | Real |  |  | 1 | 0
Current_protection_u002D__gt_MNSPTOC_u003A__1_u003A_Cooling_time | Current protection->MNSPTOC: 1 | Cooling time | 5-7200:1 | s | Time required to cool the machine | Real | Setting_Group |  |  |  | Current_protection_u002D__gt_MNSPTOC_u003A__1_u003A_Operating_curve_type | NEW | Time (46) |  |  |  |  | Unbalance\MNSPTOC1 | ResetT | Real | 1 | 0 |  | Unbalance\MNSPTOC1 | pcharac |  | NEW | Time (46) |  | Unbalance\MNSPTOC1 | ResetT | Real |  |  | 1 | 0
Current_protection_u002D__gt_MNSPTOC_u003A__2_u003A_Start_value | Current protection->MNSPTOC: 2 | Start value | 0.01-0.5:0.01 | pu | Start value of negative-sequence current | Real | Setting_Group | [7 empty] | 2 |  |  | Unbalance\MNSPTOC2 | Ipset | Real | 1 | 0 | [7 empty] | Unbalance\MNSPTOC2 | Ipset | Real |  |  | 1 | 0
[18 empty] | Unbalance\Start MNSPTOC2 | Ipset | Real | 1 | 0
Current_protection_u002D__gt_MNSPTOC_u003A__2_u003A_Operating_curve_type | Current protection->MNSPTOC: 2 | Operating curve type | ANSI Def. Time;IEC Def. Time;Inv. Curve A;Inv. Curve B |  | Selection of time delay curve type | Enum | Setting_Group | ANSI Def. Time (46);IEC Def. Time (46);Inverse curve A (46);Inverse curve B (46) | String | [8 empty] | Unbalance\MNSPTOC2 | pcharac | [10 empty] | Unbalance\MNSPTOC2 | pcharac
Current_protection_u002D__gt_MNSPTOC_u003A__2_u003A_Machine_time_Mult | Current protection->MNSPTOC: 2 | Machine time Mult | 5-100:0.1 |  | Machine time multiplier | Real | Setting_Group |  |  |  | Current_protection_u002D__gt_MNSPTOC_u003A__2_u003A_Operating_curve_type | NEW | Time (46) |  |  |  |  | Unbalance\MNSPTOC2 | Tpset | Real | 1 | 0 |  | Unbalance\MNSPTOC2 | pcharac |  | NEW | Time (46) |  | Unbalance\MNSPTOC2 | Tpset | Real |  |  | 1 | 0
Current_protection_u002D__gt_MNSPTOC_u003A__2_u003A_Operate_delay_time | Current protection->MNSPTOC: 2 | Operate delay time | 0.1-120:0.01 | s | Operate time in definite-time mode | Real | Setting_Group |  |  |  | Current_protection_u002D__gt_MNSPTOC_u003A__2_u003A_Operating_curve_type | EW | Time (46) |  |  |  |  | Unbalance\MNSPTOC2 | Tpset | Real | 1 | 0 |  | Unbalance\MNSPTOC2 | pcharac |  | EW | Time (46) |  | Unbalance\MNSPTOC2 | Tpset | Real |  |  | 1 | 0
Current_protection_u002D__gt_MNSPTOC_u003A__2_u003A_Maximum_operate_time | Current protection->MNSPTOC: 2 | Maximum operate time | 500-7200:1 | s | Max operate time regardless of the inverse characteristic | Real | Setting_Group |  |  |  | Current_protection_u002D__gt_MNSPTOC_u003A__2_u003A_Operating_curve_type | NEW | Time (46) |  |  |  |  | Unbalance\MNSPTOC2 | udeftmax | Real | 1 | 0 |  | Unbalance\MNSPTOC2 | pcharac |  | NEW | Time (46) |  | Unbalance\MNSPTOC2 | udeftmax | Real |  |  | 1 | 0
Current_protection_u002D__gt_MNSPTOC_u003A__2_u003A_Minimum_operate_time | Current protection->MNSPTOC: 2 | Minimum operate time | 0.1-120:0.01 | s | Definite minimum operate time | Real | Setting_Group |  |  |  | Current_protection_u002D__gt_MNSPTOC_u003A__2_u003A_Operating_curve_type | NEW | Time (46) |  |  |  |  | Unbalance\MNSPTOC2 | udeftmin | Real | 1 | 0 |  | Unbalance\MNSPTOC2 | pcharac |  | NEW | Time (46) |  | Unbalance\MNSPTOC2 | udeftmin | Real |  |  | 1 | 0
Current_protection_u002D__gt_MNSPTOC_u003A__2_u003A_Cooling_time | Current protection->MNSPTOC: 2 | Cooling time | 5-7200:1 | s | Time required to cool the machine | Real | Setting_Group |  |  |  | Current_protection_u002D__gt_MNSPTOC_u003A__2_u003A_Operating_curve_type | NEW | Time (46) |  |  |  |  | Unbalance\MNSPTOC2 | ResetT | Real | 1 | 0 |  | Unbalance\MNSPTOC2 | pcharac |  | NEW | Time (46) |  | Unbalance\MNSPTOC2 | ResetT | Real |  |  | 1 | 0
Voltage_protection_u002D__gt_NSPTOV_u003A__1_u003A_Start_value | Voltage protection->NSPTOV: 1 | Start value | 0.01-1:0.001 | pu | Negative sequence overvoltage start value | Real | Setting_Group | [10 empty] | Under-Overvoltage\NSPTOV1 | Ipset | Real | 1 | 0 | [7 empty] | Under-Overvoltage\NSPTOV1 | Ipset | Real |  |  | 1 | 0
Voltage_protection_u002D__gt_NSPTOV_u003A__1_u003A_Operate_delay_time | Voltage protection->NSPTOV: 1 | Operate delay time | 0.04-120:0.001 | s | Operate delay time | Real | Setting_Group | [10 empty] | Under-Overvoltage\NSPTOV1 | Tpset | Real | 1 | 0 | [7 empty] | Under-Overvoltage\NSPTOV1 | Tpset | Real |  |  | 1 | 0
Voltage_protection_u002D__gt_PHPTOV_u003A__1_u003A_Start_value | Voltage protection->PHPTOV: 1 | Start value | 0.05-1.6:0.01 | pu | Preset value to check for the voltage violation | Real | Setting_Group | [10 empty] | Under-Overvoltage\PHPTOV1 PhPh | Ipset | Real | 1 | 0 | [7 empty] | Under-Overvoltage\PHPTOV1 PhPh | Ipset | Real |  |  | 1 | 0
Voltage_protection_u002D__gt_PHPTOV_u003A__1_u003A_Time_multiplier | Voltage protection->PHPTOV: 1 | Time multiplier | 0.05-15:0.01 |  | Time multiplier in IEC curves | Real | Setting_Group |  |  |  | Voltage_protection_u002D__gt_PHPTOV_u003A__1_u003A_Operating_curve_type | NEW | Time (59) |  |  |  |  | Under-Overvoltage\PHPTOV1 PhPh | Tpset | Real | 1 | 0 |  | Under-Overvoltage\PHPTOV1 PhPh | pcharac |  | NEW | Time (59) |  | Under-Overvoltage\PHPTOV1 PhPh | Tpset | Real |  |  | 1 | 0
Voltage_protection_u002D__gt_PHPTOV_u003A__1_u003A_Operating_curve_type | Voltage protection->PHPTOV: 1 | Operating curve type | ANSI Def. Time;IEC Def. Time;Inv. Curve A;Inv. Curve B;Inv. Curve C;Programmable |  | Selection of the type of time delay curve | Enum | Setting_Group | ANSI Def. Time (59);IEC Def. Time (59);Inverse curve A (59);Inverse curve B (59);Inverse curve C (59); | String | [8 empty] | Under-Overvoltage\PHPTOV1 PhPh | pcharac | [10 empty] | Under-Overvoltage\PHPTOV1 PhPh | pcharac
Voltage_protection_u002D__gt_PHPTOV_u003A__1_u003A_Operate_delay_time | Voltage protection->PHPTOV: 1 | Operate delay time | 0.04-300:0.001 | s | Operating time delay for definite time curve | Real | Setting_Group |  |  |  | Voltage_protection_u002D__gt_PHPTOV_u003A__1_u003A_Operating_curve_type | EW | Time (59) |  |  |  |  | Under-Overvoltage\PHPTOV1 PhPh | Tpset | Real | 1 | 0 |  | Under-Overvoltage\PHPTOV1 PhPh | pcharac |  | EW | Time (59) |  | Under-Overvoltage\PHPTOV1 PhPh | Tpset | Real |  |  | 1 | 0
Voltage_protection_u002D__gt_PHPTUV_u003A__1_u003A_Start_value | Voltage protection->PHPTUV: 1 | Start value | 0.05-1.2:0.01 | pu | Preset value to check for the voltage violation | Real | Setting_Group | [10 empty] | Under-Overvoltage\PHPTUV1 PhPh | Ipset | Real | 1 | 0 | [7 empty] | Under-Overvoltage\PHPTUV1 PhPh | Ipset | Real |  |  | 1 | 0
Voltage_protection_u002D__gt_PHPTUV_u003A__1_u003A_Time_multiplier | Voltage protection->PHPTUV: 1 | Time multiplier | 0.05-15:0.01 |  | Time multiplier in IEC curves | Real | Setting_Group |  |  |  | Voltage_protection_u002D__gt_PHPTUV_u003A__1_u003A_Operating_curve_type | NEW | Time (27) |  |  |  |  | Under-Overvoltage\PHPTUV1 PhPh | Tpset | Real | 1 | 0 |  | Under-Overvoltage\PHPTUV1 PhPh | pcharac |  | NEW | Time (27) |  | Under-Overvoltage\PHPTUV1 PhPh | Tpset | Real |  |  | 1 | 0
Voltage_protection_u002D__gt_PHPTUV_u003A__1_u003A_Operating_curve_type | Voltage protection->PHPTUV: 1 | Operating curve type | ANSI Def. Time;IEC Def. Time;Inv. Curve A;Inv. Curve B;Programmable |  | Selection of the type of time delay curve | Enum | Setting_Group | ANSI Def. Time (27);IEC Def. Time (27);Inverse curve A (27);Inverse curve B (27); | String | [8 empty] | Under-Overvoltage\PHPTUV1 PhPh | pcharac | [10 empty] | Under-Overvoltage\PHPTUV1 PhPh | pcharac
Voltage_protection_u002D__gt_PHPTUV_u003A__1_u003A_Operate_delay_time | Voltage protection->PHPTUV: 1 | Operate delay time | 0.04-300:0.001 | s | Operating time delay for definite time curve | Real | Setting_Group |  |  |  | Voltage_protection_u002D__gt_PHPTUV_u003A__1_u003A_Operating_curve_type | EW | Time (27) |  |  |  |  | Under-Overvoltage\PHPTUV1 PhPh | Tpset | Real | 1 | 0 |  | Under-Overvoltage\PHPTUV1 PhPh | pcharac |  | EW | Time (27) |  | Under-Overvoltage\PHPTUV1 PhPh | Tpset | Real |  |  | 1 | 0
_END_