## Mapping
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37
StationWare | [6 empty] | Common |  |  | Import | [12 empty] | Export
[8 empty] | Enumeration |  | Pre-Condition |  |  |  |  | Instruction | [7 empty] | Pre-Condition | [5 empty] | Instruction
Key | Chapter | Display name | Range | Unit | Description | Type | Group | Mapping | Type |  | Setting | Operator | Value | Default |  | Operator | Value | Target | Parameter | Type | Scale | Offset |  | Source | Parameter | Type | Operator | Value |  | Source | Parameter | Type | Operator | Value | Scale | Offset
HW_Configuration_u002D__gt_AIM__2_u003A_CTsec1 | HW Configuration->AIM_2 | CTsec1 | 0.1-10:0.1 | A | Rated CT secondary current | Real | IED_Configuration | [7 empty] | 3 |  |  | Measurement HV | Inom | Real | 1 | 0
[18 empty] | Measurement HV 2h | Inom | Real | 1 | 0
[18 empty] | Measurement HV 5h | Inom | Real | 1 | 0
HW_Configuration_u002D__gt_AIM__2_u003A_CTsec4 | HW Configuration->AIM_2 | CTsec4 | 0.1-10:0.1 | A | Rated CT secondary current | Real | IED_Configuration | [7 empty] | 2 |  |  | Measurement Zero Seq HV | Inom | Real | 1 | 0
[18 empty] | Measurement Zero Seq HV 2h | Inom | Real | 1 | 0
HW_Configuration_u002D__gt_AIM__2_u003A_CTsec5 | HW Configuration->AIM_2 | CTsec5 | 0.1-10:0.1 | A | Rated CT secondary current | Real | IED_Configuration | [7 empty] | 4 |  |  | Measurement LV | Inom | Real | 1 | 0
[18 empty] | Measurement LV 2h | Inom | Real | 1 | 0
[18 empty] | Measurement LV 5h | Inom | Real | 1 | 0
[18 empty] | Measurement Delta LV | Inom | Real | 1 | 0
HW_Configuration_u002D__gt_AIM__2_u003A_CTsec8 | HW Configuration->AIM_2 | CTsec8 | 0.1-10:0.1 | A | Rated CT secondary current | Real | IED_Configuration | [7 empty] | 2 |  |  | Measurement Zero Seq LV | Inom | Real | 1 | 0
[18 empty] | Measurement Zero Seq LV 2h | Inom | Real | 1 | 0
HW_Configuration_u002D__gt_AIM__2_u003A_VTsec9 | HW Configuration->AIM_2 | VTsec9 | 0.001-999.999:0.001 | V | Rated VT secondary voltage | Real | IED_Configuration | [7 empty] | 2 |  |  | Measurement LV | Unom | Real | 1 | 0
[18 empty] | Measurement Delta LV | Unom | Real | 1 | 0
Current_protection_u002D__gt_EFHPTOC_u003A__1_u003A_Operation | Current protection->EFHPTOC: 1 | Operation | Off;On |  | Operation Off / On | Enum | Application_Configuration | 1;0 | Real | [8 empty] | Earth-fault HV\EFHPTOC | outserv | Real | 1 | 0 | [7 empty] | Earth-fault HV\EFHPTOC | outserv | Real |  |  | 1 | 0
Current_protection_u002D__gt_EFHPTOC_u003A__1_u003A_Reset_delay_time | Current protection->EFHPTOC: 1 | Reset delay time | 0-60:0.001 | s | Reset delay time | Real | Application_Configuration | [10 empty] | Earth-fault HV\EFHPTOC | ResetT | Real | 1 | 0 | [7 empty] | Earth-fault HV\EFHPTOC | ResetT | Real |  |  | 1 | 0
Current_protection_u002D__gt_EFHPTOC_u003A__1_u003A_Minimum_operate_time | Current protection->EFHPTOC: 1 | Minimum operate time | 0.02-60:0.001 | s | Minimum operate time for IDMT curves | Real | Application_Configuration |  |  |  | Current_protection_u002D__gt_EFHPTOC_u003A__1_u003A_Operating_curve_type | NEW | Time |  |  |  |  | Earth-fault HV\EFHPTOC | udeftmin | Real | 1 | 0 |  | Earth-fault HV\EFHPTOC | pcharac |  | NEW | Time |  | Earth-fault HV\EFHPTOC | udeftmin | Real |  |  | 1 | 0
Current_protection_u002D__gt_EFLPTOC_u003A__1_u003A_Operation | Current protection->EFLPTOC: 1 | Operation | Off;On |  | Operation Off / On | Enum | Application_Configuration | 1;0 | Real | [8 empty] | Earth-fault HV\EFLPTOC | outserv | Real | 1 | 0 | [7 empty] | Earth-fault HV\EFLPTOC | outserv | Real |  |  | 1 | 0
Current_protection_u002D__gt_EFLPTOC_u003A__1_u003A_Reset_delay_time | Current protection->EFLPTOC: 1 | Reset delay time | 0-60:0.001 | s | Reset delay time | Real | Application_Configuration | [10 empty] | Earth-fault HV\EFLPTOC | ResetT | Real | 1 | 0 | [7 empty] | Earth-fault HV\EFLPTOC | ResetT | Real |  |  | 1 | 0
Current_protection_u002D__gt_EFLPTOC_u003A__1_u003A_Minimum_operate_time | Current protection->EFLPTOC: 1 | Minimum operate time | 0.04-60:0.001 | s | Minimum operate time for IDMT curves | Real | Application_Configuration |  |  |  | Current_protection_u002D__gt_EFLPTOC_u003A__1_u003A_Operating_curve_type | NEW | Time |  |  |  |  | Earth-fault HV\EFLPTOC | udeftmin | Real | 1 | 0 |  | Earth-fault HV\EFLPTOC | pcharac |  | NEW | Time | 2 | Earth-fault HV\EFLPTOC | udeftmin | Real | GE | 0.04 | 1 | 0
0.04
Current_protection_u002D__gt_NSPTOC_u003A__1_u003A_Operation | Current protection->NSPTOC: 1 | Operation | Off;On |  | Operation Off / On | Enum | Application_Configuration | 1;0 | Real | [8 empty] | Unbalance HV\NSPTOC | outserv | Real | 1 | 0 | [7 empty] | Unbalance HV\NSPTOC | outserv | Real |  |  | 1 | 0
Current_protection_u002D__gt_NSPTOC_u003A__1_u003A_Reset_delay_time | Current protection->NSPTOC: 1 | Reset delay time | 0-60:0.001 | s | Reset delay time | Real | Application_Configuration | [10 empty] | Unbalance HV\NSPTOC | ResetT | Real | 1 | 0 | [7 empty] | Unbalance HV\NSPTOC | ResetT | Real |  |  | 1 | 0
Current_protection_u002D__gt_NSPTOC_u003A__2_u003A_Operation | Current protection->NSPTOC: 2 | Operation | Off;On |  | Operation Off / On | Enum | Application_Configuration | 1;0 | Real | [8 empty] | Unbalance LV\NSPTOC | outserv | Real | 1 | 0 | [7 empty] | Unbalance LV\NSPTOC | outserv | Real |  |  | 1 | 0
Current_protection_u002D__gt_NSPTOC_u003A__2_u003A_Reset_delay_time | Current protection->NSPTOC: 2 | Reset delay time | 0-60:0.001 | s | Reset delay time | Real | Application_Configuration | [10 empty] | Unbalance LV\NSPTOC | ResetT | Real | 1 | 0 | [7 empty] | Unbalance LV\NSPTOC | ResetT | Real |  |  | 1 | 0
Current_protection_u002D__gt_PHHPTOC_u003A__1_u003A_Operation | Current protection->PHHPTOC: 1 | Operation | Off;On |  | Operation Off / On | Enum | Application_Configuration | 1;0 | Real | [8 empty] | Overcurrent HV\PHHPTOC | outserv | Real | 1 | 0 | [7 empty] | Overcurrent HV\PHHPTOC | outserv | Real |  |  | 1 | 0
Current_protection_u002D__gt_PHHPTOC_u003A__1_u003A_Reset_delay_time | Current protection->PHHPTOC: 1 | Reset delay time | 0-60:0.001 | s | Reset delay time | Real | Application_Configuration | [10 empty] | Overcurrent HV\PHHPTOC | ResetT | Real | 1 | 0 | [7 empty] | Overcurrent HV\PHHPTOC | ResetT | Real |  |  | 1 | 0
Current_protection_u002D__gt_PHHPTOC_u003A__1_u003A_Minimum_operate_time | Current protection->PHHPTOC: 1 | Minimum operate time | 0.02-60:0.001 | s | Minimum operate time for IDMT curves | Real | Application_Configuration |  |  |  | Current_protection_u002D__gt_PHHPTOC_u003A__1_u003A_Operating_curve_type | NEW | Time |  |  |  |  | Overcurrent HV\PHHPTOC | udeftmin | Real | 1 | 0 |  | Overcurrent HV\PHHPTOC | pcharac |  | NEW | Time |  | Overcurrent HV\PHHPTOC | udeftmin | Real |  |  | 1 | 0
Current_protection_u002D__gt_PHHPTOC_u003A__2_u003A_Operation | Current protection->PHHPTOC: 2 | Operation | Off;On |  | Operation Off / On | Enum | Application_Configuration | 1;0 | Real | [8 empty] | Overcurrent LV\PHHPTOC | outserv | Real | 1 | 0 | [7 empty] | Overcurrent LV\PHHPTOC | outserv | Real |  |  | 1 | 0
Current_protection_u002D__gt_PHHPTOC_u003A__2_u003A_Reset_delay_time | Current protection->PHHPTOC: 2 | Reset delay time | 0-60:0.001 | s | Reset delay time | Real | Application_Configuration | [10 empty] | Overcurrent LV\PHHPTOC | ResetT | Real | 1 | 0 | [7 empty] | Overcurrent LV\PHHPTOC | ResetT | Real |  |  | 1 | 0
Current_protection_u002D__gt_PHHPTOC_u003A__2_u003A_Minimum_operate_time | Current protection->PHHPTOC: 2 | Minimum operate time | 0.02-60:0.001 | s | Minimum operate time for IDMT curves | Real | Application_Configuration |  |  |  | Current_protection_u002D__gt_PHHPTOC_u003A__2_u003A_Operating_curve_type | NEW | Time |  |  |  |  | Overcurrent LV\PHHPTOC | udeftmin | Real | 1 | 0 |  | Overcurrent LV\PHHPTOC | pcharac |  | NEW | Time |  | Overcurrent LV\PHHPTOC | udeftmin | Real |  |  | 1 | 0
Current_protection_u002D__gt_PHLPTOC_u003A__1_u003A_Operation | Current protection->PHLPTOC: 1 | Operation | Off;On |  | Operation Off / On | Enum | Application_Configuration | 1;0 | Real | [8 empty] | Overcurrent HV\PHLPTOC | outserv | Real | 1 | 0 | [7 empty] | Overcurrent HV\PHLPTOC | outserv | Real |  |  | 1 | 0
Current_protection_u002D__gt_PHLPTOC_u003A__1_u003A_Reset_delay_time | Current protection->PHLPTOC: 1 | Reset delay time | 0-60:0.001 | s | Reset delay time | Real | Application_Configuration | [10 empty] | Overcurrent HV\PHLPTOC | ResetT | Real | 1 | 0 | [7 empty] | Overcurrent HV\PHLPTOC | ResetT | Real |  |  | 1 | 0
Current_protection_u002D__gt_PHLPTOC_u003A__1_u003A_Minimum_operate_time | Current protection->PHLPTOC: 1 | Minimum operate time | 0.04-60:0.001 | s | Minimum operate time for IDMT curves | Real | Application_Configuration |  |  |  | Current_protection_u002D__gt_PHLPTOC_u003A__1_u003A_Operating_curve_type | NEW | Time |  |  |  |  | Overcurrent HV\PHLPTOC | udeftmin | Real | 1 | 0 |  | Overcurrent HV\PHLPTOC | pcharac |  | NEW | Time | 2 | Overcurrent HV\PHLPTOC | udeftmin | Real | GE | 0.04 | 1 | 0
0.04
Current_protection_u002D__gt_PHLPTOC_u003A__2_u003A_Operation | Current protection->PHLPTOC: 2 | Operation | Off;On |  | Operation Off / On | Enum | Application_Configuration | 1;0 | Real | [8 empty] | Overcurrent LV\PHLPTOC | outserv | Real | 1 | 0 | [7 empty] | Overcurrent LV\PHLPTOC | outserv | Real |  |  | 1 | 0
Current_protection_u002D__gt_PHLPTOC_u003A__2_u003A_Reset_delay_time | Current protection->PHLPTOC: 2 | Reset delay time | 0-60:0.001 | s | Reset delay time | Real | Application_Configuration | [10 empty] | Overcurrent LV\PHLPTOC | ResetT | Real | 1 | 0 | [7 empty] | Overcurrent LV\PHLPTOC | ResetT | Real |  |  | 1 | 0
Current_protection_u002D__gt_PHLPTOC_u003A__2_u003A_Minimum_operate_time | Current protection->PHLPTOC: 2 | Minimum operate time | 0.04-60:0.001 | s | Minimum operate time for IDMT curves | Real | Application_Configuration |  |  |  | Current_protection_u002D__gt_PHLPTOC_u003A__2_u003A_Operating_curve_type | NEW | Time |  |  |  |  | Overcurrent LV\PHLPTOC | udeftmin | Real | 1 | 0 |  | Overcurrent LV\PHLPTOC | pcharac |  | NEW | Time | 2 | Overcurrent LV\PHLPTOC | udeftmin | Real | GE | 0.04 | 1 | 0
0.04
Differential_protection_u002D__gt_LREFPNDF_u003A__1_u003A_Operation | Differential protection->LREFPNDF: 1 | Operation | Off;On |  | Operation Off / On | Enum | Application_Configuration | 1;0 | Real | [8 empty] | REF-Differential HV\REFPDIF | outserv | Real | 1 | 0 | [7 empty] | REF-Differential HV\REFPDIF | outserv | Real |  |  | 1 | 0
Differential_protection_u002D__gt_LREFPNDF_u003A__2_u003A_Operation | Differential protection->LREFPNDF: 2 | Operation | Off;On |  | Operation Off / On | Enum | Application_Configuration | 1;0 | Real | [8 empty] | REF-Differential LV\REFPDIF | outserv | Real | 1 | 0 | [7 empty] | REF-Differential LV\REFPDIF | outserv | Real |  |  | 1 | 0
Differential_protection_u002D__gt_TR2PTDF_u003A__1_u003A_Operation | Differential protection->TR2PTDF: 1 | Operation | Off;On |  | Operation Off / On | Enum | Application_Configuration | 1;0 | Real | [8 empty] | Differential\T2WPDIF | outserv | Real | 1 | 0 | [7 empty] | Differential\T2WPDIF | outserv | Real |  |  | 1 | 0
Differential_protection_u002D__gt_TR2PTDF_u003A__1_u003A_Winding_1_type | Differential protection->TR2PTDF: 1 | Winding 1 type | Y;YN;D;Z;ZN |  | Connection of the winding 1 | Enum | Application_Configuration | 2;2;1;0;0 | Real | [5 empty] | 9 | E | 2 | Differential\T2WPDIF Ct1 Adapter | icontype | Real | 1 | 0 | [6 empty] | 3 | Differential\T2WPDIF Ct1 Adapter | icontype | Real | E | 2 | 1 | 0
[16 empty] | E | 2 | Differential\T2WPDIF Ct1 Adapter 2h | icontype | Real | 1 | 0 | [7 empty] | Differential\T2WPDIF Ct1 Adapter | icontype | Real | E | 1 | 1 | 0
[16 empty] | E | 2 | Differential\T2WPDIF Ct1 Adapter 5h | icontype | Real | 1 | 0 | [7 empty] | Differential\T2WPDIF Ct1 Adapter | icontype | Real | E | 0 | 1 | 0
[16 empty] | E | 1 | Differential\T2WPDIF Ct1 Adapter | icontype | Real | 1 | 0
[16 empty] | E | 1 | Differential\T2WPDIF Ct1 Adapter 2h | icontype | Real | 1 | 0
[16 empty] | E | 1 | Differential\T2WPDIF Ct1 Adapter 5h | icontype | Real | 1 | 0
[16 empty] | E | 0 | Differential\T2WPDIF Ct1 Adapter | icontype | Real | 1 | 0
[16 empty] | E | 0 | Differential\T2WPDIF Ct1 Adapter 2h | icontype | Real | 1 | 0
[16 empty] | E | 0 | Differential\T2WPDIF Ct1 Adapter 5h | icontype | Real | 1 | 0
Differential_protection_u002D__gt_TR2PTDF_u003A__1_u003A_Winding_2_type | Differential protection->TR2PTDF: 1 | Winding 2 type | Y;YN;D;Z;ZN |  | Connection of the winding 2 | Enum | Application_Configuration | 2;2;1;0;0 | Real | [5 empty] | 9 | E | 2 | Differential\T2WPDIF Ct2 Adapter | icontype | Real | 1 | 0 | [6 empty] | 3 | Differential\T2WPDIF Ct2 Adapter | icontype | Real | E | 2 | 1 | 0
[16 empty] | E | 2 | Differential\T2WPDIF Ct2 Adapter 2h | icontype | Real | 1 | 0 | [7 empty] | Differential\T2WPDIF Ct2 Adapter | icontype | Real | E | 1 | 1 | 0
[16 empty] | E | 2 | Differential\T2WPDIF Ct2 Adapter 5h | icontype | Real | 1 | 0 | [7 empty] | Differential\T2WPDIF Ct2 Adapter | icontype | Real | E | 0 | 1 | 0
[16 empty] | E | 1 | Differential\T2WPDIF Ct2 Adapter | icontype | Real | 1 | 0
[16 empty] | E | 1 | Differential\T2WPDIF Ct2 Adapter 2h | icontype | Real | 1 | 0
[16 empty] | E | 1 | Differential\T2WPDIF Ct2 Adapter 5h | icontype | Real | 1 | 0
[16 empty] | E | 0 | Differential\T2WPDIF Ct2 Adapter | icontype | Real | 1 | 0
[16 empty] | E | 0 | Differential\T2WPDIF Ct2 Adapter 2h | icontype | Real | 1 | 0
[16 empty] | E | 0 | Differential\T2WPDIF Ct2 Adapter 5h | icontype | Real | 1 | 0
Voltage_protection_u002D__gt_PHPTOV_u003A__1_u003A_Operation | Voltage protection->PHPTOV: 1 | Operation | Off;On |  | Operation Off / On | Enum | Application_Configuration | 1;0 | Real | [8 empty] | Under-Overvoltage LV\PHPTOV1 PhPh | outserv | Real | 1 | 0 | [7 empty] | Under-Overvoltage LV\PHPTOV1 PhPh | outserv | Real |  |  | 1 | 0
Voltage_protection_u002D__gt_PHPTOV_u003A__1_u003A_Reset_delay_time | Voltage protection->PHPTOV: 1 | Reset delay time | 0-60:0.001 | s | Delay time provided to reset the timers | Real | Application_Configuration |  |  |  | Voltage_protection_u002D__gt_PHPTOV_u003A__1_u003A_Operating_curve_type | EW | Time (59) |  |  |  |  | Under-Overvoltage LV\PHPTOV1 PhPh | ResetT | Real | 1 | 0 |  | Under-Overvoltage LV\PHPTOV1 PhPh | pcharac |  | EW | Time (59) |  | Under-Overvoltage LV\PHPTOV1 PhPh | ResetT | Real |  |  | 1 | 0
Voltage_protection_u002D__gt_PHPTOV_u003A__1_u003A_Minimum_operate_time | Voltage protection->PHPTOV: 1 | Minimum operate time | 0.04-60:0.001 | s | Minimum operate time delay for IDMT curves | Real | Application_Configuration |  |  |  | Voltage_protection_u002D__gt_PHPTOV_u003A__1_u003A_Operating_curve_type | NEW | Time (59) |  |  |  |  | Under-Overvoltage LV\PHPTOV1 PhPh | udeftmin | Real | 1 | 0 |  | Under-Overvoltage LV\PHPTOV1 PhPh | pcharac |  | NEW | Time (59) |  | Under-Overvoltage LV\PHPTOV1 PhPh | udeftmin | Real |  |  | 1 | 0
Voltage_protection_u002D__gt_PHPTOV_u003A__2_u003A_Operation | Voltage protection->PHPTOV: 2 | Operation | Off;On |  | Operation Off / On | Enum | Application_Configuration | 1;0 | Real | [8 empty] | Under-Overvoltage LV\PHPTOV2 PhPh | outserv | Real | 1 | 0 | [7 empty] | Under-Overvoltage LV\PHPTOV2 PhPh | outserv | Real |  |  | 1 | 0
Voltage_protection_u002D__gt_PHPTOV_u003A__2_u003A_Reset_delay_time | Voltage protection->PHPTOV: 2 | Reset delay time | 0-60:0.001 | s | Delay time provided to reset the timers | Real | Application_Configuration |  |  |  | Voltage_protection_u002D__gt_PHPTOV_u003A__2_u003A_Operating_curve_type | EW | Time (59) |  |  |  |  | Under-Overvoltage LV\PHPTOV2 PhPh | ResetT | Real | 1 | 0 |  | Under-Overvoltage LV\PHPTOV2 PhPh | pcharac |  | EW | Time (59) |  | Under-Overvoltage LV\PHPTOV2 PhPh | ResetT | Real |  |  | 1 | 0
Voltage_protection_u002D__gt_PHPTOV_u003A__2_u003A_Minimum_operate_time | Voltage protection->PHPTOV: 2 | Minimum operate time | 0.04-60:0.001 | s | Minimum operate time delay for IDMT curves | Real | Application_Configuration |  |  |  | Voltage_protection_u002D__gt_PHPTOV_u003A__2_u003A_Operating_curve_type | NEW | Time (59) |  |  |  |  | Under-Overvoltage LV\PHPTOV2 PhPh | udeftmin | Real | 1 | 0 |  | Under-Overvoltage LV\PHPTOV2 PhPh | pcharac |  | NEW | Time (59) |  | Under-Overvoltage LV\PHPTOV2 PhPh | udeftmin | Real |  |  | 1 | 0
Voltage_protection_u002D__gt_PHPTUV_u003A__1_u003A_Operation | Voltage protection->PHPTUV: 1 | Operation | Off;On |  | Operation Off / On | Enum | Application_Configuration | 1;0 | Real | [8 empty] | Under-Overvoltage LV\PHPTUV1 PhPh | outserv | Real | 1 | 0 | [7 empty] | Under-Overvoltage LV\PHPTUV1 PhPh | outserv | Real |  |  | 1 | 0
Voltage_protection_u002D__gt_PHPTUV_u003A__1_u003A_Reset_delay_time | Voltage protection->PHPTUV: 1 | Reset delay time | 0-60:0.001 | s | Delay time provided to reset the timers | Real | Application_Configuration |  |  |  | Voltage_protection_u002D__gt_PHPTUV_u003A__1_u003A_Operating_curve_type | EW | Time (27) |  |  |  |  | Under-Overvoltage LV\PHPTUV1 PhPh | ResetT | Real | 1 | 0 |  | Under-Overvoltage LV\PHPTUV1 PhPh | pcharac |  | EW | Time (27) |  | Under-Overvoltage LV\PHPTUV1 PhPh | ResetT | Real |  |  | 1 | 0
Voltage_protection_u002D__gt_PHPTUV_u003A__1_u003A_Minimum_operate_time | Voltage protection->PHPTUV: 1 | Minimum operate time | 0.04-60:0.001 | s | Minimum operate time delay for IDMT curves | Real | Application_Configuration |  |  |  | Voltage_protection_u002D__gt_PHPTUV_u003A__1_u003A_Operating_curve_type | NEW | Time (27) |  |  |  |  | Under-Overvoltage LV\PHPTUV1 PhPh | udeftmin | Real | 1 | 0 |  | Under-Overvoltage LV\PHPTUV1 PhPh | pcharac |  | NEW | Time (27) |  | Under-Overvoltage LV\PHPTUV1 PhPh | udeftmin | Real |  |  | 1 | 0
Voltage_protection_u002D__gt_PHPTUV_u003A__2_u003A_Operation | Voltage protection->PHPTUV: 2 | Operation | Off;On |  | Operation Off / On | Enum | Application_Configuration | 1;0 | Real | [8 empty] | Under-Overvoltage LV\PHPTUV2 PhPh | outserv | Real | 1 | 0 | [7 empty] | Under-Overvoltage LV\PHPTUV2 PhPh | outserv | Real |  |  | 1 | 0
Voltage_protection_u002D__gt_PHPTUV_u003A__2_u003A_Reset_delay_time | Voltage protection->PHPTUV: 2 | Reset delay time | 0-60:0.001 | s | Delay time provided to reset the timers | Real | Application_Configuration |  |  |  | Voltage_protection_u002D__gt_PHPTUV_u003A__2_u003A_Operating_curve_type | EW | Time (27) |  |  |  |  | Under-Overvoltage LV\PHPTUV2 PhPh | ResetT | Real | 1 | 0 |  | Under-Overvoltage LV\PHPTUV2 PhPh | pcharac |  | EW | Time (27) |  | Under-Overvoltage LV\PHPTUV2 PhPh | ResetT | Real |  |  | 1 | 0
Voltage_protection_u002D__gt_PHPTUV_u003A__2_u003A_Minimum_operate_time | Voltage protection->PHPTUV: 2 | Minimum operate time | 0.04-60:0.001 | s | Minimum operate time delay for IDMT curves | Real | Application_Configuration |  |  |  | Voltage_protection_u002D__gt_PHPTUV_u003A__2_u003A_Operating_curve_type | NEW | Time (27) |  |  |  |  | Under-Overvoltage LV\PHPTUV2 PhPh | udeftmin | Real | 1 | 0 |  | Under-Overvoltage LV\PHPTUV2 PhPh | pcharac |  | NEW | Time (27) |  | Under-Overvoltage LV\PHPTUV2 PhPh | udeftmin | Real |  |  | 1 | 0
Current_protection_u002D__gt_EFHPTOC_u003A__1_u003A_Start_value | Current protection->EFHPTOC: 1 | Start value | 0.1-40:0.01 | pu | Start value | Real | Setting_Group | [10 empty] | Earth-fault HV\EFHPTOC | Ipset | Real | 1 | 0 | [7 empty] | Earth-fault HV\EFHPTOC | Ipset | Real |  |  | 1 | 0
Current_protection_u002D__gt_EFHPTOC_u003A__1_u003A_Time_multiplier | Current protection->EFHPTOC: 1 | Time multiplier | 0.05-15:0.01 |  | Time multiplier in IEC/ANSI IDMT curves | Real | Setting_Group |  |  |  | Current_protection_u002D__gt_EFHPTOC_u003A__1_u003A_Operating_curve_type | NEW | Time |  |  |  |  | Earth-fault HV\EFHPTOC | Tpset | Real | 1 | 0 |  | Earth-fault HV\EFHPTOC | pcharac |  | NEW | Time |  | Earth-fault HV\EFHPTOC | Tpset | Real |  |  | 1 | 0
Current_protection_u002D__gt_EFHPTOC_u003A__1_u003A_Operating_curve_type | Current protection->EFHPTOC: 1 | Operating curve type | ANSI Ext. inv.;ANSI Norm. inv.;ANSI Def. Time;IEC Norm. inv.;IEC Very inv.;IEC Ext. inv.;IEC Def. Time;Programmable |  | Selection of time delay curve type | Enum | Setting_Group | ANSI Ext. inv.;ANSI Norm. inv.;ANSI Def. Time;IEC Norm. inv.;IEC Very inv.;IEC Ext. inv.;IEC Def. Time; | String | [8 empty] | Earth-fault HV\EFHPTOC | pcharac | [10 empty] | Earth-fault HV\EFHPTOC | pcharac
Current_protection_u002D__gt_EFHPTOC_u003A__1_u003A_Operate_delay_time | Current protection->EFHPTOC: 1 | Operate delay time | 0.02-200:0.01 | s | Operate delay time | Real | Setting_Group |  |  |  | Current_protection_u002D__gt_EFHPTOC_u003A__1_u003A_Operating_curve_type | EW | Time |  |  |  |  | Earth-fault HV\EFHPTOC | Tpset | Real | 1 | 0 |  | Earth-fault HV\EFHPTOC | pcharac |  | EW | Time |  | Earth-fault HV\EFHPTOC | Tpset | Real |  |  | 1 | 0
Current_protection_u002D__gt_EFLPTOC_u003A__1_u003A_Start_value | Current protection->EFLPTOC: 1 | Start value | 0.01-5:0.001 | pu | Start value | Real | Setting_Group | [10 empty] | Earth-fault HV\EFLPTOC | Ipset | Real | 1 | 0 | [7 empty] | Earth-fault HV\EFLPTOC | Ipset | Real |  |  | 1 | 0
Current_protection_u002D__gt_EFLPTOC_u003A__1_u003A_Time_multiplier | Current protection->EFLPTOC: 1 | Time multiplier | 0.05-15:0.01 |  | Time multiplier in IEC/ANSI IDMT curves | Real | Setting_Group |  |  |  | Current_protection_u002D__gt_EFLPTOC_u003A__1_u003A_Operating_curve_type | NEW | Time |  |  |  |  | Earth-fault HV\EFLPTOC | Tpset | Real | 1 | 0 |  | Earth-fault HV\EFLPTOC | pcharac |  | NEW | Time |  | Earth-fault HV\EFLPTOC | Tpset | Real |  |  | 1 | 0
Current_protection_u002D__gt_EFLPTOC_u003A__1_u003A_Operating_curve_type | Current protection->EFLPTOC: 1 | Operating curve type | ANSI Ext. inv.;ANSI Very inv.;ANSI Norm. inv.;ANSI Mod. inv.;ANSI Def. Time;L.T.E. inv.;L.T.V. inv.;L.T. inv.;IEC Norm. inv.;IEC Very inv.;IEC inv.;IEC Ext. inv.;IEC S.T. inv.;IEC L.T. inv.;IEC Def. Time;Programmable;RI type;RD type |  | Selection of time delay curve type | Enum | Setting_Group | ANSI Ext. inv.;ANSI Very inv.;ANSI Norm. inv.;ANSI Mod. inv.;ANSI Def. Time;L.T.E. inv.;L.T.V. inv.;L.T. inv.;IEC Norm. inv.;IEC Very inv.;IEC inv.;IEC Ext. inv.;IEC S.T. inv.;IEC L.T. inv.;IEC Def. Time; ;RI type;RD type | String | [8 empty] | Earth-fault HV\EFLPTOC | pcharac | [10 empty] | Earth-fault HV\EFLPTOC | pcharac
Current_protection_u002D__gt_EFLPTOC_u003A__1_u003A_Operate_delay_time | Current protection->EFLPTOC: 1 | Operate delay time | 0.04-200:0.01 | s | Operate delay time | Real | Setting_Group |  |  |  | Current_protection_u002D__gt_EFLPTOC_u003A__1_u003A_Operating_curve_type | EW | Time |  |  |  |  | Earth-fault HV\EFLPTOC | Tpset | Real | 1 | 0 |  | Earth-fault HV\EFLPTOC | pcharac |  | EW | Time |  | Earth-fault HV\EFLPTOC | Tpset | Real |  |  | 1 | 0
Current_protection_u002D__gt_NSPTOC_u003A__1_u003A_Start_value | Current protection->NSPTOC: 1 | Start value | 0.01-5:0.01 | pu | Start value | Real | Setting_Group | [10 empty] | Unbalance HV\NSPTOC | Ipset | Real | 1 | 0 | [7 empty] | Unbalance HV\NSPTOC | Ipset | Real |  |  | 1 | 0
Current_protection_u002D__gt_NSPTOC_u003A__1_u003A_Time_multiplier | Current protection->NSPTOC: 1 | Time multiplier | 0.05-15:0.01 |  | Time multiplier/ Time Dial in IEC/ANSI curves | Real | Setting_Group |  |  |  | Current_protection_u002D__gt_NSPTOC_u003A__1_u003A_Operating_curve_type | NEW | Time |  |  |  |  | Unbalance HV\NSPTOC | Tpset | Real | 1 | 0 |  | Unbalance HV\NSPTOC | pcharac |  | NEW | Time |  | Unbalance HV\NSPTOC | Tpset | Real |  |  | 1 | 0
Current_protection_u002D__gt_NSPTOC_u003A__1_u003A_Operating_curve_type | Current protection->NSPTOC: 1 | Operating curve type | ANSI Ext. inv.;ANSI Very inv.;ANSI Norm. inv.;ANSI Mod. inv.;ANSI Def. Time;L.T.E. inv.;L.T.V. inv.;L.T. inv.;IEC Norm. inv.;IEC Very inv.;IEC inv.;IEC Ext. inv.;IEC S.T. inv.;IEC L.T. inv.;IEC Def. Time;Programmable;RI type;RD type |  | Selection of time delay curve type | Enum | Setting_Group | ANSI Ext. inv.;ANSI Very inv.;ANSI Norm. inv.;ANSI Mod. inv.;ANSI Def. Time;L.T.E. inv.;L.T.V. inv.;L.T. inv.;IEC Norm. inv.;IEC Very inv.;IEC inv.;IEC Ext. inv.;IEC S.T. inv.;IEC L.T. inv.;IEC Def. Time; ;RI type;RD type | String | [8 empty] | Unbalance HV\NSPTOC | pcharac | [10 empty] | Unbalance HV\NSPTOC | pcharac
Current_protection_u002D__gt_NSPTOC_u003A__1_u003A_Operate_delay_time | Current protection->NSPTOC: 1 | Operate delay time | 0.04-200:0.01 | s | Operate Delay Time | Real | Setting_Group |  |  |  | Current_protection_u002D__gt_NSPTOC_u003A__1_u003A_Operating_curve_type | EW | Time |  |  |  |  | Unbalance HV\NSPTOC | Tpset | Real | 1 | 0 |  | Unbalance HV\NSPTOC | pcharac |  | EW | Time |  | Unbalance HV\NSPTOC | Tpset | Real |  |  | 1 | 0
Current_protection_u002D__gt_NSPTOC_u003A__1_u003A_Minimum_operate_time | Current protection->NSPTOC: 1 | Minimum operate time | 0.04-60:0.001 | s | Minimum operate time for IDMT curves | Real | Setting_Group |  |  |  | Current_protection_u002D__gt_NSPTOC_u003A__1_u003A_Operating_curve_type | NEW | Time |  |  |  |  | Unbalance HV\NSPTOC | udeftmin | Real | 1 | 0 |  | Unbalance HV\NSPTOC | pcharac |  | NEW | Time |  | Unbalance HV\NSPTOC | udeftmin | Real |  |  | 1 | 0
Current_protection_u002D__gt_NSPTOC_u003A__2_u003A_Start_value | Current protection->NSPTOC: 2 | Start value | 0.01-5:0.01 | pu | Start value | Real | Setting_Group | [10 empty] | Unbalance LV\NSPTOC | Ipset | Real | 1 | 0 | [7 empty] | Unbalance LV\NSPTOC | Ipset | Real |  |  | 1 | 0
Current_protection_u002D__gt_NSPTOC_u003A__2_u003A_Time_multiplier | Current protection->NSPTOC: 2 | Time multiplier | 0.05-15:0.01 |  | Time multiplier/ Time Dial in IEC/ANSI curves | Real | Setting_Group |  |  |  | Current_protection_u002D__gt_NSPTOC_u003A__2_u003A_Operating_curve_type | NEW | Time |  |  |  |  | Unbalance LV\NSPTOC | Tpset | Real | 1 | 0 |  | Unbalance LV\NSPTOC | pcharac |  | NEW | Time |  | Unbalance LV\NSPTOC | Tpset | Real |  |  | 1 | 0
Current_protection_u002D__gt_NSPTOC_u003A__2_u003A_Operating_curve_type | Current protection->NSPTOC: 2 | Operating curve type | ANSI Ext. inv.;ANSI Very inv.;ANSI Norm. inv.;ANSI Mod. inv.;ANSI Def. Time;L.T.E. inv.;L.T.V. inv.;L.T. inv.;IEC Norm. inv.;IEC Very inv.;IEC inv.;IEC Ext. inv.;IEC S.T. inv.;IEC L.T. inv.;IEC Def. Time;Programmable;RI type;RD type |  | Selection of time delay curve type | Enum | Setting_Group | ANSI Ext. inv.;ANSI Very inv.;ANSI Norm. inv.;ANSI Mod. inv.;ANSI Def. Time;L.T.E. inv.;L.T.V. inv.;L.T. inv.;IEC Norm. inv.;IEC Very inv.;IEC inv.;IEC Ext. inv.;IEC S.T. inv.;IEC L.T. inv.;IEC Def. Time; ;RI type;RD type | String | [8 empty] | Unbalance LV\NSPTOC | pcharac | [10 empty] | Unbalance LV\NSPTOC | pcharac
Current_protection_u002D__gt_NSPTOC_u003A__2_u003A_Operate_delay_time | Current protection->NSPTOC: 2 | Operate delay time | 0.04-200:0.01 | s | Operate Delay Time | Real | Setting_Group |  |  |  | Current_protection_u002D__gt_NSPTOC_u003A__2_u003A_Operating_curve_type | EW | Time |  |  |  |  | Unbalance LV\NSPTOC | Tpset | Real | 1 | 0 |  | Unbalance LV\NSPTOC | pcharac |  | EW | Time |  | Unbalance LV\NSPTOC | Tpset | Real |  |  | 1 | 0
Current_protection_u002D__gt_NSPTOC_u003A__2_u003A_Minimum_operate_time | Current protection->NSPTOC: 2 | Minimum operate time | 0.04-60:0.001 | s | Minimum operate time for IDMT curves | Real | Setting_Group |  |  |  | Current_protection_u002D__gt_NSPTOC_u003A__2_u003A_Operating_curve_type | NEW | Time |  |  |  |  | Unbalance LV\NSPTOC | udeftmin | Real | 1 | 0 |  | Unbalance LV\NSPTOC | pcharac |  | NEW | Time |  | Unbalance LV\NSPTOC | udeftmin | Real |  |  | 1 | 0
Current_protection_u002D__gt_PHHPTOC_u003A__1_u003A_Start_value | Current protection->PHHPTOC: 1 | Start value | 0.1-40:0.01 | pu | Start value | Real | Setting_Group | [10 empty] | Overcurrent HV\PHHPTOC | Ipset | Real | 1 | 0 | [7 empty] | Overcurrent HV\PHHPTOC | Ipset | Real |  |  | 1 | 0
Current_protection_u002D__gt_PHHPTOC_u003A__1_u003A_Time_multiplier | Current protection->PHHPTOC: 1 | Time multiplier | 0.05-15:0.01 |  | Time multiplier in IEC/ANSI curves | Real | Setting_Group |  |  |  | Current_protection_u002D__gt_PHHPTOC_u003A__1_u003A_Operating_curve_type | NEW | Time |  |  |  |  | Overcurrent HV\PHHPTOC | Tpset | Real | 1 | 0 |  | Overcurrent HV\PHHPTOC | pcharac |  | NEW | Time |  | Overcurrent HV\PHHPTOC | Tpset | Real |  |  | 1 | 0
Current_protection_u002D__gt_PHHPTOC_u003A__1_u003A_Operating_curve_type | Current protection->PHHPTOC: 1 | Operating curve type | ANSI Ext. inv.;ANSI Norm. inv.;ANSI Def. Time;IEC Norm. inv.;IEC Very inv.;IEC Ext. inv.;IEC Def. Time;Programmable |  | Selection of time delay curve type | Enum | Setting_Group | ANSI Ext. inv.;ANSI Norm. inv.;ANSI Def. Time;IEC Norm. inv.;IEC Very inv.;IEC Ext. inv.;IEC Def. Time; | String | [8 empty] | Overcurrent HV\PHHPTOC | pcharac | [10 empty] | Overcurrent HV\PHHPTOC | pcharac
Current_protection_u002D__gt_PHHPTOC_u003A__1_u003A_Operate_delay_time | Current protection->PHHPTOC: 1 | Operate delay time | 0.02-200:0.01 | s | Operate delay time | Real | Setting_Group |  |  |  | Current_protection_u002D__gt_PHHPTOC_u003A__1_u003A_Operating_curve_type | EW | Time |  |  |  |  | Overcurrent HV\PHHPTOC | Tpset | Real | 1 | 0 |  | Overcurrent HV\PHHPTOC | pcharac |  | EW | Time |  | Overcurrent HV\PHHPTOC | Tpset | Real |  |  | 1 | 0
Current_protection_u002D__gt_PHHPTOC_u003A__2_u003A_Start_value | Current protection->PHHPTOC: 2 | Start value | 0.1-40:0.01 | pu | Start value | Real | Setting_Group | [10 empty] | Overcurrent LV\PHHPTOC | Ipset | Real | 1 | 0 | [7 empty] | Overcurrent LV\PHHPTOC | Ipset | Real |  |  | 1 | 0
Current_protection_u002D__gt_PHHPTOC_u003A__2_u003A_Time_multiplier | Current protection->PHHPTOC: 2 | Time multiplier | 0.05-15:0.01 |  | Time multiplier in IEC/ANSI curves | Real | Setting_Group |  |  |  | Current_protection_u002D__gt_PHHPTOC_u003A__2_u003A_Operating_curve_type | NEW | Time |  |  |  |  | Overcurrent LV\PHHPTOC | Tpset | Real | 1 | 0 |  | Overcurrent LV\PHHPTOC | pcharac |  | NEW | Time |  | Overcurrent LV\PHHPTOC | Tpset | Real |  |  | 1 | 0
Current_protection_u002D__gt_PHHPTOC_u003A__2_u003A_Operating_curve_type | Current protection->PHHPTOC: 2 | Operating curve type | ANSI Ext. inv.;ANSI Norm. inv.;ANSI Def. Time;IEC Norm. inv.;IEC Very inv.;IEC Ext. inv.;IEC Def. Time;Programmable |  | Selection of time delay curve type | Enum | Setting_Group | ANSI Ext. inv.;ANSI Norm. inv.;ANSI Def. Time;IEC Norm. inv.;IEC Very inv.;IEC Ext. inv.;IEC Def. Time; | String | [8 empty] | Overcurrent LV\PHHPTOC | pcharac | [10 empty] | Overcurrent LV\PHHPTOC | pcharac
Current_protection_u002D__gt_PHHPTOC_u003A__2_u003A_Operate_delay_time | Current protection->PHHPTOC: 2 | Operate delay time | 0.02-200:0.01 | s | Operate delay time | Real | Setting_Group |  |  |  | Current_protection_u002D__gt_PHHPTOC_u003A__2_u003A_Operating_curve_type | EW | Time |  |  |  |  | Overcurrent LV\PHHPTOC | Tpset | Real | 1 | 0 |  | Overcurrent LV\PHHPTOC | pcharac |  | EW | Time |  | Overcurrent LV\PHHPTOC | Tpset | Real |  |  | 1 | 0
Current_protection_u002D__gt_PHLPTOC_u003A__1_u003A_Start_value | Current protection->PHLPTOC: 1 | Start value | 0.05-5:0.01 | pu | Start value | Real | Setting_Group | [10 empty] | Overcurrent HV\PHLPTOC | Ipset | Real | 1 | 0 | [7 empty] | Overcurrent HV\PHLPTOC | Ipset | Real |  |  | 1 | 0
Current_protection_u002D__gt_PHLPTOC_u003A__1_u003A_Time_multiplier | Current protection->PHLPTOC: 1 | Time multiplier | 0.05-15:0.01 |  | Time multiplier in IEC/ANSI curves | Real | Setting_Group |  |  |  | Current_protection_u002D__gt_PHLPTOC_u003A__1_u003A_Operating_curve_type | NEW | Time |  |  |  |  | Overcurrent HV\PHLPTOC | Tpset | Real | 1 | 0 |  | Overcurrent HV\PHLPTOC | pcharac |  | NEW | Time |  | Overcurrent HV\PHLPTOC | Tpset | Real |  |  | 1 | 0
Current_protection_u002D__gt_PHLPTOC_u003A__1_u003A_Operating_curve_type | Current protection->PHLPTOC: 1 | Operating curve type | ANSI Ext. inv.;ANSI Very inv.;ANSI Norm. inv.;ANSI Mod. inv.;ANSI Def. Time;L.T.E. inv.;L.T.V. inv.;L.T. inv.;IEC Norm. inv.;IEC Very inv.;IEC inv.;IEC Ext. inv.;IEC S.T. inv.;IEC L.T. inv.;IEC Def. Time;Programmable;RI type;RD type |  | Selection of time delay curve type | Enum | Setting_Group | ANSI Ext. inv.;ANSI Very inv.;ANSI Norm. inv.;ANSI Mod. inv.;ANSI Def. Time;L.T.E. inv.;L.T.V. inv.;L.T. inv.;IEC Norm. inv.;IEC Very inv.;IEC inv.;IEC Ext. inv.;IEC S.T. inv.;IEC L.T. inv.;IEC Def. Time; ;RI type;RD type | String | [8 empty] | Overcurrent HV\PHLPTOC | pcharac | [10 empty] | Overcurrent HV\PHLPTOC | pcharac
Current_protection_u002D__gt_PHLPTOC_u003A__1_u003A_Operate_delay_time | Current protection->PHLPTOC: 1 | Operate delay time | 0.04-200:0.01 | s | Operate delay time | Real | Setting_Group |  |  |  | Current_protection_u002D__gt_PHLPTOC_u003A__1_u003A_Operating_curve_type | EW | Time |  |  |  |  | Overcurrent HV\PHLPTOC | Tpset | Real | 1 | 0 |  | Overcurrent HV\PHLPTOC | pcharac |  | EW | Time |  | Overcurrent HV\PHLPTOC | Tpset | Real |  |  | 1 | 0
Current_protection_u002D__gt_PHLPTOC_u003A__2_u003A_Start_value | Current protection->PHLPTOC: 2 | Start value | 0.05-5:0.01 | pu | Start value | Real | Setting_Group | [10 empty] | Overcurrent LV\PHLPTOC | Ipset | Real | 1 | 0 | [7 empty] | Overcurrent LV\PHLPTOC | Ipset | Real |  |  | 1 | 0
Current_protection_u002D__gt_PHLPTOC_u003A__2_u003A_Time_multiplier | Current protection->PHLPTOC: 2 | Time multiplier | 0.05-15:0.01 |  | Time multiplier in IEC/ANSI curves | Real | Setting_Group |  |  |  | Current_protection_u002D__gt_PHLPTOC_u003A__2_u003A_Operating_curve_type | NEW | Time |  |  |  |  | Overcurrent LV\PHLPTOC | Tpset | Real | 1 | 0 |  | Overcurrent LV\PHLPTOC | pcharac |  | NEW | Time |  | Overcurrent LV\PHLPTOC | Tpset | Real |  |  | 1 | 0
Current_protection_u002D__gt_PHLPTOC_u003A__2_u003A_Operating_curve_type | Current protection->PHLPTOC: 2 | Operating curve type | ANSI Ext. inv.;ANSI Very inv.;ANSI Norm. inv.;ANSI Mod. inv.;ANSI Def. Time;L.T.E. inv.;L.T.V. inv.;L.T. inv.;IEC Norm. inv.;IEC Very inv.;IEC inv.;IEC Ext. inv.;IEC S.T. inv.;IEC L.T. inv.;IEC Def. Time;Programmable;RI type;RD type |  | Selection of time delay curve type | Enum | Setting_Group | ANSI Ext. inv.;ANSI Very inv.;ANSI Norm. inv.;ANSI Mod. inv.;ANSI Def. Time;L.T.E. inv.;L.T.V. inv.;L.T. inv.;IEC Norm. inv.;IEC Very inv.;IEC inv.;IEC Ext. inv.;IEC S.T. inv.;IEC L.T. inv.;IEC Def. Time; ;RI type;RD type | String | [8 empty] | Overcurrent LV\PHLPTOC | pcharac | [10 empty] | Overcurrent LV\PHLPTOC | pcharac
Current_protection_u002D__gt_PHLPTOC_u003A__2_u003A_Operate_delay_time | Current protection->PHLPTOC: 2 | Operate delay time | 0.04-200:0.01 | s | Operate delay time | Real | Setting_Group |  |  |  | Current_protection_u002D__gt_PHLPTOC_u003A__2_u003A_Operating_curve_type | EW | Time |  |  |  |  | Overcurrent LV\PHLPTOC | Tpset | Real | 1 | 0 |  | Overcurrent LV\PHLPTOC | pcharac |  | EW | Time |  | Overcurrent LV\PHLPTOC | Tpset | Real |  |  | 1 | 0
Differential_protection_u002D__gt_LREFPNDF_u003A__1_u003A_Restraint_mode | Differential protection->LREFPNDF: 1 | Restraint mode | None;2nd harmonic |  | Setting to allow for second harmonic blocking | Enum | Setting_Group | 0;1 | Real | [5 empty] | 2 | E | 0 | REF-Differential HV\REFPDIF | h2interblock | Real | 0 | 1 | [6 empty] | 2 | REF-Differential HV\REFPDIF | h2interblock | Real | E | 0 | 0 | 1
[16 empty] | E | 1 | REF-Differential HV\REFPDIF | h2interblock | Real | 0 | 0 | [7 empty] | REF-Differential HV\REFPDIF | h2interblock | Real | E | 1 | 0 | 0
Differential_protection_u002D__gt_LREFPNDF_u003A__1_u003A_Operate_value | Differential protection->LREFPNDF: 1 | Operate value | 5-50:1 | % | Min ratio of differential and nominal current for a trip | Real | Setting_Group | [10 empty] | REF-Differential HV\REFPDIF | Idiff | Real | 0.01 | 0 | [7 empty] | REF-Differential HV\REFPDIF | Idiff | Real |  |  | 100 | 0
Differential_protection_u002D__gt_LREFPNDF_u003A__1_u003A_Start_value_2_u002E_H | Differential protection->LREFPNDF: 1 | Start value 2.H | 10-50:1 | % | Ratio to cause the second harmonic blocking | Real | Setting_Group | [10 empty] | REF-Differential HV\REFPDIF | H2threshold | Real | 1 | 0 | [7 empty] | REF-Differential HV\REFPDIF | H2threshold | Real |  |  | 1 | 0
Differential_protection_u002D__gt_LREFPNDF_u003A__2_u003A_Restraint_mode | Differential protection->LREFPNDF: 2 | Restraint mode | None;2nd harmonic |  | Setting to allow for second harmonic blocking | Enum | Setting_Group | 0;1 | Real | [5 empty] | 2 | E | 0 | REF-Differential LV\REFPDIF | h2interblock | Real | 0 | 1 | [6 empty] | 2 | REF-Differential LV\REFPDIF | h2interblock | Real | E | 0 | 0 | 1
[16 empty] | E | 1 | REF-Differential LV\REFPDIF | h2interblock | Real | 0 | 0 | [7 empty] | REF-Differential LV\REFPDIF | h2interblock | Real | E | 1 | 0 | 0
Differential_protection_u002D__gt_LREFPNDF_u003A__2_u003A_Operate_value | Differential protection->LREFPNDF: 2 | Operate value | 5-50:1 | % | Min ratio of differential and nominal current for a trip | Real | Setting_Group | [10 empty] | REF-Differential LV\REFPDIF | Idiff | Real | 0.01 | 0 | [7 empty] | REF-Differential LV\REFPDIF | Idiff | Real |  |  | 100 | 0
Differential_protection_u002D__gt_LREFPNDF_u003A__2_u003A_Start_value_2_u002E_H | Differential protection->LREFPNDF: 2 | Start value 2.H | 10-50:1 | % | Ratio to cause the second harmonic blocking | Real | Setting_Group | [10 empty] | REF-Differential LV\REFPDIF | H2threshold | Real | 1 | 0 | [7 empty] | REF-Differential LV\REFPDIF | H2threshold | Real |  |  | 1 | 0
Differential_protection_u002D__gt_TR2PTDF_u003A__1_u003A_Restraint_mode | Differential protection->TR2PTDF: 1 | Restraint mode | 2.h & 5.h & wav;Waveform;2.h & waveform;5.h & waveform |  | Selects what harmonic blocking methods are in use | Enum | Setting_Group | 0;1;2;3 | Real | [5 empty] | 8 | E | 0 | Differential\T2WPDIF | h2interblock | Real | 0 | 1 | 2 | Differential\T2WPDIF | h2interblock | Real | E | 1 | 2 | Differential\T2WPDIF | h5interblock | Real | E | 1 | 0 | 0
[16 empty] | E | 0 | Differential\T2WPDIF | h5interblock | Real | 0 | 1 | [7 empty] | Differential\T2WPDIF | h5interblock | Real | E | 0 | 0 | 2
[16 empty] | E | 1 | Differential\T2WPDIF | h2interblock | Real | 0 | 0 | [6 empty] | 2 | Differential\T2WPDIF | h5interblock | Real | E | 1 | 0 | 3
[16 empty] | E | 1 | Differential\T2WPDIF | h5interblock | Real | 0 | 0 | [7 empty] | Differential\T2WPDIF | h5interblock | Real | E | 0 | 0 | 1
[16 empty] | E | 3 | Differential\T2WPDIF | h2interblock | Real | 0 | 1
[16 empty] | E | 3 | Differential\T2WPDIF | h5interblock | Real | 0 | 0
[16 empty] | E | 4 | Differential\T2WPDIF | h2interblock | Real | 0 | 0
[16 empty] | E | 4 | Differential\T2WPDIF | h5interblock | Real | 0 | 1
Differential_protection_u002D__gt_TR2PTDF_u003A__1_u003A_High_operate_value | Differential protection->TR2PTDF: 1 | High operate value | 500-3000:1 | % | Instantaneous stage setting | Real | Setting_Group | [10 empty] | Differential\T2WPDIF | Idiffunrest | Real | 0.01 | 0 | [7 empty] | Differential\T2WPDIF | Idiffunrest | Real |  |  | 100 | 0
Differential_protection_u002D__gt_TR2PTDF_u003A__1_u003A_Low_operate_value | Differential protection->TR2PTDF: 1 | Low operate value | 5-50:1 | % | Basic setting for stabilized operation | Real | Setting_Group | [10 empty] | Differential\T2WPDIF | Idiff | Real | 0.01 | 0 | [7 empty] | Differential\T2WPDIF | Idiff | Real |  |  | 100 | 0
Differential_protection_u002D__gt_TR2PTDF_u003A__1_u003A_Slope_section_2 | Differential protection->TR2PTDF: 1 | Slope section 2 | 10-50:1 | % | Slope of the second line of the operating characteristics | Real | Setting_Group | [10 empty] | Differential\T2WPDIF | Irestrpercent1 | Real | 1 | 0 | [7 empty] | Differential\T2WPDIF | Irestrpercent1 | Real |  |  | 1 | 0
Differential_protection_u002D__gt_TR2PTDF_u003A__1_u003A_End_section_2 | Differential protection->TR2PTDF: 1 | End section 2 | 100-500:1 | % | Turn-point between sections 2 and 3 of the characteristics | Real | Setting_Group | [10 empty] | Differential\T2WPDIF | Ipset2 | Real | 0.01 | 0 | [7 empty] | Differential\T2WPDIF | Ipset2 | Real |  |  | 100 | 0
Differential_protection_u002D__gt_TR2PTDF_u003A__1_u003A_Start_value_2_u002E_H | Differential protection->TR2PTDF: 1 | Start value 2.H | 7-20:1 | % | 2. harmonic blocking ratio | Real | Setting_Group | [10 empty] | Differential\T2WPDIF | H2threshold | Real | 1 | 0 | [7 empty] | Differential\T2WPDIF | H2threshold | Real |  |  | 1 | 0
Differential_protection_u002D__gt_TR2PTDF_u003A__1_u003A_Start_value_5_u002E_H | Differential protection->TR2PTDF: 1 | Start value 5.H | 10-50:1 | % | 5. harmonic blocking ratio | Real | Setting_Group | [10 empty] | Differential\T2WPDIF | H5threshold | Real | 1 | 0 | [7 empty] | Differential\T2WPDIF | H5threshold | Real |  |  | 1 | 0
Voltage_protection_u002D__gt_PHPTOV_u003A__1_u003A_Start_value | Voltage protection->PHPTOV: 1 | Start value | 0.05-1.6:0.01 | pu | Preset value to check for the voltage violation | Real | Setting_Group | [10 empty] | Under-Overvoltage LV\PHPTOV1 PhPh | Ipset | Real | 1 | 0 | [7 empty] | Under-Overvoltage LV\PHPTOV1 PhPh | Ipset | Real |  |  | 1 | 0
Voltage_protection_u002D__gt_PHPTOV_u003A__1_u003A_Time_multiplier | Voltage protection->PHPTOV: 1 | Time multiplier | 0.05-15:0.01 |  | Time multiplier in IEC curves | Real | Setting_Group |  |  |  | Voltage_protection_u002D__gt_PHPTOV_u003A__1_u003A_Operating_curve_type | NEW | Time (59) |  |  |  |  | Under-Overvoltage LV\PHPTOV1 PhPh | Tpset | Real | 1 | 0 |  | Under-Overvoltage LV\PHPTOV1 PhPh | pcharac |  | NEW | Time (59) |  | Under-Overvoltage LV\PHPTOV1 PhPh | Tpset | Real |  |  | 1 | 0
Voltage_protection_u002D__gt_PHPTOV_u003A__1_u003A_Operating_curve_type | Voltage protection->PHPTOV: 1 | Operating curve type | ANSI Def. Time;IEC Def. Time;Inv. Curve A;Inv. Curve B;Inv. Curve C;Programmable |  | Selection of the type of time delay curve | Enum | Setting_Group | ANSI Def. Time (59);IEC Def. Time (59);Inverse curve A (59);Inverse curve B (59);Inverse curve C (59); | String | [8 empty] | Under-Overvoltage LV\PHPTOV1 PhPh | pcharac | [10 empty] | Under-Overvoltage LV\PHPTOV1 PhPh | pcharac
Voltage_protection_u002D__gt_PHPTOV_u003A__1_u003A_Operate_delay_time | Voltage protection->PHPTOV: 1 | Operate delay time | 0.04-300:0.001 | s | Operating time delay for definite time curve | Real | Setting_Group |  |  |  | Voltage_protection_u002D__gt_PHPTOV_u003A__1_u003A_Operating_curve_type | EW | Time (59) |  |  |  |  | Under-Overvoltage LV\PHPTOV1 PhPh | Tpset | Real | 1 | 0 |  | Under-Overvoltage LV\PHPTOV1 PhPh | pcharac |  | EW | Time (59) |  | Under-Overvoltage LV\PHPTOV1 PhPh | Tpset | Real |  |  | 1 | 0
Voltage_protection_u002D__gt_PHPTOV_u003A__2_u003A_Start_value | Voltage protection->PHPTOV: 2 | Start value | 0.05-1.6:0.01 | pu | Preset value to check for the voltage violation | Real | Setting_Group | [10 empty] | Under-Overvoltage LV\PHPTOV2 PhPh | Ipset | Real | 1 | 0 | [7 empty] | Under-Overvoltage LV\PHPTOV2 PhPh | Ipset | Real |  |  | 1 | 0
Voltage_protection_u002D__gt_PHPTOV_u003A__2_u003A_Time_multiplier | Voltage protection->PHPTOV: 2 | Time multiplier | 0.05-15:0.01 |  | Time multiplier in IEC curves | Real | Setting_Group |  |  |  | Voltage_protection_u002D__gt_PHPTOV_u003A__2_u003A_Operating_curve_type | NEW | Time (59) |  |  |  |  | Under-Overvoltage LV\PHPTOV2 PhPh | Tpset | Real | 1 | 0 |  | Under-Overvoltage LV\PHPTOV2 PhPh | pcharac |  | NEW | Time (59) |  | Under-Overvoltage LV\PHPTOV2 PhPh | Tpset | Real |  |  | 1 | 0
Voltage_protection_u002D__gt_PHPTOV_u003A__2_u003A_Operating_curve_type | Voltage protection->PHPTOV: 2 | Operating curve type | ANSI Def. Time;IEC Def. Time;Inv. Curve A;Inv. Curve B;Inv. Curve C;Programmable |  | Selection of the type of time delay curve | Enum | Setting_Group | ANSI Def. Time (59);IEC Def. Time (59);Inverse curve A (59);Inverse curve B (59);Inverse curve C (59); | String | [8 empty] | Under-Overvoltage LV\PHPTOV2 PhPh | pcharac | [10 empty] | Under-Overvoltage LV\PHPTOV2 PhPh | pcharac
Voltage_protection_u002D__gt_PHPTOV_u003A__2_u003A_Operate_delay_time | Voltage protection->PHPTOV: 2 | Operate delay time | 0.04-300:0.001 | s | Operating time delay for definite time curve | Real | Setting_Group |  |  |  | Voltage_protection_u002D__gt_PHPTOV_u003A__2_u003A_Operating_curve_type | EW | Time (59) |  |  |  |  | Under-Overvoltage LV\PHPTOV2 PhPh | Tpset | Real | 1 | 0 |  | Under-Overvoltage LV\PHPTOV2 PhPh | pcharac |  | EW | Time (59) |  | Under-Overvoltage LV\PHPTOV2 PhPh | Tpset | Real |  |  | 1 | 0
Voltage_protection_u002D__gt_PHPTUV_u003A__1_u003A_Start_value | Voltage protection->PHPTUV: 1 | Start value | 0.05-1.2:0.01 | pu | Preset value to check for the voltage violation | Real | Setting_Group | [10 empty] | Under-Overvoltage LV\PHPTUV1 PhPh | Ipset | Real | 1 | 0 | [7 empty] | Under-Overvoltage LV\PHPTUV1 PhPh | Ipset | Real |  |  | 1 | 0
Voltage_protection_u002D__gt_PHPTUV_u003A__1_u003A_Time_multiplier | Voltage protection->PHPTUV: 1 | Time multiplier | 0.05-15:0.01 |  | Time multiplier in IEC curves | Real | Setting_Group |  |  |  | Voltage_protection_u002D__gt_PHPTUV_u003A__1_u003A_Operating_curve_type | NEW | Time (27) |  |  |  |  | Under-Overvoltage LV\PHPTUV1 PhPh | Tpset | Real | 1 | 0 |  | Under-Overvoltage LV\PHPTUV1 PhPh | pcharac |  | NEW | Time (27) |  | Under-Overvoltage LV\PHPTUV1 PhPh | Tpset | Real |  |  | 1 | 0
Voltage_protection_u002D__gt_PHPTUV_u003A__1_u003A_Operating_curve_type | Voltage protection->PHPTUV: 1 | Operating curve type | ANSI Def. Time;IEC Def. Time;Inv. Curve A;Inv. Curve B;Programmable |  | Selection of the type of time delay curve | Enum | Setting_Group | ANSI Def. Time (27);IEC Def. Time (27);Inverse curve A (27);Inverse curve B (27); | String | [8 empty] | Under-Overvoltage LV\PHPTUV1 PhPh | pcharac | [10 empty] | Under-Overvoltage LV\PHPTUV1 PhPh | pcharac
Voltage_protection_u002D__gt_PHPTUV_u003A__1_u003A_Operate_delay_time | Voltage protection->PHPTUV: 1 | Operate delay time | 0.04-300:0.001 | s | Operating time delay for definite time curve | Real | Setting_Group |  |  |  | Voltage_protection_u002D__gt_PHPTUV_u003A__1_u003A_Operating_curve_type | EW | Time (27) |  |  |  |  | Under-Overvoltage LV\PHPTUV1 PhPh | Tpset | Real | 1 | 0 |  | Under-Overvoltage LV\PHPTUV1 PhPh | pcharac |  | EW | Time (27) |  | Under-Overvoltage LV\PHPTUV1 PhPh | Tpset | Real |  |  | 1 | 0
Voltage_protection_u002D__gt_PHPTUV_u003A__2_u003A_Start_value | Voltage protection->PHPTUV: 2 | Start value | 0.05-1.2:0.01 | pu | Preset value to check for the voltage violation | Real | Setting_Group | [10 empty] | Under-Overvoltage LV\PHPTUV2 PhPh | Ipset | Real | 1 | 0 | [7 empty] | Under-Overvoltage LV\PHPTUV2 PhPh | Ipset | Real |  |  | 1 | 0
Voltage_protection_u002D__gt_PHPTUV_u003A__2_u003A_Time_multiplier | Voltage protection->PHPTUV: 2 | Time multiplier | 0.05-15:0.01 |  | Time multiplier in IEC curves | Real | Setting_Group |  |  |  | Voltage_protection_u002D__gt_PHPTUV_u003A__2_u003A_Operating_curve_type | NEW | Time (27) |  |  |  |  | Under-Overvoltage LV\PHPTUV2 PhPh | Tpset | Real | 1 | 0 |  | Under-Overvoltage LV\PHPTUV2 PhPh | pcharac |  | NEW | Time (27) |  | Under-Overvoltage LV\PHPTUV2 PhPh | Tpset | Real |  |  | 1 | 0
Voltage_protection_u002D__gt_PHPTUV_u003A__2_u003A_Operating_curve_type | Voltage protection->PHPTUV: 2 | Operating curve type | ANSI Def. Time;IEC Def. Time;Inv. Curve A;Inv. Curve B;Programmable |  | Selection of the type of time delay curve | Enum | Setting_Group | ANSI Def. Time (27);IEC Def. Time (27);Inverse curve A (27);Inverse curve B (27); | String | [8 empty] | Under-Overvoltage LV\PHPTUV2 PhPh | pcharac | [10 empty] | Under-Overvoltage LV\PHPTUV2 PhPh | pcharac
Voltage_protection_u002D__gt_PHPTUV_u003A__2_u003A_Operate_delay_time | Voltage protection->PHPTUV: 2 | Operate delay time | 0.04-300:0.001 | s | Operating time delay for definite time curve | Real | Setting_Group |  |  |  | Voltage_protection_u002D__gt_PHPTUV_u003A__2_u003A_Operating_curve_type | EW | Time (27) |  |  |  |  | Under-Overvoltage LV\PHPTUV2 PhPh | Tpset | Real | 1 | 0 |  | Under-Overvoltage LV\PHPTUV2 PhPh | pcharac |  | EW | Time (27) |  | Under-Overvoltage LV\PHPTUV2 PhPh | Tpset | Real |  |  | 1 | 0
_END_
Current_protection_u002D__gt_EFLPTOC_u003A__2_u003A_Operation | Current protection->EFLPTOC: 2 | Operation | Off;On |  | Operation Off / On | Enum | Application_Configuration | 1;0 | Real | [8 empty] | Earth-fault LV\EFHPTOC | outserv | Real | 1 | 0 | [7 empty] | Earth-fault LV\EFHPTOC | outserv | Real |  |  | 1 | 0
Current_protection_u002D__gt_EFHPTOC_u003A__2_u003A_Reset_delay_time | Current protection->EFHPTOC: 2 | Reset delay time | 0-60:0.001 | s | Reset delay time | Real | Application_Configuration | [10 empty] | Earth-fault LV\EFHPTOC | ResetT | Real | 1 | 0 | [7 empty] | Earth-fault LV\EFHPTOC | ResetT | Real |  |  | 1 | 0
Current_protection_u002D__gt_EFHPTOC_u003A__2_u003A_Minimum_operate_time | Current protection->EFHPTOC: 2 | Minimum operate time | 0.02-60:0.001 | s | Minimum operate time for IDMT curves | Real | Application_Configuration |  |  |  | Current_protection_u002D__gt_EFHPTOC_u003A__2_u003A_Operating_curve_type | NEW | Time |  |  |  |  | Earth-fault LV\EFHPTOC | udeftmin | Real | 1 | 0 |  | Earth-fault LV\EFHPTOC | pcharac |  | NEW | Time |  | Earth-fault LV\EFHPTOC | udeftmin | Real |  |  | 1 | 0
Current_protection_u002D__gt_EFLPTOC_u003A__2_u003A_Operation | Current protection->EFLPTOC: 2 | Operation | Off;On |  | Operation Off / On | Enum | Application_Configuration | 1;0 | Real | [8 empty] | Earth-fault LV\EFLPTOC | outserv | Real | 1 | 0 | [7 empty] | Earth-fault LV\EFLPTOC | outserv | Real |  |  | 1 | 0
Current_protection_u002D__gt_EFLPTOC_u003A__2_u003A_Reset_delay_time | Current protection->EFLPTOC: 2 | Reset delay time | 0-60:0.001 | s | Reset delay time | Real | Application_Configuration | [10 empty] | Earth-fault LV\EFLPTOC | ResetT | Real | 1 | 0 | [7 empty] | Earth-fault LV\EFLPTOC | ResetT | Real |  |  | 1 | 0
Current_protection_u002D__gt_EFLPTOC_u003A__2_u003A_Minimum_operate_time | Current protection->EFLPTOC: 2 | Minimum operate time | 0.04-60:0.001 | s | Minimum operate time for IDMT curves | Real | Application_Configuration |  |  |  | Current_protection_u002D__gt_EFLPTOC_u003A__2_u003A_Operating_curve_type | NEW | Time |  |  |  |  | Earth-fault LV\EFLPTOC | udeftmin | Real | 1 | 0 |  | Earth-fault LV\EFLPTOC | pcharac |  | NEW | Time |  | Earth-fault LV\EFLPTOC | udeftmin | Real |  |  | 1 | 0
Current_protection_u002D__gt_EFHPTOC_u003A__2_u003A_Start_value | Current protection->EFHPTOC: 2 | Start value | 0.1-40:0.01 | pu | Start value | Real | Setting_Group | [10 empty] | Earth-fault LV\EFHPTOC | Ipset | Real | 1 | 0 | [7 empty] | Earth-fault LV\EFHPTOC | Ipset | Real |  |  | 1 | 0
Current_protection_u002D__gt_EFHPTOC_u003A__2_u003A_Time_multiplier | Current protection->EFHPTOC: 2 | Time multiplier | 0.05-15:0.01 |  | Time multiplier in IEC/ANSI IDMT curves | Real | Setting_Group |  |  |  | Current_protection_u002D__gt_EFHPTOC_u003A__2_u003A_Operating_curve_type | NEW | Time |  |  |  |  | Earth-fault LV\EFHPTOC | Tpset | Real | 1 | 0 |  | Earth-fault LV\EFHPTOC | pcharac |  | NEW | Time |  | Earth-fault LV\EFHPTOC | Tpset | Real |  |  | 1 | 0
Current_protection_u002D__gt_EFHPTOC_u003A__2_u003A_Operating_curve_type | Current protection->EFHPTOC: 2 | Operating curve type | ANSI Ext. inv.;ANSI Norm. inv.;ANSI Def. Time;IEC Norm. inv.;IEC Very inv.;IEC Ext. inv.;IEC Def. Time;Programmable |  | Selection of time delay curve type | Enum | Setting_Group | ANSI Ext. inv.;ANSI Norm. inv.;ANSI Def. Time;IEC Norm. inv.;IEC Very inv.;IEC Ext. inv.;IEC Def. Time; | String | [8 empty] | Earth-fault LV\EFHPTOC | pcharac | [10 empty] | Earth-fault LV\EFHPTOC | pcharac
Current_protection_u002D__gt_EFHPTOC_u003A__2_u003A_Operate_delay_time | Current protection->EFHPTOC: 2 | Operate delay time | 0.02-200:0.01 | s | Operate delay time | Real | Setting_Group |  |  |  | Current_protection_u002D__gt_EFHPTOC_u003A__2_u003A_Operating_curve_type | EW | Time |  |  |  |  | Earth-fault LV\EFHPTOC | Tpset | Real | 1 | 0 |  | Earth-fault LV\EFHPTOC | pcharac |  | EW | Time |  | Earth-fault LV\EFHPTOC | Tpset | Real |  |  | 1 | 0
Current_protection_u002D__gt_EFLPTOC_u003A__2_u003A_Start_value | Current protection->EFLPTOC: 2 | Start value | 0.01-5:0.001 | pu | Start value | Real | Setting_Group | [10 empty] | Earth-fault LV\EFLPTOC | Ipset | Real | 1 | 0 | [7 empty] | Earth-fault LV\EFLPTOC | Ipset | Real |  |  | 1 | 0
Current_protection_u002D__gt_EFLPTOC_u003A__2_u003A_Time_multiplier | Current protection->EFLPTOC: 2 | Time multiplier | 0.05-15:0.01 |  | Time multiplier in IEC/ANSI IDMT curves | Real | Setting_Group |  |  |  | Current_protection_u002D__gt_EFLPTOC_u003A__2_u003A_Operating_curve_type | NEW | Time |  |  |  |  | Earth-fault LV\EFLPTOC | Tpset | Real | 1 | 0 |  | Earth-fault LV\EFLPTOC | pcharac |  | NEW | Time |  | Earth-fault LV\EFLPTOC | Tpset | Real |  |  | 1 | 0
Current_protection_u002D__gt_EFLPTOC_u003A__2_u003A_Operating_curve_type | Current protection->EFLPTOC: 2 | Operating curve type | ANSI Ext. inv.;ANSI Very inv.;ANSI Norm. inv.;ANSI Mod. inv.;ANSI Def. Time;L.T.E. inv.;L.T.V. inv.;L.T. inv.;IEC Norm. inv.;IEC Very inv.;IEC inv.;IEC Ext. inv.;IEC S.T. inv.;IEC L.T. inv.;IEC Def. Time;Programmable;RI type;RD type |  | Selection of time delay curve type | Enum | Setting_Group | ANSI Ext. inv.;ANSI Very inv.;ANSI Norm. inv.;ANSI Mod. inv.;ANSI Def. Time;L.T.E. inv.;L.T.V. inv.;L.T. inv.;IEC Norm. inv.;IEC Very inv.;IEC inv.;IEC Ext. inv.;IEC S.T. inv.;IEC L.T. inv.;IEC Def. Time; ;RI type;RD type | String | [8 empty] | Earth-fault LV\EFLPTOC | pcharac | [10 empty] | Earth-fault LV\EFLPTOC | pcharac
Current_protection_u002D__gt_EFLPTOC_u003A__2_u003A_Operate_delay_time | Current protection->EFLPTOC: 2 | Operate delay time | 0.04-200:0.01 | s | Operate delay time | Real | Setting_Group |  |  |  | Current_protection_u002D__gt_EFLPTOC_u003A__2_u003A_Operating_curve_type | EW | Time |  |  |  |  | Earth-fault LV\EFLPTOC | Tpset | Real | 1 | 0 |  | Earth-fault LV\EFLPTOC | pcharac |  | NEW | Time |  | Earth-fault LV\EFLPTOC | Tpset | Real |  |  | 1 | 0